## Energy&Water (hidden)
Energy
| Value (updated data) | Validation
1) Prices in US$ | * Check that price is in range of [a,b]
Electricity (kWh) | 0.47 | TRUE
Natural gas (lbs) | 0
Diesel (gallons) | 4 | Donot have price range for Diesel or others
Oil (gallons) | 0
2) Pre-retrofitting consumption
Electricity (kWh) | 34800
Natural gas (lbs) | 0
Diesel (gallons) | 45
Oil (gallons) | 0
3) Post-retrofitting Saving
Window Electricity | 9744
Window Natural Gas | 0
Window Diesel | 0
Window Oil | 0
Roof Electricity | 0
Roof Natural Gas | 0
Roof Diesel | 0
Roof Oil | 0
HVAC Electricity | 8526
HVAC Natural Gas | 0
HVAC Diesel | 0
HVAC Oil | 0
Lighting Electricity | 2825
Lighting Natural Gas | 0
Lighting Diesel | 0
Lighting Oil | 0
Renewable energy Electricity | 27800
Renewable energy Natural Gas | 0
Renewable energy Diesel | 0
Renewable energy Oil | 0
Water heating Electricity | 0
Water heating Natural Gas | 0
Water heating Diesel | 0
Water heating Oil | 0
Laundry equipment Electricity | 0
Laundry equipment Natural Gas | 0
Laundry equipment Diesel | 0
Laundry equipment Oil | 0
Other non-medical equipment Electricity | 0
Other non-medical equipment Natural Gas | 0
Other non-medical equipment Diesel | 0
Other non-medical equipment Oil | 0
Medical equipment Electricity | 0
Medical equipment Natural Gas | 0
Medical equipment Diesel | 0
Medical equipment Oil | 0
Total Post-retrofitting Saving
Windows | 9744
Roof | 0
HVAC | 0
Lighting | 2825
Renewable energy | 27800
Water heating | 0
Laundry equipment | 0
Other non-medical equipment | 0
Medical equipment | 0
Calculated Savings
Window Electricity | 4579.68
Window Natural Gas | 0
Window Diesel | 0
Window Oil | 0
Total | 4579.68
Roof Electricity | 0
Roof Natural Gas | 0
Roof Diesel | 0
Roof Oil | 0
Total | 0
HVAC Electricity | 4007.22
HVAC Natural Gas | 0
HVAC Diesel | 0
HVAC Oil | 0
Total | 4007.22
Lighting Electricity | 1327.75
Lighting Natural Gas | 0
Lighting Diesel | 0
Lighting Oil | 0
Total | 1327.75
Renewable energy Electricity | 13066
Renewable energy Natural Gas | 0
Renewable energy Diesel | 0
Renewable energy Oil | 0
Total | 13066
Water heating Electricity | 0
Water heating Natural Gas | 0
Water heating Diesel | 0
Water heating Oil | 0
Total | 0
Laundry equipment Electricity | 0
Laundry equipment Natural Gas | 0
Laundry equipment Diesel | 0
Laundry equipment Oil | 0
Total | 0
Other non-medical equipment Electricity | 0
Other non-medical equipment Natural Gas | 0
Other non-medical equipment Diesel | 0
Other non-medical equipment Oil | 0
Total | 0
Medical equipment Electricity | 0
Medical equipment Natural Gas | 0
Medical equipment Diesel | 0
Medical equipment Oil | 0
Total | 0
4) Savings | * Validate: Calculated Saving = Given Saving
Windows | 0 | FALSE
Roof | 0 | TRUE
HVAC | 0 | FALSE
Lighting | 0 | FALSE
Renewable energy | 0 | FALSE
Water heating | 0 | TRUE
Laundry equipment | 0 | TRUE
Other non-medical equipment | 0 | TRUE
Medical equipment | 0 | TRUE
Investment
Windows | 0
Roof | 0
HVAC | 25300
Lighting | 10100
Renewable energy | 120000
Water heating | 8500
Laundry equipment | 0
Other non-medical equipment | 0
Medical equipment | 0

## Sheet1 (hidden)
Question in Qualtrics | Question in the VBA form | Label | Default data | Updated data | Temporary data
Q2 | REST | Country | Dominica | Dominica | Dominica
Q5 | N/A | What currency do you use locally? Please note: When asked for the cost of anything from this point forward in the survey, please put it in United States Dollars (USD).
Q6 | N/A | What is the current exchange rate for your country's currency for 1 US Dollar (USD)?
Q8 | REST | Health Care Facility Name | Add a name | Add a name | Add a name
Q9 | N/A | Street Address
Q10_1 | GeneralInformation Q3 | Latitude - Decimal degrees | 15.4239 | 15.4239 | 15.4239
Q10_2 | GeneralInformation Q3 | Latitude - Minutes
Q10_3 | GeneralInformation Q3 | Latitude - Seconds
Q11_1 | GeneralInformation Q4 | Longitude - Decimal degrees | -60.6399 | -60.6399 | -60.6399
Q11_2 | GeneralInformation Q4 | Longitude - Minutes
Q11_3 | GeneralInformation Q4 | Longitude - Seconds
Q12_1 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Sunday | 0 | 0 | 0
Q12_2 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Monday | 8 | 8 | 8
Q12_3 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Tuesday | 8 | 8 | 8
Q12_4 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Wednesday | 8 | 8 | 8
Q12_5 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Thursday | 8 | 8 | 8
Q12_6 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Friday | 8 | 8 | 8
Q12_7 | GeneralInformation Q5 | Operating Hours: How many hours a day does the health care facility operate? The total will reflect how many hours the facility is open per week. It refers to normal operations, not to emergency or urgent care services. - Saturday | 0 | 0 | 0
Q13_1_1 | GeneralInformation Q6 | Number of Staff (Full and Part Time - including healthcare providers and all other workers working in the facility). - Full-time - Number of Staff | 9 | 9 | 9
Q13_2_1 | GeneralInformation Q6 | Number of Staff (Full and Part Time - including healthcare providers and all other workers working in the facility). - Part time (3 or more days a week) - Number of Staff
Q13_3_1 | GeneralInformation Q6 | Number of Staff (Full and Part Time - including healthcare providers and all other workers working in the facility). - Part time (less than 3 days a week) - Number of Staff
Q14 | GeneralInformation Q7a | Healthcare services provided by the facility (check all that apply) - Primary care or ambulatory services Primary care or ambulatory services | TRUE | TRUE | TRUE
Q14 | GeneralInformation Q7b | Healthcare services provided by the facility (check all that apply) - Outpatient surgery services
Q14 | GeneralInformation Q7c | Healthcare services provided by the facility (check all that apply) - Emergency or urgent care services | TRUE | TRUE | TRUE
Q14 | GeneralInformation Q7d | Healthcare services provided by the facility (check all that apply) - Inpatient hospital services | FALSE | FALSE | FALSE
Q14 | N/A | Healthcare services provided by the facility (check all that apply) - Nursing home or other assisting living services
Q14 | N/A | Healthcare services provided by the facility (check all that apply) - Dental lab services
Q14 | N/A | Healthcare services provided by the facility (check all that apply) - Pharmacy services
Q14_6_TEXT | N/A | Healthcare services provided by the facility (check all that apply) - Other - Text
Q15 | GeneralInformation Q8 | Number of Exam/Consulting Rooms
Q16_1_1 | GeneralInformation Q9 | Please provide the average number of patient consultations per day (given if the day is slow, normal, or busy). - Slow day - Average number of patient consultations per day | 15 | 15 | 15
Q16_2_1 | GeneralInformation Q9 | Please provide the average number of patient consultations per day (given if the day is slow, normal, or busy). - Normal day - Average number of patient consultations per day | 25 | 25 | 25
Q16_3_1 | GeneralInformation Q9 | Please provide the average number of patient consultations per day (given if the day is slow, normal, or busy). - Busy day - Average number of patient consultations per day | 45 | 45 | 45
Q17 | GeneralInformation Q10 | Number of Beds | 1 | 1 | 1
Q18 | GeneralInformation Q11 | On an average day, how many patients are admitted to the health care facility? | 1 | 1 | 1
Q19 | GeneralInformation Q12 | What is the average length of stay (in days) in the health care facility? | 2 | 2 | 2
Q22 | Safety Q1 | Construction Class Definitions Please refer to the construction class definitions by clicking on the link above to help determine the closest construction class/building material of your location. | 9 | 9 | 9
Q23 | Safety Q2 | What is the most prominent construction material for the health care facility? (Please choose one from the drop-down menu). | 1 | 1 | 1
Q24 | Safety Q3 | Replacement Value (the amount an entity would have to pay to replace the building to be retrofitted at the present time, according to its current worth, in the event it is destroyed or demolished). Please give value in United States Dollars (USD). | 1000000 | 1000000 | 1000000
Q26 | Safety Q4a | Was the building constructed after 1980? | TRUE | TRUE | TRUE
Q26 | Safety Q4b | Was the building constructed after 1980? |  | FALSE | FALSE
Q27 | Safety Q5 | Number of Stories/Floors | 1 | 1 | 1
Q28 | Safety Q6 | Gross Floor Area (sq. m.) of the facility to be retrofitted (the total area of your building - everything inside the walls. This means plazas, parking lots and other outside areas are not included). | 335 | 335 | 335
Q29#1_1_1 | Safety Q7 | Please consider the floor plan of the facility. - Pre-Retrofitting - Height (in meters) between the ground outside of the facility, and the floo... - Height (in meters) between the ground outside of the facility, and the floor of the first level, inside the facility. - | 0.3 | 0.3 | 0.3
Q30#1_1_1 | Safety Q8 | Please consider the roof of the facility. - Pre-Retrofitting - Distance between the roof supports (in meters) - | 3 | 3 | 3
Q30#1_2_1 | Safety Q8 | Please consider the roof of the facility. - Pre-Retrofitting - Length of the roof (in meters) - | 18.303 | 18.303 | 18.303
Q30#1_3_1 | Safety Q8 | Please consider the roof of the facility. - Pre-Retrofitting - Roof inclination angle (please give answer in degrees) - pictures may be us... - Roof inclination angle (please give answer in degrees) - pictures may be used to make the estimate. - | 20 | 20 | 20
Q31 | Safety Q9 | What is the type of material of the roof? | 0 | 0 | 0
Q32 | N/A | You have selected that the material of the ceiling is something other than concrete. Please, specify what type of material the ceiling is.
Q33 | Safety Q11 | Please, provide the current pressure resistance of the roof-wall connection (in pounds) (Conversion: 1 pound (lb) = 2.2 kg). Please estimate using the lowest resistance known. | 319 | 319 | 319
Q32#1_2_1 | Safety Q12 | Please consider the windows and/or glass doors in the facility. - Pre-Retrofitting - Size of largest window (in meters-squared/m2) - | 1 | 1 | 1
Q31#1_1_1 | Safety Q13 | Please consider the walls in the facility - Pre-Retrofitting - Maximum distance between columns (in meters). The distance should be the lo... - Maximum distance between columns (in meters). The distance should be the longest of the facility, considering columns or other walls (brick walls, not drywalls) as supports. - | 9.1515 | 9.1515 | 9.1515
Q31#1_2_1 | Safety Q13 | Please consider the walls in the facility - Pre-Retrofitting - Height of the walls (in meters). The highest wall's value should be used. - | 3 | 3 | 3
Q36 | N/A | Are you aware of any other retrofitting work not completely funded by PAHO regarding the Hospital Safety Index?
Q36 | N/A | Are you aware of any other retrofitting work not completely funded by PAHO regarding the Hospital Safety Index?
Q37 | N/A | You selected that you are aware of other retrofitting work for the Hospital Safety Index that is not completely funded by PAHO/DFID. Please briefly describe this additional work; and, please contact Alejandro Arrieta at alejarri@fiu.edu to provide more information.
Q39#1_4 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Substructural components | 2 | 2 | 2
Q39#1_5 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Superstructural components: Roof | 0 | 0 | 0
Q39#1_6 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Superstructural components: Walls | 2 | 2 | 2
Q39#1_7 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Superstructural components: Windows | 1 | 1 | 1
Q39#1_8 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Superstructural components: Floor | 2 | 2 | 2
Q39#1_9 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Superstructural components: Others | 0 | 0 | 0
Q39#1_10 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Structures that protect sources of electricity in emergency situations (e.g. generator room) | 2 | 2 | 2
Q39#1_11 | Safety Q26 | Projected retrofitting work to improve safety - Based on Pre-Retrofitting HSI, determine the safety of each component in case of emergency situations - Structures that protects water reserves in emergency situations (e.g. storage tank room) | 0 | 0 | 0
Q39#2_4 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Substructural components | 2 | 2 | 2
Q39#2_5 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Superstructural components: Roof | 4 | 4 | 4
Q39#2_6 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Superstructural components: Walls | 4 | 4 | 4
Q39#2_7 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Superstructural components: Windows | 4 | 4 | 4
Q39#2_8 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Superstructural components: Floor | 4 | 4 | 4
Q39#2_9 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Superstructural components: Others | 4 | 4 | 4
Q39#2_10 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Structures that protect sources of electricity in emergency situations (e.g. generator room) | 4 | 4 | 4
Q39#2_11 | Safety Q26 | Projected retrofitting work to improve safety - Based on projected retrofitting work, assess the Post-Retrofitting HSI - Structures that protects water reserves in emergency situations (e.g. storage tank room) | 4 | 4 | 4
Q39#3_4_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Substructural components - Minimum cost (USD) | 0 | 0 | 0
Q39#3_4_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Substructural components - Maximum cost (USD)
Q39#3_5_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Roof - Minimum cost (USD) | 36000 | 36000 | 36000
Q39#3_5_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Roof - Maximum cost (USD)
Q39#3_6_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Walls - Minimum cost (USD) | 64800 | 64800 | 64800
Q39#3_6_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Walls - Maximum cost (USD)
Q39#3_7_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Windows - Minimum cost (USD) | 47000 | 47000 | 47000
Q39#3_7_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Windows - Maximum cost (USD)
Q39#3_8_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Floor - Minimum cost (USD) | 18300 | 18300 | 18300
Q39#3_8_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Floor - Maximum cost (USD)
Q39#3_9_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Others - Minimum cost (USD) | 3500 | 3500 | 3500
Q39#3_9_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Superstructural components: Others - Maximum cost (USD)
Q39#3_10_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Structures that protect sources of electricity in emergency situations (e.... - Structures that protect sources of electricity in emergency situations (e.g. generator room) - Minimum cost (USD) | 34000 | 34000 | 34000
Q39#3_10_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Structures that protect sources of electricity in emergency situations (e.... - Structures that protect sources of electricity in emergency situations (e.g. generator room) - Maximum cost (USD)
Q39#3_11_1 | Safety Q26 | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Structures that protects water reserves in emergency situations (e.g. stora... - Structures that protects water reserves in emergency situations (e.g. storage tank room) - Minimum cost (USD) | 1700 | 1700 | 1700
Q39#3_11_2 | N/A | Projected retrofitting work to improve safety - Provide an estimated range of the associated retrofitting work - Structures that protects water reserves in emergency situations (e.g. stora... - Structures that protects water reserves in emergency situations (e.g. storage tank room) - Maximum cost (USD)
Q41 | Safety Q16 | Catchment Population (the potential total number of people served by this healthcare facility). | 3036 | 3036 | 3036
Q43 | Safety Q17 | Please choose the most common construction class in the catchment area, the class that best represents the majority of the residential buildings in the catchment area of the health care facility, from the drop down menu below. | 7 | 7 | 7
Q44 | Safety Q18 | What fraction of constructions can be classified as this construction class? Please provide a rough estimate of the percentage of residential buildings that are in this construction class (for example, 40% are class C1). | 1 | 1 | 1
Q45 | Safety Q19 | What are the most common number of stories/floors for this construction class? | 1 | 1 | 1
Q46 | Safety Q20 | Now, please choose the second most common construction class in the catchment area from the drop down menu below. | 9 | 9 | 9
Q47 | Safety Q21 | What fraction of constructions can be classified as this construction class? Please provide a rough estimate of the percentage of residential buildings that are in this construction class (for example, 40% are class C1). | 4 | 4 | 4
Q48 | Safety Q22 | What are the most common number of stories/floors for this construction class? | 1 | 1 | 1
Q49 | Safety Q23 | Finally, please choose the third most common construction class in the catchment area from the drop down menu below. | 0 | 0 | 0
Q50 | Safety Q24 | What fraction of constructions can be classified as this construction class? Please provide a rough estimate of the percentage of residential buildings that are in this construction class (for example, 40% are class C1). | 4 | 4 | 4
Q51 | Safety Q25 | What are the most common number of stories/floors for this construction class? | 1 | 1 | 1
Q57 | N/A | What types of energy are directly consumed in the facility
Q58_1_1 | Enerygy Q1 | Report the average annual consumption of this facility (consider the previous 12 months) - Electricity (kWh) - Units | 34800 | 34800 | 34800
Q58_2_1 | Enerygy Q1 | Report the average annual consumption of this facility (consider the previous 12 months) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lb... - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs) - Units
Q58_3_1 | Enerygy Q1 | Report the average annual consumption of this facility (consider the previous 12 months) - Diesel (gallons) - Units | 45 | 45 | 45
Q58_4_1 | Enerygy Q1 | Report the average annual consumption of this facility (consider the previous 12 months) - Oil (gallons) - Units
Q59_1_1 | Enerygy Q2 | Report the average price of energy per unit of energy in the last 12 months (in United States Dollars (USD)). - Electricity (USD/kWh) - Price | 0.47 | 0.47 | 0.47
Q59_2_1 | Enerygy Q2 | Report the average price of energy per unit of energy in the last 12 months (in United States Dollars (USD)). - Natural Gas (USD/lbs) (Conversion: 1 kg = 2.2 lbs) - Price
Q59_3_1 | Enerygy Q2 | Report the average price of energy per unit of energy in the last 12 months (in United States Dollars (USD)). - Diesel (USD/gallons) - Price | 4 | 4 | 4
Q59_4_1 | Enerygy Q2 | Report the average price of energy per unit of energy in the last 12 months (in United States Dollars (USD)). - Oil (USD/gallons) - Price
Q60#1_1_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) - | 0 | 0 | 0
Q60#1_2_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) - | 0 | 0 | 0
Q60#1_3_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - HVAC (air conditioning units will be replaced with R410a inverter units) - | 25300 | 25300 | 25300
Q60#1_4_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) - | 10100 | 10100 | 10100
Q60#1_5_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Renewable energy (27kWh Photovoltaic System) - | 120000 | 120000 | 120000
Q60#1_6_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Water heating (Water heaters will be replaced with solar water heaters) - | 8500 | 8500 | 8500
Q60#1_7_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) - | 0 | 0 | 0
Q60#1_8_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Other non-medical equipment - | 0 | 0 | 0
Q60#1_9_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Associated Retrofitting Investment Cost of Energy Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit - | 0 | 0 | 0
Q60#2_1_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) - Electricity (kWh) | 9744 | 9744 | 9744
Q60#2_1_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_1_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) - Diesel (gallons)
Q60#2_1_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) - Oil (gallons)
Q60#2_2_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) - Electricity (kWh)
Q60#2_2_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_2_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) - Diesel (gallons)
Q60#2_2_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) - Oil (gallons)
Q60#2_3_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - HVAC (air conditioning units will be replaced with R410a inverter units) - Electricity (kWh) | 8526 | 8526 | 8526
Q60#2_3_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - HVAC (air conditioning units will be replaced with R410a inverter units) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_3_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - HVAC (air conditioning units will be replaced with R410a inverter units) - Diesel (gallons)
Q60#2_3_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - HVAC (air conditioning units will be replaced with R410a inverter units) - Oil (gallons)
Q60#2_4_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) - Electricity (kWh) | 2825 | 2825 | 2825
Q60#2_4_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_4_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) - Diesel (gallons)
Q60#2_4_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) - Oil (gallons)
Q60#2_5_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Renewable energy (27kWh Photovoltaic System) - Electricity (kWh) | 27800 | 27800 | 27800
Q60#2_5_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Renewable energy (27kWh Photovoltaic System) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_5_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Renewable energy (27kWh Photovoltaic System) - Diesel (gallons)
Q60#2_5_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Renewable energy (27kWh Photovoltaic System) - Oil (gallons)
Q60#2_6_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Water heating (Water heaters will be replaced with solar water heaters) - Electricity (kWh)
Q60#2_6_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Water heating (Water heaters will be replaced with solar water heaters) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_6_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Water heating (Water heaters will be replaced with solar water heaters) - Diesel (gallons)
Q60#2_6_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Water heating (Water heaters will be replaced with solar water heaters) - Oil (gallons)
Q60#2_7_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) - Electricity (kWh)
Q60#2_7_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_7_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) - Diesel (gallons)
Q60#2_7_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) - Oil (gallons)
Q60#2_8_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Other non-medical equipment - Electricity (kWh)
Q60#2_8_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Other non-medical equipment - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_8_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Other non-medical equipment - Diesel (gallons)
Q60#2_8_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Other non-medical equipment - Oil (gallons)
Q60#2_9_1 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit - Electricity (kWh)
Q60#2_9_2 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit - Natural Gas (please list number in pounds (lbs)) (Conversion: 1 kg = 2.2 lbs)
Q60#2_9_3 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit - Diesel (gallons)
Q60#2_9_4 | Enerygy Q3 | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Energy Savings due to Retrofitting - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit - Oil (gallons)
Q60#3_1_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Windows (Tinted windows reduce the amount of radiation transmitted through... - Windows (Tinted windows reduce the amount of radiation transmitted through the glass keeping the room cooler) -
Q60#3_2_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Roofs (New hip roof will provide a base for the solar panels to be mounted... - Roofs (New hip roof will provide a base for the solar panels to be mounted and will be significantly cooler than existing concrete roof) -
Q60#3_3_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - HVAC (air conditioning units will be replaced with R410a inverter units) -
Q60#3_4_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures... - Lighting (Existing lamps will be replaced with LED lamps, cost of fixtures are included) -
Q60#3_5_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Renewable energy (27kWh Photovoltaic System) -
Q60#3_6_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Water heating (Water heaters will be replaced with solar water heaters) -
Q60#3_7_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Laundry equipment (Washing machine will be replaced with a commercial grade... - Laundry equipment (Washing machine will be replaced with a commercial grade energy star rated unit) -
Q60#3_8_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Other non-medical equipment -
Q60#3_9_1 | N/A | Complete the following table based on estimations from technical specifications and other sources... - Estimated Annual Savings in United States Dollars (USD). - Medical equipment (Sterilizer will be replaced with more energy and water e... - Medical equipment (Sterilizer will be replaced with more energy and water efficient unit -
Q65_1_1 | Water Q1 | Report the average annual consumption of this facility (consider the previous 12 months) - Water (gallons) - Units | 398104 | 398104 | 398104
Q66_1_1 | Water Q2 | Report the average price of water per gallon in the last 12 months (in United States Dollars (USD)). - Water (gallons) - Price | 0.05 | 0.05 | 0.05
Q67#1_1_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Operations and Medical Equipment (installation of systems to medical equipm... - Operations and Medical Equipment (installation of systems to medical equipment to reduce water use; repair leaks and unnecessary flows) - | 0 | 0 | 0
Q67#1_2_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Bathrooms/Restrooms (installation of systems, flow control fixtures, and ot... - Bathrooms/Restrooms (installation of systems, flow control fixtures, and other water-savings equipment in faucets, toilets, urinals, etc.; repair leaks and unnecessary flows) - | 7400 | 7400 | 7400
Q67#1_3_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Laundry (install washwater, rinsewater or reclamation systems to reuse rins... - Laundry (install washwater, rinsewater or reclamation systems to reuse rinsewater for wash cycle to reduce water use; repair leaks and unnecessary flows) - | 0 | 0 | 0
Q67#1_4_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Building Maintenance (install water-efficient boiler and cooling systems, c... - Building Maintenance (install water-efficient boiler and cooling systems, cleaning systems and other building maintenance systems; repair leaks and unnecessary flows) - | 0 | 0 | 0
Q67#1_5_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Cafeteria/Food Service (install water-efficient systems for pot washing, ga... - Cafeteria/Food Service (install water-efficient systems for pot washing, garbage disposal, etc.; repair leaks and unnecessary flows) - | 0 | 0 | 0
Q67#1_6_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler syst... - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler systems, etc.; repair leaks and unnecessary flows) - | 0 | 0 | 0
Q67#1_7_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Associated Retrofitting Investment Cost of Water-Saving Improvements in United States Dollars (USD). Write 0 if no investment is performed for this item. - TOTAL (provide the total investment, -
Q67#2_1_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Operations and Medical Equipment (installation of systems to medical equipm... - Operations and Medical Equipment (installation of systems to medical equipment to reduce water use; repair leaks and unnecessary flows) - Water (gallons)
Q67#2_2_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Bathrooms/Restrooms (installation of systems, flow control fixtures, and ot... - Bathrooms/Restrooms (installation of systems, flow control fixtures, and other water-savings equipment in faucets, toilets, urinals, etc.; repair leaks and unnecessary flows) - Water (gallons) | 86388 | 86388 | 86388
Q67#2_3_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Laundry (install washwater, rinsewater or reclamation systems to reuse rins... - Laundry (install washwater, rinsewater or reclamation systems to reuse rinsewater for wash cycle to reduce water use; repair leaks and unnecessary flows) - Water (gallons)
Q67#2_4_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Building Maintenance (install water-efficient boiler and cooling systems, c... - Building Maintenance (install water-efficient boiler and cooling systems, cleaning systems and other building maintenance systems; repair leaks and unnecessary flows) - Water (gallons)
Q67#2_5_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Cafeteria/Food Service (install water-efficient systems for pot washing, ga... - Cafeteria/Food Service (install water-efficient systems for pot washing, garbage disposal, etc.; repair leaks and unnecessary flows) - Water (gallons)
Q67#2_6_1 | Water Q3 | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler syst... - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler systems, etc.; repair leaks and unnecessary flows) - Water (gallons)
Q67#2_7_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Water Savings due to Retrofitting - TOTAL (provide the total investment, - Water (gallons)
Q67#3_1_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Operations and Medical Equipment (installation of systems to medical equipm... - Operations and Medical Equipment (installation of systems to medical equipment to reduce water use; repair leaks and unnecessary flows) -
Q67#3_2_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Bathrooms/Restrooms (installation of systems, flow control fixtures, and ot... - Bathrooms/Restrooms (installation of systems, flow control fixtures, and other water-savings equipment in faucets, toilets, urinals, etc.; repair leaks and unnecessary flows) -
Q67#3_3_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Laundry (install washwater, rinsewater or reclamation systems to reuse rins... - Laundry (install washwater, rinsewater or reclamation systems to reuse rinsewater for wash cycle to reduce water use; repair leaks and unnecessary flows) -
Q67#3_4_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Building Maintenance (install water-efficient boiler and cooling systems, c... - Building Maintenance (install water-efficient boiler and cooling systems, cleaning systems and other building maintenance systems; repair leaks and unnecessary flows) -
Q67#3_5_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Cafeteria/Food Service (install water-efficient systems for pot washing, ga... - Cafeteria/Food Service (install water-efficient systems for pot washing, garbage disposal, etc.; repair leaks and unnecessary flows) -
Q67#3_6_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler syst... - Outdoor Water Use (install water-efficient hoses, irrigation/sprinkler systems, etc.; repair leaks and unnecessary flows) -
Q67#3_7_1 | N/A | Complete the following tables based on estimations from technical specifications and other source... - Estimated Annual Savings in United States Dollars (USD). - TOTAL (provide the total investment, -
NEW | Safety Q5 | Number of Stories/Floors (Post-Retrofitted) | 1 | 1 | 1
NEW | Safety Q6 | Gross Floor Area (sq. m.) of the facility post-retrofitted (the total area of your building - everything inside the walls. This means plazas, parking lots and other outside areas are not included). | 335 | 335 | 335
NEW | Safety Q7 | Please consider the floor plan of the facility. - Post-Retrofitting - Height (in meters) between the ground outside of the facility, and the floo... - Height (in meters) between the ground outside of the facility, and the floor of the first level, inside the facility. - | 0.3 | 0.3 | 0.3
NEW | Safety Q8 | Please consider the roof of the facility. - Post-Retrofitting - Distance between the roof supports (in meters) - | 3 | 3 | 3
NEW | Safety Q8 | Please consider the roof of the facility. - Post-Retrofitting - Length of the roof (in meters) - | 18.303 | 18.303 | 18.303
NEW | Safety Q8 | Please consider the roof of the facility. - Post-Retrofitting - Roof inclination angle (please give answer in degrees) - pictures may be us... - Roof inclination angle (please give answer in degrees) - pictures may be used to make the estimate. - | 20 | 20 | 20
NEW | Safety Q9 | What is the type of material of the roof? | 0 | 0 | 0
NEW | Safety Q11 | Please, provide the current pressure resistance of the roof-wall connection (in pounds) (Conversion: 1 pound (lb) = 2.2 kg). Please estimate using the lowest resistance known. | 319 | 319 | 319
NEW | Safety Q12 | Please consider the windows and/or glass doors in the facility. - Post-Retrofitting - Size of largest window (in meters-squared/m2) - | 1 | 1 | 1
NEW | Safety Q13 | Please consider the walls in the facility - Post-Retrofitting - Maximum distance between columns (in meters). The distance should be the lo... - Maximum distance between columns (in meters). The distance should be the longest of the facility, considering columns or other walls (brick walls, not drywalls) as supports. - | 9.1515 | 9.1515 | 9.1515
NEW | Safety Q13 | Please consider the walls in the facility - Post-Retrofitting - Height of the walls (in meters). The highest wall's value should be used. - | 3 | 3 | 3

## PGA (hidden)
|  | LATITUDE | LONGITUDE | PGA_0.2 SEC | PGA-0.5 SEC | PGA-1.0 SEC
215237 | 9-59 | 9 | -59 | 0 | 0 | 0
215958 | 9-59.5 | 9 | -59.5 | 0 | 0 | 0
216679 | 9-60 | 9 | -60 | 0 | 0 | 0
217400 | 9-60.5 | 9 | -60.5 | 0 | 0 | 0
218121 | 9-61 | 9 | -61 | 0 | 0 | 0
218842 | 9-61.5 | 9 | -61.5 | 0 | 0 | 0
219563 | 9-62 | 9 | -62 | 0 | 0 | 0
220284 | 9-62.5 | 9 | -62.5 | 0 | 0 | 0
221005 | 9-63 | 9 | -63 | 0 | 0 | 0
221726 | 9-63.5 | 9 | -63.5 | 0 | 0 | 0
222447 | 9-64 | 9 | -64 | 0 | 0 | 0
223168 | 9-64.5 | 9 | -64.5 | 0 | 0 | 0
223889 | 9-65 | 9 | -65 | 0 | 0 | 0
224610 | 9-65.5 | 9 | -65.5 | 0 | 0 | 0
225331 | 9-66 | 9 | -66 | 0 | 0 | 0
226052 | 9-66.5 | 9 | -66.5 | 0 | 0 | 0
226773 | 9-67 | 9 | -67 | 0 | 0 | 0
227494 | 9-67.5 | 9 | -67.5 | 0 | 0 | 0
228215 | 9-68 | 9 | -68 | 0 | 0 | 0
228936 | 9-68.5 | 9 | -68.5 | 0 | 0 | 0
229657 | 9-69 | 9 | -69 | 0 | 0 | 0
230378 | 9-69.5 | 9 | -69.5 | 0 | 0 | 0
231099 | 9-70 | 9 | -70 | 0 | 0 | 0
231820 | 9-70.5 | 9 | -70.5 | 0 | 0 | 0
232541 | 9-71 | 9 | -71 | 0 | 0 | 0
233262 | 9-71.5 | 9 | -71.5 | 0 | 0 | 0
233983 | 9-72 | 9 | -72 | 0 | 0 | 0
234704 | 9-72.5 | 9 | -72.5 | 0 | 0 | 0
235425 | 9-73 | 9 | -73 | 0 | 0 | 0
236146 | 9-73.5 | 9 | -73.5 | 0 | 0 | 0
236867 | 9-74 | 9 | -74 | 0 | 0 | 0
237588 | 9-74.5 | 9 | -74.5 | 0 | 0 | 0
238309 | 9-75 | 9 | -75 | 0 | 0 | 0
239030 | 9-75.5 | 9 | -75.5 | 0 | 0 | 0
239751 | 9-76 | 9 | -76 | 0 | 0 | 0
240472 | 9-76.5 | 9 | -76.5 | 0 | 0 | 0
241193 | 9-77 | 9 | -77 | 0 | 0 | 0
241914 | 9-77.5 | 9 | -77.5 | 0 | 0 | 0
242635 | 9-78 | 9 | -78 | 0 | 0 | 0
243356 | 9-78.5 | 9 | -78.5 | 0 | 0 | 0
244077 | 9-79 | 9 | -79 | 0 | 0 | 0
244798 | 9-79.5 | 9 | -79.5 | 0 | 0 | 0
245519 | 9-80 | 9 | -80 | 0 | 0 | 0
246240 | 9-80.5 | 9 | -80.5 | 0 | 0 | 0
246961 | 9-81 | 9 | -81 | 0 | 0 | 0
247682 | 9-81.5 | 9 | -81.5 | 0 | 0 | 0
248403 | 9-82 | 9 | -82 | 0 | 0 | 0
249124 | 9-82.5 | 9 | -82.5 | 0 | 0 | 0
249845 | 9-83 | 9 | -83 | 0 | 0 | 0
250566 | 9-83.5 | 9 | -83.5 | 0 | 0 | 0
251287 | 9-84 | 9 | -84 | 0 | 0 | 0
252008 | 9-84.5 | 9 | -84.5 | 0 | 0 | 0
252729 | 9-85 | 9 | -85 | 0 | 0 | 0
253450 | 9-85.5 | 9 | -85.5 | 0 | 0 | 0
254171 | 9-86 | 9 | -86 | 0 | 0 | 0
254892 | 9-86.5 | 9 | -86.5 | 0 | 0 | 0
255613 | 9-87 | 9 | -87 | 0 | 0 | 0
256334 | 9-87.5 | 9 | -87.5 | 0 | 0 | 0
257055 | 9-88 | 9 | -88 | 0 | 0 | 0
257776 | 9-88.5 | 9 | -88.5 | 0 | 0 | 0
258497 | 9-89 | 9 | -89 | 0 | 0 | 0
259218 | 9-89.5 | 9 | -89.5 | 0 | 0 | 0
259939 | 9-90 | 9 | -90 | 0 | 0 | 0
215238 | 9.5-59 | 9.5 | -59 | 0 | 0 | 0
215959 | 9.5-59.5 | 9.5 | -59.5 | 0 | 0 | 0
216680 | 9.5-60 | 9.5 | -60 | 0 | 0 | 0
217401 | 9.5-60.5 | 9.5 | -60.5 | 0 | 0 | 0
218122 | 9.5-61 | 9.5 | -61 | 0 | 0 | 0
218843 | 9.5-61.5 | 9.5 | -61.5 | 0 | 0 | 0
219564 | 9.5-62 | 9.5 | -62 | 0 | 0 | 0
220285 | 9.5-62.5 | 9.5 | -62.5 | 0 | 0 | 0
221006 | 9.5-63 | 9.5 | -63 | 0 | 0 | 0
221727 | 9.5-63.5 | 9.5 | -63.5 | 0 | 0 | 0
222448 | 9.5-64 | 9.5 | -64 | 0 | 0 | 0
223169 | 9.5-64.5 | 9.5 | -64.5 | 0 | 0 | 0
223890 | 9.5-65 | 9.5 | -65 | 0 | 0 | 0
224611 | 9.5-65.5 | 9.5 | -65.5 | 0 | 0 | 0
225332 | 9.5-66 | 9.5 | -66 | 0 | 0 | 0
226053 | 9.5-66.5 | 9.5 | -66.5 | 0 | 0 | 0
226774 | 9.5-67 | 9.5 | -67 | 0 | 0 | 0
227495 | 9.5-67.5 | 9.5 | -67.5 | 0 | 0 | 0
228216 | 9.5-68 | 9.5 | -68 | 0 | 0 | 0
228937 | 9.5-68.5 | 9.5 | -68.5 | 0 | 0 | 0
229658 | 9.5-69 | 9.5 | -69 | 0 | 0 | 0
230379 | 9.5-69.5 | 9.5 | -69.5 | 0 | 0 | 0
231100 | 9.5-70 | 9.5 | -70 | 0 | 0 | 0
231821 | 9.5-70.5 | 9.5 | -70.5 | 0 | 0 | 0
232542 | 9.5-71 | 9.5 | -71 | 0 | 0 | 0
233263 | 9.5-71.5 | 9.5 | -71.5 | 0 | 0 | 0
233984 | 9.5-72 | 9.5 | -72 | 0 | 0 | 0
234705 | 9.5-72.5 | 9.5 | -72.5 | 0 | 0 | 0
235426 | 9.5-73 | 9.5 | -73 | 0 | 0 | 0
236147 | 9.5-73.5 | 9.5 | -73.5 | 0 | 0 | 0
236868 | 9.5-74 | 9.5 | -74 | 0 | 0 | 0
237589 | 9.5-74.5 | 9.5 | -74.5 | 0 | 0 | 0
238310 | 9.5-75 | 9.5 | -75 | 0 | 0 | 0
239031 | 9.5-75.5 | 9.5 | -75.5 | 0 | 0 | 0
239752 | 9.5-76 | 9.5 | -76 | 0 | 0 | 0
240473 | 9.5-76.5 | 9.5 | -76.5 | 0 | 0 | 0
241194 | 9.5-77 | 9.5 | -77 | 0 | 0 | 0
241915 | 9.5-77.5 | 9.5 | -77.5 | 0 | 0 | 0
242636 | 9.5-78 | 9.5 | -78 | 0 | 0 | 0
243357 | 9.5-78.5 | 9.5 | -78.5 | 0 | 0 | 0
244078 | 9.5-79 | 9.5 | -79 | 0 | 0 | 0
244799 | 9.5-79.5 | 9.5 | -79.5 | 0 | 0 | 0
245520 | 9.5-80 | 9.5 | -80 | 0 | 0 | 0
246241 | 9.5-80.5 | 9.5 | -80.5 | 0 | 0 | 0
246962 | 9.5-81 | 9.5 | -81 | 0 | 0 | 0
247683 | 9.5-81.5 | 9.5 | -81.5 | 0 | 0 | 0
248404 | 9.5-82 | 9.5 | -82 | 0 | 0 | 0
249125 | 9.5-82.5 | 9.5 | -82.5 | 0 | 0 | 0
249846 | 9.5-83 | 9.5 | -83 | 0 | 0 | 0
250567 | 9.5-83.5 | 9.5 | -83.5 | 0 | 0 | 0
251288 | 9.5-84 | 9.5 | -84 | 0 | 0 | 0
252009 | 9.5-84.5 | 9.5 | -84.5 | 0 | 0 | 0
252730 | 9.5-85 | 9.5 | -85 | 0 | 0 | 0
253451 | 9.5-85.5 | 9.5 | -85.5 | 0 | 0 | 0
254172 | 9.5-86 | 9.5 | -86 | 0 | 0 | 0
254893 | 9.5-86.5 | 9.5 | -86.5 | 0 | 0 | 0
255614 | 9.5-87 | 9.5 | -87 | 0 | 0 | 0
256335 | 9.5-87.5 | 9.5 | -87.5 | 0 | 0 | 0
257056 | 9.5-88 | 9.5 | -88 | 0 | 0 | 0
257777 | 9.5-88.5 | 9.5 | -88.5 | 0 | 0 | 0
258498 | 9.5-89 | 9.5 | -89 | 0 | 0 | 0
259219 | 9.5-89.5 | 9.5 | -89.5 | 0 | 0 | 0
259940 | 9.5-90 | 9.5 | -90 | 0 | 0 | 0
215239 | 10-59 | 10 | -59 | 0 | 0 | 0
215960 | 10-59.5 | 10 | -59.5 | 0 | 0 | 0
216681 | 10-60 | 10 | -60 | 0 | 0 | 0
217402 | 10-60.5 | 10 | -60.5 | 0 | 0 | 0
218123 | 10-61 | 10 | -61 | 0 | 0 | 0
218844 | 10-61.5 | 10 | -61.5 | 0 | 0 | 0
219565 | 10-62 | 10 | -62 | 0 | 0 | 0
220286 | 10-62.5 | 10 | -62.5 | 0 | 0 | 0
221007 | 10-63 | 10 | -63 | 0 | 0 | 0
221728 | 10-63.5 | 10 | -63.5 | 0 | 0 | 0
222449 | 10-64 | 10 | -64 | 0 | 0 | 0
223170 | 10-64.5 | 10 | -64.5 | 0 | 0 | 0
223891 | 10-65 | 10 | -65 | 0 | 0 | 0
224612 | 10-65.5 | 10 | -65.5 | 0 | 0 | 0
225333 | 10-66 | 10 | -66 | 0 | 0 | 0
226054 | 10-66.5 | 10 | -66.5 | 0 | 0 | 0
226775 | 10-67 | 10 | -67 | 0 | 0 | 0
227496 | 10-67.5 | 10 | -67.5 | 0 | 0 | 0
228217 | 10-68 | 10 | -68 | 0 | 0 | 0
228938 | 10-68.5 | 10 | -68.5 | 0 | 0 | 0
229659 | 10-69 | 10 | -69 | 0 | 0 | 0
230380 | 10-69.5 | 10 | -69.5 | 0 | 0 | 0
231101 | 10-70 | 10 | -70 | 0 | 0 | 0
231822 | 10-70.5 | 10 | -70.5 | 0 | 0 | 0
232543 | 10-71 | 10 | -71 | 0 | 0 | 0
233264 | 10-71.5 | 10 | -71.5 | 0 | 0 | 0
233985 | 10-72 | 10 | -72 | 0 | 0 | 0
234706 | 10-72.5 | 10 | -72.5 | 0 | 0 | 0
235427 | 10-73 | 10 | -73 | 0 | 0 | 0
236148 | 10-73.5 | 10 | -73.5 | 0 | 0 | 0
236869 | 10-74 | 10 | -74 | 0 | 0 | 0
237590 | 10-74.5 | 10 | -74.5 | 0 | 0 | 0
238311 | 10-75 | 10 | -75 | 0 | 0 | 0
239032 | 10-75.5 | 10 | -75.5 | 0 | 0 | 0
239753 | 10-76 | 10 | -76 | 0 | 0 | 0
240474 | 10-76.5 | 10 | -76.5 | 0 | 0 | 0
241195 | 10-77 | 10 | -77 | 0 | 0 | 0
241916 | 10-77.5 | 10 | -77.5 | 0 | 0 | 0
242637 | 10-78 | 10 | -78 | 0 | 0 | 0
243358 | 10-78.5 | 10 | -78.5 | 0 | 0 | 0
244079 | 10-79 | 10 | -79 | 0 | 0 | 0
244800 | 10-79.5 | 10 | -79.5 | 0 | 0 | 0
245521 | 10-80 | 10 | -80 | 0 | 0 | 0
246242 | 10-80.5 | 10 | -80.5 | 0 | 0 | 0
246963 | 10-81 | 10 | -81 | 0 | 0 | 0
247684 | 10-81.5 | 10 | -81.5 | 0 | 0 | 0
248405 | 10-82 | 10 | -82 | 0 | 0 | 0
249126 | 10-82.5 | 10 | -82.5 | 0 | 0 | 0
249847 | 10-83 | 10 | -83 | 0 | 0 | 0
250568 | 10-83.5 | 10 | -83.5 | 0 | 0 | 0
251289 | 10-84 | 10 | -84 | 0 | 0 | 0
252010 | 10-84.5 | 10 | -84.5 | 0 | 0 | 0
252731 | 10-85 | 10 | -85 | 0 | 0 | 0
253452 | 10-85.5 | 10 | -85.5 | 0 | 0 | 0
254173 | 10-86 | 10 | -86 | 0 | 0 | 0
254894 | 10-86.5 | 10 | -86.5 | 0 | 0 | 0
255615 | 10-87 | 10 | -87 | 0 | 0 | 0
256336 | 10-87.5 | 10 | -87.5 | 0 | 0 | 0
257057 | 10-88 | 10 | -88 | 0 | 0 | 0
257778 | 10-88.5 | 10 | -88.5 | 0 | 0 | 0
258499 | 10-89 | 10 | -89 | 0 | 0 | 0
259220 | 10-89.5 | 10 | -89.5 | 0 | 0 | 0
259941 | 10-90 | 10 | -90 | 0 | 0 | 0
215240 | 10.5-59 | 10.5 | -59 | 0 | 0 | 0
215961 | 10.5-59.5 | 10.5 | -59.5 | 0 | 0 | 0
216682 | 10.5-60 | 10.5 | -60 | 0 | 0 | 0
217403 | 10.5-60.5 | 10.5 | -60.5 | 0 | 0 | 0
218124 | 10.5-61 | 10.5 | -61 | 0 | 0 | 0
218845 | 10.5-61.5 | 10.5 | -61.5 | 0 | 0 | 0
219566 | 10.5-62 | 10.5 | -62 | 0 | 0 | 0
220287 | 10.5-62.5 | 10.5 | -62.5 | 0 | 0 | 0
221008 | 10.5-63 | 10.5 | -63 | 0 | 0 | 0
221729 | 10.5-63.5 | 10.5 | -63.5 | 0 | 0 | 0
222450 | 10.5-64 | 10.5 | -64 | 0 | 0 | 0
223171 | 10.5-64.5 | 10.5 | -64.5 | 0 | 0 | 0
223892 | 10.5-65 | 10.5 | -65 | 0 | 0 | 0
224613 | 10.5-65.5 | 10.5 | -65.5 | 0 | 0 | 0
225334 | 10.5-66 | 10.5 | -66 | 0 | 0 | 0
226055 | 10.5-66.5 | 10.5 | -66.5 | 0 | 0 | 0
226776 | 10.5-67 | 10.5 | -67 | 0 | 0 | 0
227497 | 10.5-67.5 | 10.5 | -67.5 | 0 | 0 | 0
228218 | 10.5-68 | 10.5 | -68 | 0 | 0 | 0
228939 | 10.5-68.5 | 10.5 | -68.5 | 0 | 0 | 0
229660 | 10.5-69 | 10.5 | -69 | 0 | 0 | 0
230381 | 10.5-69.5 | 10.5 | -69.5 | 0 | 0 | 0
231102 | 10.5-70 | 10.5 | -70 | 0 | 0 | 0
231823 | 10.5-70.5 | 10.5 | -70.5 | 0 | 0 | 0
232544 | 10.5-71 | 10.5 | -71 | 0 | 0 | 0
233265 | 10.5-71.5 | 10.5 | -71.5 | 0 | 0 | 0
233986 | 10.5-72 | 10.5 | -72 | 0 | 0 | 0
234707 | 10.5-72.5 | 10.5 | -72.5 | 0 | 0 | 0
235428 | 10.5-73 | 10.5 | -73 | 0 | 0 | 0
236149 | 10.5-73.5 | 10.5 | -73.5 | 0 | 0 | 0
236870 | 10.5-74 | 10.5 | -74 | 0 | 0 | 0
237591 | 10.5-74.5 | 10.5 | -74.5 | 0 | 0 | 0
238312 | 10.5-75 | 10.5 | -75 | 0 | 0 | 0
239033 | 10.5-75.5 | 10.5 | -75.5 | 0 | 0 | 0
239754 | 10.5-76 | 10.5 | -76 | 0 | 0 | 0
240475 | 10.5-76.5 | 10.5 | -76.5 | 0 | 0 | 0
241196 | 10.5-77 | 10.5 | -77 | 0 | 0 | 0
241917 | 10.5-77.5 | 10.5 | -77.5 | 0 | 0 | 0
242638 | 10.5-78 | 10.5 | -78 | 0 | 0 | 0
243359 | 10.5-78.5 | 10.5 | -78.5 | 0 | 0 | 0
244080 | 10.5-79 | 10.5 | -79 | 0 | 0 | 0
244801 | 10.5-79.5 | 10.5 | -79.5 | 0 | 0 | 0
245522 | 10.5-80 | 10.5 | -80 | 0 | 0 | 0
246243 | 10.5-80.5 | 10.5 | -80.5 | 0 | 0 | 0
246964 | 10.5-81 | 10.5 | -81 | 0 | 0 | 0
247685 | 10.5-81.5 | 10.5 | -81.5 | 0 | 0 | 0
248406 | 10.5-82 | 10.5 | -82 | 0 | 0 | 0
249127 | 10.5-82.5 | 10.5 | -82.5 | 0 | 0 | 0
249848 | 10.5-83 | 10.5 | -83 | 0 | 0 | 0
250569 | 10.5-83.5 | 10.5 | -83.5 | 0 | 0 | 0
251290 | 10.5-84 | 10.5 | -84 | 0 | 0 | 0
252011 | 10.5-84.5 | 10.5 | -84.5 | 0 | 0 | 0
252732 | 10.5-85 | 10.5 | -85 | 0 | 0 | 0
253453 | 10.5-85.5 | 10.5 | -85.5 | 0 | 0 | 0
254174 | 10.5-86 | 10.5 | -86 | 0 | 0 | 0
254895 | 10.5-86.5 | 10.5 | -86.5 | 0 | 0 | 0
255616 | 10.5-87 | 10.5 | -87 | 0 | 0 | 0
256337 | 10.5-87.5 | 10.5 | -87.5 | 0 | 0 | 0
257058 | 10.5-88 | 10.5 | -88 | 0 | 0 | 0
257779 | 10.5-88.5 | 10.5 | -88.5 | 0 | 0 | 0
258500 | 10.5-89 | 10.5 | -89 | 0 | 0 | 0
259221 | 10.5-89.5 | 10.5 | -89.5 | 0 | 0 | 0
259942 | 10.5-90 | 10.5 | -90 | 0 | 0 | 0
215241 | 11-59 | 11 | -59 | 0 | 0 | 0
215962 | 11-59.5 | 11 | -59.5 | 0 | 0 | 0
216683 | 11-60 | 11 | -60 | 0 | 0 | 0
217404 | 11-60.5 | 11 | -60.5 | 0 | 0 | 0
218125 | 11-61 | 11 | -61 | 0 | 0 | 0
218846 | 11-61.5 | 11 | -61.5 | 0 | 0 | 0
219567 | 11-62 | 11 | -62 | 0 | 0 | 0
220288 | 11-62.5 | 11 | -62.5 | 0 | 0 | 0
221009 | 11-63 | 11 | -63 | 0 | 0 | 0
221730 | 11-63.5 | 11 | -63.5 | 0 | 0 | 0
222451 | 11-64 | 11 | -64 | 0 | 0 | 0
223172 | 11-64.5 | 11 | -64.5 | 0 | 0 | 0
223893 | 11-65 | 11 | -65 | 0 | 0 | 0
224614 | 11-65.5 | 11 | -65.5 | 0 | 0 | 0
225335 | 11-66 | 11 | -66 | 0 | 0 | 0
226056 | 11-66.5 | 11 | -66.5 | 0 | 0 | 0
226777 | 11-67 | 11 | -67 | 0 | 0 | 0
227498 | 11-67.5 | 11 | -67.5 | 0 | 0 | 0
228219 | 11-68 | 11 | -68 | 0 | 0 | 0
228940 | 11-68.5 | 11 | -68.5 | 0 | 0 | 0
229661 | 11-69 | 11 | -69 | 0 | 0 | 0
230382 | 11-69.5 | 11 | -69.5 | 0 | 0 | 0
231103 | 11-70 | 11 | -70 | 0 | 0 | 0
231824 | 11-70.5 | 11 | -70.5 | 0 | 0 | 0
232545 | 11-71 | 11 | -71 | 0 | 0 | 0
233266 | 11-71.5 | 11 | -71.5 | 0 | 0 | 0
233987 | 11-72 | 11 | -72 | 0 | 0 | 0
234708 | 11-72.5 | 11 | -72.5 | 0 | 0 | 0
235429 | 11-73 | 11 | -73 | 0 | 0 | 0
236150 | 11-73.5 | 11 | -73.5 | 0 | 0 | 0
236871 | 11-74 | 11 | -74 | 0 | 0 | 0
237592 | 11-74.5 | 11 | -74.5 | 0 | 0 | 0
238313 | 11-75 | 11 | -75 | 0 | 0 | 0
239034 | 11-75.5 | 11 | -75.5 | 0 | 0 | 0
239755 | 11-76 | 11 | -76 | 0 | 0 | 0
240476 | 11-76.5 | 11 | -76.5 | 0 | 0 | 0
241197 | 11-77 | 11 | -77 | 0 | 0 | 0
241918 | 11-77.5 | 11 | -77.5 | 0 | 0 | 0
242639 | 11-78 | 11 | -78 | 0 | 0 | 0
243360 | 11-78.5 | 11 | -78.5 | 0 | 0 | 0
244081 | 11-79 | 11 | -79 | 0 | 0 | 0
244802 | 11-79.5 | 11 | -79.5 | 0 | 0 | 0
245523 | 11-80 | 11 | -80 | 0 | 0 | 0
246244 | 11-80.5 | 11 | -80.5 | 0 | 0 | 0
246965 | 11-81 | 11 | -81 | 0 | 0 | 0
247686 | 11-81.5 | 11 | -81.5 | 0 | 0 | 0
248407 | 11-82 | 11 | -82 | 0 | 0 | 0
249128 | 11-82.5 | 11 | -82.5 | 0 | 0 | 0
249849 | 11-83 | 11 | -83 | 0 | 0 | 0
250570 | 11-83.5 | 11 | -83.5 | 0 | 0 | 0
251291 | 11-84 | 11 | -84 | 0 | 0 | 0
252012 | 11-84.5 | 11 | -84.5 | 0 | 0 | 0
252733 | 11-85 | 11 | -85 | 0 | 0 | 0
253454 | 11-85.5 | 11 | -85.5 | 0 | 0 | 0
254175 | 11-86 | 11 | -86 | 0 | 0 | 0
254896 | 11-86.5 | 11 | -86.5 | 0 | 0 | 0
255617 | 11-87 | 11 | -87 | 0 | 0 | 0
256338 | 11-87.5 | 11 | -87.5 | 0 | 0 | 0
257059 | 11-88 | 11 | -88 | 0 | 0 | 0
257780 | 11-88.5 | 11 | -88.5 | 0 | 0 | 0
258501 | 11-89 | 11 | -89 | 0 | 0 | 0
259222 | 11-89.5 | 11 | -89.5 | 0 | 0 | 0
259943 | 11-90 | 11 | -90 | 0 | 0 | 0
215242 | 11.5-59 | 11.5 | -59 | 0 | 0 | 0
215963 | 11.5-59.5 | 11.5 | -59.5 | 0 | 0 | 0
216684 | 11.5-60 | 11.5 | -60 | 0 | 0 | 0
217405 | 11.5-60.5 | 11.5 | -60.5 | 0 | 0 | 0
218126 | 11.5-61 | 11.5 | -61 | 0 | 0 | 0
218847 | 11.5-61.5 | 11.5 | -61.5 | 0 | 0 | 0
219568 | 11.5-62 | 11.5 | -62 | 0 | 0 | 0
220289 | 11.5-62.5 | 11.5 | -62.5 | 0 | 0 | 0
221010 | 11.5-63 | 11.5 | -63 | 0 | 0 | 0
221731 | 11.5-63.5 | 11.5 | -63.5 | 0 | 0 | 0
222452 | 11.5-64 | 11.5 | -64 | 0 | 0 | 0
223173 | 11.5-64.5 | 11.5 | -64.5 | 0 | 0 | 0
223894 | 11.5-65 | 11.5 | -65 | 0 | 0 | 0
224615 | 11.5-65.5 | 11.5 | -65.5 | 0 | 0 | 0
225336 | 11.5-66 | 11.5 | -66 | 0 | 0 | 0
226057 | 11.5-66.5 | 11.5 | -66.5 | 0 | 0 | 0
226778 | 11.5-67 | 11.5 | -67 | 0 | 0 | 0
227499 | 11.5-67.5 | 11.5 | -67.5 | 0 | 0 | 0
228220 | 11.5-68 | 11.5 | -68 | 0 | 0 | 0
228941 | 11.5-68.5 | 11.5 | -68.5 | 0 | 0 | 0
229662 | 11.5-69 | 11.5 | -69 | 0 | 0 | 0
230383 | 11.5-69.5 | 11.5 | -69.5 | 0 | 0 | 0
231104 | 11.5-70 | 11.5 | -70 | 0 | 0 | 0
231825 | 11.5-70.5 | 11.5 | -70.5 | 0 | 0 | 0
232546 | 11.5-71 | 11.5 | -71 | 0 | 0 | 0
233267 | 11.5-71.5 | 11.5 | -71.5 | 0 | 0 | 0
233988 | 11.5-72 | 11.5 | -72 | 0 | 0 | 0
234709 | 11.5-72.5 | 11.5 | -72.5 | 0 | 0 | 0
235430 | 11.5-73 | 11.5 | -73 | 0 | 0 | 0
236151 | 11.5-73.5 | 11.5 | -73.5 | 0 | 0 | 0
236872 | 11.5-74 | 11.5 | -74 | 0 | 0 | 0
237593 | 11.5-74.5 | 11.5 | -74.5 | 0 | 0 | 0
238314 | 11.5-75 | 11.5 | -75 | 0 | 0 | 0
239035 | 11.5-75.5 | 11.5 | -75.5 | 0 | 0 | 0
239756 | 11.5-76 | 11.5 | -76 | 0 | 0 | 0
240477 | 11.5-76.5 | 11.5 | -76.5 | 0 | 0 | 0
241198 | 11.5-77 | 11.5 | -77 | 0 | 0 | 0
241919 | 11.5-77.5 | 11.5 | -77.5 | 0 | 0 | 0
242640 | 11.5-78 | 11.5 | -78 | 0 | 0 | 0
243361 | 11.5-78.5 | 11.5 | -78.5 | 0 | 0 | 0
244082 | 11.5-79 | 11.5 | -79 | 0 | 0 | 0
244803 | 11.5-79.5 | 11.5 | -79.5 | 0 | 0 | 0
245524 | 11.5-80 | 11.5 | -80 | 0 | 0 | 0
246245 | 11.5-80.5 | 11.5 | -80.5 | 0 | 0 | 0
246966 | 11.5-81 | 11.5 | -81 | 0 | 0 | 0
247687 | 11.5-81.5 | 11.5 | -81.5 | 0 | 0 | 0
248408 | 11.5-82 | 11.5 | -82 | 0 | 0 | 0
249129 | 11.5-82.5 | 11.5 | -82.5 | 0 | 0 | 0
249850 | 11.5-83 | 11.5 | -83 | 0 | 0 | 0
250571 | 11.5-83.5 | 11.5 | -83.5 | 0 | 0 | 0
251292 | 11.5-84 | 11.5 | -84 | 0 | 0 | 0
252013 | 11.5-84.5 | 11.5 | -84.5 | 0 | 0 | 0
252734 | 11.5-85 | 11.5 | -85 | 0 | 0 | 0
253455 | 11.5-85.5 | 11.5 | -85.5 | 0 | 0 | 0
254176 | 11.5-86 | 11.5 | -86 | 0 | 0 | 0
254897 | 11.5-86.5 | 11.5 | -86.5 | 0 | 0 | 0
255618 | 11.5-87 | 11.5 | -87 | 0 | 0 | 0
256339 | 11.5-87.5 | 11.5 | -87.5 | 0 | 0 | 0
257060 | 11.5-88 | 11.5 | -88 | 0 | 0 | 0
257781 | 11.5-88.5 | 11.5 | -88.5 | 0 | 0 | 0
258502 | 11.5-89 | 11.5 | -89 | 0 | 0 | 0
259223 | 11.5-89.5 | 11.5 | -89.5 | 0 | 0 | 0
259944 | 11.5-90 | 11.5 | -90 | 0 | 0 | 0
215243 | 12-59 | 12 | -59 | 0 | 0 | 0
215964 | 12-59.5 | 12 | -59.5 | 0 | 0 | 0
216685 | 12-60 | 12 | -60 | 0 | 0 | 0
217406 | 12-60.5 | 12 | -60.5 | 0 | 0 | 0
218127 | 12-61 | 12 | -61 | 0 | 0 | 0
218848 | 12-61.5 | 12 | -61.5 | 0 | 0 | 0
219569 | 12-62 | 12 | -62 | 0 | 0 | 0
220290 | 12-62.5 | 12 | -62.5 | 0 | 0 | 0
221011 | 12-63 | 12 | -63 | 0 | 0 | 0
221732 | 12-63.5 | 12 | -63.5 | 0 | 0 | 0
222453 | 12-64 | 12 | -64 | 0 | 0 | 0
223174 | 12-64.5 | 12 | -64.5 | 0 | 0 | 0
223895 | 12-65 | 12 | -65 | 0 | 0 | 0
224616 | 12-65.5 | 12 | -65.5 | 0 | 0 | 0
225337 | 12-66 | 12 | -66 | 0 | 0 | 0
226058 | 12-66.5 | 12 | -66.5 | 0 | 0 | 0
226779 | 12-67 | 12 | -67 | 0 | 0 | 0
227500 | 12-67.5 | 12 | -67.5 | 0 | 0 | 0
228221 | 12-68 | 12 | -68 | 0 | 0 | 0
228942 | 12-68.5 | 12 | -68.5 | 0 | 0 | 0
229663 | 12-69 | 12 | -69 | 0 | 0 | 0
230384 | 12-69.5 | 12 | -69.5 | 0 | 0 | 0
231105 | 12-70 | 12 | -70 | 0 | 0 | 0
231826 | 12-70.5 | 12 | -70.5 | 0 | 0 | 0
232547 | 12-71 | 12 | -71 | 0 | 0 | 0
233268 | 12-71.5 | 12 | -71.5 | 0 | 0 | 0
233989 | 12-72 | 12 | -72 | 0 | 0 | 0
234710 | 12-72.5 | 12 | -72.5 | 0 | 0 | 0
235431 | 12-73 | 12 | -73 | 0 | 0 | 0
236152 | 12-73.5 | 12 | -73.5 | 0 | 0 | 0
236873 | 12-74 | 12 | -74 | 0 | 0 | 0
237594 | 12-74.5 | 12 | -74.5 | 0 | 0 | 0
238315 | 12-75 | 12 | -75 | 0 | 0 | 0
239036 | 12-75.5 | 12 | -75.5 | 0 | 0 | 0
239757 | 12-76 | 12 | -76 | 0 | 0 | 0
240478 | 12-76.5 | 12 | -76.5 | 0 | 0 | 0
241199 | 12-77 | 12 | -77 | 0 | 0 | 0
241920 | 12-77.5 | 12 | -77.5 | 0 | 0 | 0
242641 | 12-78 | 12 | -78 | 0 | 0 | 0
243362 | 12-78.5 | 12 | -78.5 | 0 | 0 | 0
244083 | 12-79 | 12 | -79 | 0 | 0 | 0
244804 | 12-79.5 | 12 | -79.5 | 0 | 0 | 0
245525 | 12-80 | 12 | -80 | 0 | 0 | 0
246246 | 12-80.5 | 12 | -80.5 | 0 | 0 | 0
246967 | 12-81 | 12 | -81 | 0 | 0 | 0
247688 | 12-81.5 | 12 | -81.5 | 0 | 0 | 0
248409 | 12-82 | 12 | -82 | 0 | 0 | 0
249130 | 12-82.5 | 12 | -82.5 | 0 | 0 | 0
249851 | 12-83 | 12 | -83 | 0 | 0 | 0
250572 | 12-83.5 | 12 | -83.5 | 0 | 0 | 0
251293 | 12-84 | 12 | -84 | 0 | 0 | 0
252014 | 12-84.5 | 12 | -84.5 | 0 | 0 | 0
252735 | 12-85 | 12 | -85 | 0 | 0 | 0
253456 | 12-85.5 | 12 | -85.5 | 0 | 0 | 0
254177 | 12-86 | 12 | -86 | 0 | 0 | 0
254898 | 12-86.5 | 12 | -86.5 | 0 | 0 | 0
255619 | 12-87 | 12 | -87 | 0 | 0 | 0
256340 | 12-87.5 | 12 | -87.5 | 0 | 0 | 0
257061 | 12-88 | 12 | -88 | 0 | 0 | 0
257782 | 12-88.5 | 12 | -88.5 | 0 | 0 | 0
258503 | 12-89 | 12 | -89 | 0 | 0 | 0
259224 | 12-89.5 | 12 | -89.5 | 0 | 0 | 0
259945 | 12-90 | 12 | -90 | 0 | 0 | 0
215244 | 12.5-59 | 12.5 | -59 | 0 | 0 | 0
215965 | 12.5-59.5 | 12.5 | -59.5 | 0 | 0 | 0
216686 | 12.5-60 | 12.5 | -60 | 0 | 0 | 0
217407 | 12.5-60.5 | 12.5 | -60.5 | 0 | 0 | 0
218128 | 12.5-61 | 12.5 | -61 | 0 | 0 | 0
218849 | 12.5-61.5 | 12.5 | -61.5 | 0 | 0 | 0
219570 | 12.5-62 | 12.5 | -62 | 0 | 0 | 0
220291 | 12.5-62.5 | 12.5 | -62.5 | 0 | 0 | 0
221012 | 12.5-63 | 12.5 | -63 | 0 | 0 | 0
221733 | 12.5-63.5 | 12.5 | -63.5 | 0 | 0 | 0
222454 | 12.5-64 | 12.5 | -64 | 0 | 0 | 0
223175 | 12.5-64.5 | 12.5 | -64.5 | 0 | 0 | 0
223896 | 12.5-65 | 12.5 | -65 | 0 | 0 | 0
224617 | 12.5-65.5 | 12.5 | -65.5 | 0 | 0 | 0
225338 | 12.5-66 | 12.5 | -66 | 0 | 0 | 0
226059 | 12.5-66.5 | 12.5 | -66.5 | 0 | 0 | 0
226780 | 12.5-67 | 12.5 | -67 | 0 | 0 | 0
227501 | 12.5-67.5 | 12.5 | -67.5 | 0 | 0 | 0
228222 | 12.5-68 | 12.5 | -68 | 0 | 0 | 0
228943 | 12.5-68.5 | 12.5 | -68.5 | 0 | 0 | 0
229664 | 12.5-69 | 12.5 | -69 | 0 | 0 | 0
230385 | 12.5-69.5 | 12.5 | -69.5 | 0 | 0 | 0
231106 | 12.5-70 | 12.5 | -70 | 0 | 0 | 0
231827 | 12.5-70.5 | 12.5 | -70.5 | 0 | 0 | 0
232548 | 12.5-71 | 12.5 | -71 | 0 | 0 | 0
233269 | 12.5-71.5 | 12.5 | -71.5 | 0 | 0 | 0
233990 | 12.5-72 | 12.5 | -72 | 0 | 0 | 0
234711 | 12.5-72.5 | 12.5 | -72.5 | 0 | 0 | 0
235432 | 12.5-73 | 12.5 | -73 | 0 | 0 | 0
236153 | 12.5-73.5 | 12.5 | -73.5 | 0 | 0 | 0
236874 | 12.5-74 | 12.5 | -74 | 0 | 0 | 0
237595 | 12.5-74.5 | 12.5 | -74.5 | 0 | 0 | 0
238316 | 12.5-75 | 12.5 | -75 | 0 | 0 | 0
239037 | 12.5-75.5 | 12.5 | -75.5 | 0 | 0 | 0
239758 | 12.5-76 | 12.5 | -76 | 0 | 0 | 0
240479 | 12.5-76.5 | 12.5 | -76.5 | 0 | 0 | 0
241200 | 12.5-77 | 12.5 | -77 | 0 | 0 | 0
241921 | 12.5-77.5 | 12.5 | -77.5 | 0 | 0 | 0
242642 | 12.5-78 | 12.5 | -78 | 0 | 0 | 0
243363 | 12.5-78.5 | 12.5 | -78.5 | 0 | 0 | 0
244084 | 12.5-79 | 12.5 | -79 | 0 | 0 | 0
244805 | 12.5-79.5 | 12.5 | -79.5 | 0 | 0 | 0
245526 | 12.5-80 | 12.5 | -80 | 0 | 0 | 0
246247 | 12.5-80.5 | 12.5 | -80.5 | 0 | 0 | 0
246968 | 12.5-81 | 12.5 | -81 | 0 | 0 | 0
247689 | 12.5-81.5 | 12.5 | -81.5 | 0 | 0 | 0
248410 | 12.5-82 | 12.5 | -82 | 0 | 0 | 0
249131 | 12.5-82.5 | 12.5 | -82.5 | 0 | 0 | 0
249852 | 12.5-83 | 12.5 | -83 | 0 | 0 | 0
250573 | 12.5-83.5 | 12.5 | -83.5 | 0 | 0 | 0
251294 | 12.5-84 | 12.5 | -84 | 0 | 0 | 0
252015 | 12.5-84.5 | 12.5 | -84.5 | 0 | 0 | 0
252736 | 12.5-85 | 12.5 | -85 | 0 | 0 | 0
253457 | 12.5-85.5 | 12.5 | -85.5 | 0 | 0 | 0
254178 | 12.5-86 | 12.5 | -86 | 0 | 0 | 0
254899 | 12.5-86.5 | 12.5 | -86.5 | 0 | 0 | 0
255620 | 12.5-87 | 12.5 | -87 | 0 | 0 | 0
256341 | 12.5-87.5 | 12.5 | -87.5 | 0 | 0 | 0
257062 | 12.5-88 | 12.5 | -88 | 0 | 0 | 0
257783 | 12.5-88.5 | 12.5 | -88.5 | 0 | 0 | 0
258504 | 12.5-89 | 12.5 | -89 | 0 | 0 | 0
259225 | 12.5-89.5 | 12.5 | -89.5 | 0 | 0 | 0
259946 | 12.5-90 | 12.5 | -90 | 0 | 0 | 0
215245 | 13-59 | 13 | -59 | 0 | 0 | 0
215966 | 13-59.5 | 13 | -59.5 | 0 | 0 | 0
216687 | 13-60 | 13 | -60 | 0 | 0 | 0
217408 | 13-60.5 | 13 | -60.5 | 0 | 0 | 0
218129 | 13-61 | 13 | -61 | 0 | 0 | 0
218850 | 13-61.5 | 13 | -61.5 | 0 | 0 | 0
219571 | 13-62 | 13 | -62 | 0 | 0 | 0
220292 | 13-62.5 | 13 | -62.5 | 0 | 0 | 0
221013 | 13-63 | 13 | -63 | 0 | 0 | 0
221734 | 13-63.5 | 13 | -63.5 | 0 | 0 | 0
222455 | 13-64 | 13 | -64 | 0 | 0 | 0
223176 | 13-64.5 | 13 | -64.5 | 0 | 0 | 0
223897 | 13-65 | 13 | -65 | 0 | 0 | 0
224618 | 13-65.5 | 13 | -65.5 | 0 | 0 | 0
225339 | 13-66 | 13 | -66 | 0 | 0 | 0
226060 | 13-66.5 | 13 | -66.5 | 0 | 0 | 0
226781 | 13-67 | 13 | -67 | 0 | 0 | 0
227502 | 13-67.5 | 13 | -67.5 | 0 | 0 | 0
228223 | 13-68 | 13 | -68 | 0 | 0 | 0
228944 | 13-68.5 | 13 | -68.5 | 0 | 0 | 0
229665 | 13-69 | 13 | -69 | 0 | 0 | 0
230386 | 13-69.5 | 13 | -69.5 | 0 | 0 | 0
231107 | 13-70 | 13 | -70 | 0 | 0 | 0
231828 | 13-70.5 | 13 | -70.5 | 0 | 0 | 0
232549 | 13-71 | 13 | -71 | 0 | 0 | 0
233270 | 13-71.5 | 13 | -71.5 | 0 | 0 | 0
233991 | 13-72 | 13 | -72 | 0 | 0 | 0
234712 | 13-72.5 | 13 | -72.5 | 0 | 0 | 0
235433 | 13-73 | 13 | -73 | 0 | 0 | 0
236154 | 13-73.5 | 13 | -73.5 | 0 | 0 | 0
236875 | 13-74 | 13 | -74 | 0 | 0 | 0
237596 | 13-74.5 | 13 | -74.5 | 0 | 0 | 0
238317 | 13-75 | 13 | -75 | 0 | 0 | 0
239038 | 13-75.5 | 13 | -75.5 | 0 | 0 | 0
239759 | 13-76 | 13 | -76 | 0 | 0 | 0
240480 | 13-76.5 | 13 | -76.5 | 0 | 0 | 0
241201 | 13-77 | 13 | -77 | 0 | 0 | 0
241922 | 13-77.5 | 13 | -77.5 | 0 | 0 | 0
242643 | 13-78 | 13 | -78 | 0 | 0 | 0
243364 | 13-78.5 | 13 | -78.5 | 0 | 0 | 0
244085 | 13-79 | 13 | -79 | 0 | 0 | 0
244806 | 13-79.5 | 13 | -79.5 | 0 | 0 | 0
245527 | 13-80 | 13 | -80 | 0 | 0 | 0
246248 | 13-80.5 | 13 | -80.5 | 0 | 0 | 0
246969 | 13-81 | 13 | -81 | 0 | 0 | 0
247690 | 13-81.5 | 13 | -81.5 | 0 | 0 | 0
248411 | 13-82 | 13 | -82 | 0 | 0 | 0
249132 | 13-82.5 | 13 | -82.5 | 0 | 0 | 0
249853 | 13-83 | 13 | -83 | 0 | 0 | 0
250574 | 13-83.5 | 13 | -83.5 | 0 | 0 | 0
251295 | 13-84 | 13 | -84 | 0 | 0 | 0
252016 | 13-84.5 | 13 | -84.5 | 0 | 0 | 0
252737 | 13-85 | 13 | -85 | 0 | 0 | 0
253458 | 13-85.5 | 13 | -85.5 | 0 | 0 | 0
254179 | 13-86 | 13 | -86 | 0 | 0 | 0
254900 | 13-86.5 | 13 | -86.5 | 0 | 0 | 0
255621 | 13-87 | 13 | -87 | 0 | 0 | 0
256342 | 13-87.5 | 13 | -87.5 | 0 | 0 | 0
257063 | 13-88 | 13 | -88 | 0 | 0 | 0
257784 | 13-88.5 | 13 | -88.5 | 0 | 0 | 0
258505 | 13-89 | 13 | -89 | 0 | 0 | 0
259226 | 13-89.5 | 13 | -89.5 | 0 | 0 | 0
259947 | 13-90 | 13 | -90 | 0 | 0 | 0
215246 | 13.5-59 | 13.5 | -59 | 0 | 0 | 0
215967 | 13.5-59.5 | 13.5 | -59.5 | 0 | 0 | 0
216688 | 13.5-60 | 13.5 | -60 | 0 | 0 | 0
217409 | 13.5-60.5 | 13.5 | -60.5 | 0 | 0 | 0
218130 | 13.5-61 | 13.5 | -61 | 0 | 0 | 0
218851 | 13.5-61.5 | 13.5 | -61.5 | 0 | 0 | 0
219572 | 13.5-62 | 13.5 | -62 | 0 | 0 | 0
220293 | 13.5-62.5 | 13.5 | -62.5 | 0 | 0 | 0
221014 | 13.5-63 | 13.5 | -63 | 0 | 0 | 0
221735 | 13.5-63.5 | 13.5 | -63.5 | 0 | 0 | 0
222456 | 13.5-64 | 13.5 | -64 | 0 | 0 | 0
223177 | 13.5-64.5 | 13.5 | -64.5 | 0 | 0 | 0
223898 | 13.5-65 | 13.5 | -65 | 0 | 0 | 0
224619 | 13.5-65.5 | 13.5 | -65.5 | 0 | 0 | 0
225340 | 13.5-66 | 13.5 | -66 | 0 | 0 | 0
226061 | 13.5-66.5 | 13.5 | -66.5 | 0 | 0 | 0
226782 | 13.5-67 | 13.5 | -67 | 0 | 0 | 0
227503 | 13.5-67.5 | 13.5 | -67.5 | 0 | 0 | 0
228224 | 13.5-68 | 13.5 | -68 | 0 | 0 | 0
228945 | 13.5-68.5 | 13.5 | -68.5 | 0 | 0 | 0
229666 | 13.5-69 | 13.5 | -69 | 0 | 0 | 0
230387 | 13.5-69.5 | 13.5 | -69.5 | 0 | 0 | 0
231108 | 13.5-70 | 13.5 | -70 | 0 | 0 | 0
231829 | 13.5-70.5 | 13.5 | -70.5 | 0 | 0 | 0
232550 | 13.5-71 | 13.5 | -71 | 0 | 0 | 0
233271 | 13.5-71.5 | 13.5 | -71.5 | 0 | 0 | 0
233992 | 13.5-72 | 13.5 | -72 | 0 | 0 | 0
234713 | 13.5-72.5 | 13.5 | -72.5 | 0 | 0 | 0
235434 | 13.5-73 | 13.5 | -73 | 0 | 0 | 0
236155 | 13.5-73.5 | 13.5 | -73.5 | 0 | 0 | 0
236876 | 13.5-74 | 13.5 | -74 | 0 | 0 | 0
237597 | 13.5-74.5 | 13.5 | -74.5 | 0 | 0 | 0
238318 | 13.5-75 | 13.5 | -75 | 0 | 0 | 0
239039 | 13.5-75.5 | 13.5 | -75.5 | 0 | 0 | 0
239760 | 13.5-76 | 13.5 | -76 | 0 | 0 | 0
240481 | 13.5-76.5 | 13.5 | -76.5 | 0 | 0 | 0
241202 | 13.5-77 | 13.5 | -77 | 0 | 0 | 0
241923 | 13.5-77.5 | 13.5 | -77.5 | 0 | 0 | 0
242644 | 13.5-78 | 13.5 | -78 | 0 | 0 | 0
243365 | 13.5-78.5 | 13.5 | -78.5 | 0 | 0 | 0
244086 | 13.5-79 | 13.5 | -79 | 0 | 0 | 0
244807 | 13.5-79.5 | 13.5 | -79.5 | 0 | 0 | 0
245528 | 13.5-80 | 13.5 | -80 | 0 | 0 | 0
246249 | 13.5-80.5 | 13.5 | -80.5 | 0 | 0 | 0
246970 | 13.5-81 | 13.5 | -81 | 0 | 0 | 0
247691 | 13.5-81.5 | 13.5 | -81.5 | 0 | 0 | 0
248412 | 13.5-82 | 13.5 | -82 | 0 | 0 | 0
249133 | 13.5-82.5 | 13.5 | -82.5 | 0 | 0 | 0
249854 | 13.5-83 | 13.5 | -83 | 0 | 0 | 0
250575 | 13.5-83.5 | 13.5 | -83.5 | 0 | 0 | 0
251296 | 13.5-84 | 13.5 | -84 | 0 | 0 | 0
252017 | 13.5-84.5 | 13.5 | -84.5 | 0 | 0 | 0
252738 | 13.5-85 | 13.5 | -85 | 0 | 0 | 0
253459 | 13.5-85.5 | 13.5 | -85.5 | 0 | 0 | 0
254180 | 13.5-86 | 13.5 | -86 | 0 | 0 | 0
254901 | 13.5-86.5 | 13.5 | -86.5 | 0 | 0 | 0
255622 | 13.5-87 | 13.5 | -87 | 0 | 0 | 0
256343 | 13.5-87.5 | 13.5 | -87.5 | 0 | 0 | 0
257064 | 13.5-88 | 13.5 | -88 | 0 | 0 | 0
257785 | 13.5-88.5 | 13.5 | -88.5 | 0 | 0 | 0
258506 | 13.5-89 | 13.5 | -89 | 0 | 0 | 0
259227 | 13.5-89.5 | 13.5 | -89.5 | 0 | 0 | 0
259948 | 13.5-90 | 13.5 | -90 | 0 | 0 | 0
215247 | 14-59 | 14 | -59 | 0 | 0 | 0
215968 | 14-59.5 | 14 | -59.5 | 0 | 0 | 0
216689 | 14-60 | 14 | -60 | 0 | 0 | 0
217410 | 14-60.5 | 14 | -60.5 | 0 | 0 | 0
218131 | 14-61 | 14 | -61 | 0 | 0 | 0
218852 | 14-61.5 | 14 | -61.5 | 0 | 0 | 0
219573 | 14-62 | 14 | -62 | 0 | 0 | 0
220294 | 14-62.5 | 14 | -62.5 | 0 | 0 | 0
221015 | 14-63 | 14 | -63 | 0 | 0 | 0
221736 | 14-63.5 | 14 | -63.5 | 0 | 0 | 0
222457 | 14-64 | 14 | -64 | 0 | 0 | 0
223178 | 14-64.5 | 14 | -64.5 | 0 | 0 | 0
223899 | 14-65 | 14 | -65 | 0 | 0 | 0
224620 | 14-65.5 | 14 | -65.5 | 0 | 0 | 0
225341 | 14-66 | 14 | -66 | 0 | 0 | 0
226062 | 14-66.5 | 14 | -66.5 | 0 | 0 | 0
226783 | 14-67 | 14 | -67 | 0 | 0 | 0
227504 | 14-67.5 | 14 | -67.5 | 0 | 0 | 0
228225 | 14-68 | 14 | -68 | 0 | 0 | 0
228946 | 14-68.5 | 14 | -68.5 | 0 | 0 | 0
229667 | 14-69 | 14 | -69 | 0 | 0 | 0
230388 | 14-69.5 | 14 | -69.5 | 0 | 0 | 0
231109 | 14-70 | 14 | -70 | 0 | 0 | 0
231830 | 14-70.5 | 14 | -70.5 | 0 | 0 | 0
232551 | 14-71 | 14 | -71 | 0 | 0 | 0
233272 | 14-71.5 | 14 | -71.5 | 0 | 0 | 0
233993 | 14-72 | 14 | -72 | 0 | 0 | 0
234714 | 14-72.5 | 14 | -72.5 | 0 | 0 | 0
235435 | 14-73 | 14 | -73 | 0 | 0 | 0
236156 | 14-73.5 | 14 | -73.5 | 0 | 0 | 0
236877 | 14-74 | 14 | -74 | 0 | 0 | 0
237598 | 14-74.5 | 14 | -74.5 | 0 | 0 | 0
238319 | 14-75 | 14 | -75 | 0 | 0 | 0
239040 | 14-75.5 | 14 | -75.5 | 0 | 0 | 0
239761 | 14-76 | 14 | -76 | 0 | 0 | 0
240482 | 14-76.5 | 14 | -76.5 | 0 | 0 | 0
241203 | 14-77 | 14 | -77 | 0 | 0 | 0
241924 | 14-77.5 | 14 | -77.5 | 0 | 0 | 0
242645 | 14-78 | 14 | -78 | 0 | 0 | 0
243366 | 14-78.5 | 14 | -78.5 | 0 | 0 | 0
244087 | 14-79 | 14 | -79 | 0 | 0 | 0
244808 | 14-79.5 | 14 | -79.5 | 0 | 0 | 0
245529 | 14-80 | 14 | -80 | 0 | 0 | 0
246250 | 14-80.5 | 14 | -80.5 | 0 | 0 | 0
246971 | 14-81 | 14 | -81 | 0 | 0 | 0
247692 | 14-81.5 | 14 | -81.5 | 0 | 0 | 0
248413 | 14-82 | 14 | -82 | 0 | 0 | 0
249134 | 14-82.5 | 14 | -82.5 | 0 | 0 | 0
249855 | 14-83 | 14 | -83 | 0 | 0 | 0
250576 | 14-83.5 | 14 | -83.5 | 0 | 0 | 0
251297 | 14-84 | 14 | -84 | 0 | 0 | 0
252018 | 14-84.5 | 14 | -84.5 | 0 | 0 | 0
252739 | 14-85 | 14 | -85 | 0 | 0 | 0
253460 | 14-85.5 | 14 | -85.5 | 0 | 0 | 0
254181 | 14-86 | 14 | -86 | 0 | 0 | 0
254902 | 14-86.5 | 14 | -86.5 | 0 | 0 | 0
255623 | 14-87 | 14 | -87 | 0 | 0 | 0
256344 | 14-87.5 | 14 | -87.5 | 0 | 0 | 0
257065 | 14-88 | 14 | -88 | 0 | 0 | 0
257786 | 14-88.5 | 14 | -88.5 | 0 | 0 | 0
258507 | 14-89 | 14 | -89 | 0 | 0 | 0
259228 | 14-89.5 | 14 | -89.5 | 0 | 0 | 0
259949 | 14-90 | 14 | -90 | 0 | 0 | 0
215248 | 14.5-59 | 14.5 | -59 | 0 | 0 | 0
215969 | 14.5-59.5 | 14.5 | -59.5 | 0 | 0 | 0
216690 | 14.5-60 | 14.5 | -60 | 0 | 0 | 0
217411 | 14.5-60.5 | 14.5 | -60.5 | 0 | 0 | 0
218132 | 14.5-61 | 14.5 | -61 | 0 | 0 | 0
218853 | 14.5-61.5 | 14.5 | -61.5 | 0 | 0 | 0
219574 | 14.5-62 | 14.5 | -62 | 0 | 0 | 0
220295 | 14.5-62.5 | 14.5 | -62.5 | 0 | 0 | 0
221016 | 14.5-63 | 14.5 | -63 | 0 | 0 | 0
221737 | 14.5-63.5 | 14.5 | -63.5 | 0 | 0 | 0
222458 | 14.5-64 | 14.5 | -64 | 0 | 0 | 0
223179 | 14.5-64.5 | 14.5 | -64.5 | 0 | 0 | 0
223900 | 14.5-65 | 14.5 | -65 | 0 | 0 | 0
224621 | 14.5-65.5 | 14.5 | -65.5 | 0 | 0 | 0
225342 | 14.5-66 | 14.5 | -66 | 0 | 0 | 0
226063 | 14.5-66.5 | 14.5 | -66.5 | 0 | 0 | 0
226784 | 14.5-67 | 14.5 | -67 | 0 | 0 | 0
227505 | 14.5-67.5 | 14.5 | -67.5 | 0 | 0 | 0
228226 | 14.5-68 | 14.5 | -68 | 0 | 0 | 0
228947 | 14.5-68.5 | 14.5 | -68.5 | 0 | 0 | 0
229668 | 14.5-69 | 14.5 | -69 | 0 | 0 | 0
230389 | 14.5-69.5 | 14.5 | -69.5 | 0 | 0 | 0
231110 | 14.5-70 | 14.5 | -70 | 0 | 0 | 0
231831 | 14.5-70.5 | 14.5 | -70.5 | 0 | 0 | 0
232552 | 14.5-71 | 14.5 | -71 | 0 | 0 | 0
233273 | 14.5-71.5 | 14.5 | -71.5 | 0 | 0 | 0
233994 | 14.5-72 | 14.5 | -72 | 0 | 0 | 0
234715 | 14.5-72.5 | 14.5 | -72.5 | 0 | 0 | 0
235436 | 14.5-73 | 14.5 | -73 | 0 | 0 | 0
236157 | 14.5-73.5 | 14.5 | -73.5 | 0 | 0 | 0
236878 | 14.5-74 | 14.5 | -74 | 0 | 0 | 0
237599 | 14.5-74.5 | 14.5 | -74.5 | 0 | 0 | 0
238320 | 14.5-75 | 14.5 | -75 | 0 | 0 | 0
239041 | 14.5-75.5 | 14.5 | -75.5 | 0 | 0 | 0
239762 | 14.5-76 | 14.5 | -76 | 0 | 0 | 0
240483 | 14.5-76.5 | 14.5 | -76.5 | 0 | 0 | 0
241204 | 14.5-77 | 14.5 | -77 | 0 | 0 | 0
241925 | 14.5-77.5 | 14.5 | -77.5 | 0 | 0 | 0
242646 | 14.5-78 | 14.5 | -78 | 0 | 0 | 0
243367 | 14.5-78.5 | 14.5 | -78.5 | 0 | 0 | 0
244088 | 14.5-79 | 14.5 | -79 | 0 | 0 | 0
244809 | 14.5-79.5 | 14.5 | -79.5 | 0 | 0 | 0
245530 | 14.5-80 | 14.5 | -80 | 0 | 0 | 0
246251 | 14.5-80.5 | 14.5 | -80.5 | 0 | 0 | 0
246972 | 14.5-81 | 14.5 | -81 | 0 | 0 | 0
247693 | 14.5-81.5 | 14.5 | -81.5 | 0 | 0 | 0
248414 | 14.5-82 | 14.5 | -82 | 0 | 0 | 0
249135 | 14.5-82.5 | 14.5 | -82.5 | 0 | 0 | 0
249856 | 14.5-83 | 14.5 | -83 | 0 | 0 | 0
250577 | 14.5-83.5 | 14.5 | -83.5 | 0 | 0 | 0
251298 | 14.5-84 | 14.5 | -84 | 0 | 0 | 0
252019 | 14.5-84.5 | 14.5 | -84.5 | 0 | 0 | 0
252740 | 14.5-85 | 14.5 | -85 | 0 | 0 | 0
253461 | 14.5-85.5 | 14.5 | -85.5 | 0 | 0 | 0
254182 | 14.5-86 | 14.5 | -86 | 0 | 0 | 0
254903 | 14.5-86.5 | 14.5 | -86.5 | 0 | 0 | 0
255624 | 14.5-87 | 14.5 | -87 | 0 | 0 | 0
256345 | 14.5-87.5 | 14.5 | -87.5 | 0 | 0 | 0
257066 | 14.5-88 | 14.5 | -88 | 0 | 0 | 0
257787 | 14.5-88.5 | 14.5 | -88.5 | 0 | 0 | 0
258508 | 14.5-89 | 14.5 | -89 | 0 | 0 | 0
259229 | 14.5-89.5 | 14.5 | -89.5 | 0 | 0 | 0
259950 | 14.5-90 | 14.5 | -90 | 0 | 0 | 0
215249 | 15-59 | 15 | -59 | 0 | 0 | 0
215970 | 15-59.5 | 15 | -59.5 | 0 | 0 | 0
216691 | 15-60 | 15 | -60 | 0 | 0 | 0
217412 | 15-60.5 | 15 | -60.5 | 0 | 0 | 0
218133 | 15-61 | 15 | -61 | 0 | 0 | 0
218854 | 15-61.5 | 15 | -61.5 | 0 | 0 | 0
219575 | 15-62 | 15 | -62 | 0 | 0 | 0
220296 | 15-62.5 | 15 | -62.5 | 0 | 0 | 0
221017 | 15-63 | 15 | -63 | 0 | 0 | 0
221738 | 15-63.5 | 15 | -63.5 | 0 | 0 | 0
222459 | 15-64 | 15 | -64 | 0 | 0 | 0
223180 | 15-64.5 | 15 | -64.5 | 0 | 0 | 0
223901 | 15-65 | 15 | -65 | 0 | 0 | 0
224622 | 15-65.5 | 15 | -65.5 | 0 | 0 | 0
225343 | 15-66 | 15 | -66 | 0 | 0 | 0
226064 | 15-66.5 | 15 | -66.5 | 0 | 0 | 0
226785 | 15-67 | 15 | -67 | 0 | 0 | 0
227506 | 15-67.5 | 15 | -67.5 | 0 | 0 | 0
228227 | 15-68 | 15 | -68 | 0 | 0 | 0
228948 | 15-68.5 | 15 | -68.5 | 0 | 0 | 0
229669 | 15-69 | 15 | -69 | 0 | 0 | 0
230390 | 15-69.5 | 15 | -69.5 | 0 | 0 | 0
231111 | 15-70 | 15 | -70 | 0 | 0 | 0
231832 | 15-70.5 | 15 | -70.5 | 0 | 0 | 0
232553 | 15-71 | 15 | -71 | 0 | 0 | 0
233274 | 15-71.5 | 15 | -71.5 | 0 | 0 | 0
233995 | 15-72 | 15 | -72 | 0 | 0 | 0
234716 | 15-72.5 | 15 | -72.5 | 0 | 0 | 0
235437 | 15-73 | 15 | -73 | 0 | 0 | 0
236158 | 15-73.5 | 15 | -73.5 | 0 | 0 | 0
236879 | 15-74 | 15 | -74 | 0 | 0 | 0
237600 | 15-74.5 | 15 | -74.5 | 0 | 0 | 0
238321 | 15-75 | 15 | -75 | 0 | 0 | 0
239042 | 15-75.5 | 15 | -75.5 | 0 | 0 | 0
239763 | 15-76 | 15 | -76 | 0 | 0 | 0
240484 | 15-76.5 | 15 | -76.5 | 0 | 0 | 0
241205 | 15-77 | 15 | -77 | 0 | 0 | 0
241926 | 15-77.5 | 15 | -77.5 | 0 | 0 | 0
242647 | 15-78 | 15 | -78 | 0 | 0 | 0
243368 | 15-78.5 | 15 | -78.5 | 0 | 0 | 0
244089 | 15-79 | 15 | -79 | 0 | 0 | 0
244810 | 15-79.5 | 15 | -79.5 | 0 | 0 | 0
245531 | 15-80 | 15 | -80 | 0 | 0 | 0
246252 | 15-80.5 | 15 | -80.5 | 0 | 0 | 0
246973 | 15-81 | 15 | -81 | 0 | 0 | 0
247694 | 15-81.5 | 15 | -81.5 | 0 | 0 | 0
248415 | 15-82 | 15 | -82 | 0 | 0 | 0
249136 | 15-82.5 | 15 | -82.5 | 0 | 0 | 0
249857 | 15-83 | 15 | -83 | 0 | 0 | 0
250578 | 15-83.5 | 15 | -83.5 | 0 | 0 | 0
251299 | 15-84 | 15 | -84 | 0 | 0 | 0
252020 | 15-84.5 | 15 | -84.5 | 0 | 0 | 0
252741 | 15-85 | 15 | -85 | 0 | 0 | 0
253462 | 15-85.5 | 15 | -85.5 | 0 | 0 | 0
254183 | 15-86 | 15 | -86 | 0 | 0 | 0
254904 | 15-86.5 | 15 | -86.5 | 0 | 0 | 0
255625 | 15-87 | 15 | -87 | 0 | 0 | 0
256346 | 15-87.5 | 15 | -87.5 | 0 | 0 | 0
257067 | 15-88 | 15 | -88 | 0 | 0 | 0
257788 | 15-88.5 | 15 | -88.5 | 0 | 0 | 0
258509 | 15-89 | 15 | -89 | 0 | 0 | 0
259230 | 15-89.5 | 15 | -89.5 | 0 | 0 | 0
259951 | 15-90 | 15 | -90 | 0 | 0 | 0
215250 | 15.5-59 | 15.5 | -59 | 0 | 0 | 0
215971 | 15.5-59.5 | 15.5 | -59.5 | 0 | 0 | 0
216692 | 15.5-60 | 15.5 | -60 | 0 | 0 | 0
217413 | 15.5-60.5 | 15.5 | -60.5 | 0 | 0 | 0
218134 | 15.5-61 | 15.5 | -61 | 0 | 0 | 0
218855 | 15.5-61.5 | 15.5 | -61.5 | 0 | 0 | 0
219576 | 15.5-62 | 15.5 | -62 | 0 | 0 | 0
220297 | 15.5-62.5 | 15.5 | -62.5 | 0 | 0 | 0
221018 | 15.5-63 | 15.5 | -63 | 0 | 0 | 0
221739 | 15.5-63.5 | 15.5 | -63.5 | 0 | 0 | 0
222460 | 15.5-64 | 15.5 | -64 | 0 | 0 | 0
223181 | 15.5-64.5 | 15.5 | -64.5 | 0 | 0 | 0
223902 | 15.5-65 | 15.5 | -65 | 0 | 0 | 0
224623 | 15.5-65.5 | 15.5 | -65.5 | 0 | 0 | 0
225344 | 15.5-66 | 15.5 | -66 | 0 | 0 | 0
226065 | 15.5-66.5 | 15.5 | -66.5 | 0 | 0 | 0
226786 | 15.5-67 | 15.5 | -67 | 0 | 0 | 0
227507 | 15.5-67.5 | 15.5 | -67.5 | 0 | 0 | 0
228228 | 15.5-68 | 15.5 | -68 | 0 | 0 | 0
228949 | 15.5-68.5 | 15.5 | -68.5 | 0 | 0 | 0
229670 | 15.5-69 | 15.5 | -69 | 0 | 0 | 0
230391 | 15.5-69.5 | 15.5 | -69.5 | 0 | 0 | 0
231112 | 15.5-70 | 15.5 | -70 | 0 | 0 | 0
231833 | 15.5-70.5 | 15.5 | -70.5 | 0 | 0 | 0
232554 | 15.5-71 | 15.5 | -71 | 0 | 0 | 0
233275 | 15.5-71.5 | 15.5 | -71.5 | 0 | 0 | 0
233996 | 15.5-72 | 15.5 | -72 | 0 | 0 | 0
234717 | 15.5-72.5 | 15.5 | -72.5 | 0 | 0 | 0
235438 | 15.5-73 | 15.5 | -73 | 0 | 0 | 0
236159 | 15.5-73.5 | 15.5 | -73.5 | 0 | 0 | 0
236880 | 15.5-74 | 15.5 | -74 | 0 | 0 | 0
237601 | 15.5-74.5 | 15.5 | -74.5 | 0 | 0 | 0
238322 | 15.5-75 | 15.5 | -75 | 0 | 0 | 0
239043 | 15.5-75.5 | 15.5 | -75.5 | 0 | 0 | 0
239764 | 15.5-76 | 15.5 | -76 | 0 | 0 | 0
240485 | 15.5-76.5 | 15.5 | -76.5 | 0 | 0 | 0
241206 | 15.5-77 | 15.5 | -77 | 0 | 0 | 0
241927 | 15.5-77.5 | 15.5 | -77.5 | 0 | 0 | 0
242648 | 15.5-78 | 15.5 | -78 | 0 | 0 | 0
243369 | 15.5-78.5 | 15.5 | -78.5 | 0 | 0 | 0
244090 | 15.5-79 | 15.5 | -79 | 0 | 0 | 0
244811 | 15.5-79.5 | 15.5 | -79.5 | 0 | 0 | 0
245532 | 15.5-80 | 15.5 | -80 | 0 | 0 | 0
246253 | 15.5-80.5 | 15.5 | -80.5 | 0 | 0 | 0
246974 | 15.5-81 | 15.5 | -81 | 0 | 0 | 0
247695 | 15.5-81.5 | 15.5 | -81.5 | 0 | 0 | 0
248416 | 15.5-82 | 15.5 | -82 | 0 | 0 | 0
249137 | 15.5-82.5 | 15.5 | -82.5 | 0 | 0 | 0
249858 | 15.5-83 | 15.5 | -83 | 0 | 0 | 0
250579 | 15.5-83.5 | 15.5 | -83.5 | 0 | 0 | 0
251300 | 15.5-84 | 15.5 | -84 | 0 | 0 | 0
252021 | 15.5-84.5 | 15.5 | -84.5 | 0 | 0 | 0
252742 | 15.5-85 | 15.5 | -85 | 0 | 0 | 0
253463 | 15.5-85.5 | 15.5 | -85.5 | 0 | 0 | 0
254184 | 15.5-86 | 15.5 | -86 | 0 | 0 | 0
254905 | 15.5-86.5 | 15.5 | -86.5 | 0 | 0 | 0
255626 | 15.5-87 | 15.5 | -87 | 0 | 0 | 0
256347 | 15.5-87.5 | 15.5 | -87.5 | 0 | 0 | 0
257068 | 15.5-88 | 15.5 | -88 | 0 | 0 | 0
257789 | 15.5-88.5 | 15.5 | -88.5 | 0 | 0 | 0
258510 | 15.5-89 | 15.5 | -89 | 0 | 0 | 0
259231 | 15.5-89.5 | 15.5 | -89.5 | 0 | 0 | 0
259952 | 15.5-90 | 15.5 | -90 | 0 | 0 | 0
215251 | 16-59 | 16 | -59 | 0 | 0 | 0
215972 | 16-59.5 | 16 | -59.5 | 0 | 0 | 0
216693 | 16-60 | 16 | -60 | 0 | 0 | 0
217414 | 16-60.5 | 16 | -60.5 | 0 | 0 | 0
218135 | 16-61 | 16 | -61 | 0 | 0 | 0
218856 | 16-61.5 | 16 | -61.5 | 0 | 0 | 0
219577 | 16-62 | 16 | -62 | 0 | 0 | 0
220298 | 16-62.5 | 16 | -62.5 | 0 | 0 | 0
221019 | 16-63 | 16 | -63 | 0 | 0 | 0
221740 | 16-63.5 | 16 | -63.5 | 0 | 0 | 0
222461 | 16-64 | 16 | -64 | 0 | 0 | 0
223182 | 16-64.5 | 16 | -64.5 | 0 | 0 | 0
223903 | 16-65 | 16 | -65 | 0 | 0 | 0
224624 | 16-65.5 | 16 | -65.5 | 0 | 0 | 0
225345 | 16-66 | 16 | -66 | 0 | 0 | 0
226066 | 16-66.5 | 16 | -66.5 | 0 | 0 | 0
226787 | 16-67 | 16 | -67 | 0 | 0 | 0
227508 | 16-67.5 | 16 | -67.5 | 0 | 0 | 0
228229 | 16-68 | 16 | -68 | 0 | 0 | 0
228950 | 16-68.5 | 16 | -68.5 | 0 | 0 | 0
229671 | 16-69 | 16 | -69 | 0 | 0 | 0
230392 | 16-69.5 | 16 | -69.5 | 0 | 0 | 0
231113 | 16-70 | 16 | -70 | 0 | 0 | 0
231834 | 16-70.5 | 16 | -70.5 | 0 | 0 | 0
232555 | 16-71 | 16 | -71 | 0 | 0 | 0
233276 | 16-71.5 | 16 | -71.5 | 0 | 0 | 0
233997 | 16-72 | 16 | -72 | 0 | 0 | 0
234718 | 16-72.5 | 16 | -72.5 | 0 | 0 | 0
235439 | 16-73 | 16 | -73 | 0 | 0 | 0
236160 | 16-73.5 | 16 | -73.5 | 0 | 0 | 0
236881 | 16-74 | 16 | -74 | 0 | 0 | 0
237602 | 16-74.5 | 16 | -74.5 | 0 | 0 | 0
238323 | 16-75 | 16 | -75 | 0 | 0 | 0
239044 | 16-75.5 | 16 | -75.5 | 0 | 0 | 0
239765 | 16-76 | 16 | -76 | 0 | 0 | 0
240486 | 16-76.5 | 16 | -76.5 | 0 | 0 | 0
241207 | 16-77 | 16 | -77 | 0 | 0 | 0
241928 | 16-77.5 | 16 | -77.5 | 0 | 0 | 0
242649 | 16-78 | 16 | -78 | 0 | 0 | 0
243370 | 16-78.5 | 16 | -78.5 | 0 | 0 | 0
244091 | 16-79 | 16 | -79 | 0 | 0 | 0
244812 | 16-79.5 | 16 | -79.5 | 0 | 0 | 0
245533 | 16-80 | 16 | -80 | 0 | 0 | 0
246254 | 16-80.5 | 16 | -80.5 | 0 | 0 | 0
246975 | 16-81 | 16 | -81 | 0 | 0 | 0
247696 | 16-81.5 | 16 | -81.5 | 0 | 0 | 0
248417 | 16-82 | 16 | -82 | 0 | 0 | 0
249138 | 16-82.5 | 16 | -82.5 | 0 | 0 | 0
249859 | 16-83 | 16 | -83 | 0 | 0 | 0
250580 | 16-83.5 | 16 | -83.5 | 0 | 0 | 0
251301 | 16-84 | 16 | -84 | 0 | 0 | 0
252022 | 16-84.5 | 16 | -84.5 | 0 | 0 | 0
252743 | 16-85 | 16 | -85 | 0 | 0 | 0
253464 | 16-85.5 | 16 | -85.5 | 0 | 0 | 0
254185 | 16-86 | 16 | -86 | 0 | 0 | 0
254906 | 16-86.5 | 16 | -86.5 | 0 | 0 | 0
255627 | 16-87 | 16 | -87 | 0 | 0 | 0
256348 | 16-87.5 | 16 | -87.5 | 0 | 0 | 0
257069 | 16-88 | 16 | -88 | 0 | 0 | 0
257790 | 16-88.5 | 16 | -88.5 | 0 | 0 | 0
258511 | 16-89 | 16 | -89 | 0 | 0 | 0
259232 | 16-89.5 | 16 | -89.5 | 0 | 0 | 0
259953 | 16-90 | 16 | -90 | 0 | 0 | 0
215252 | 16.5-59 | 16.5 | -59 | 0 | 0 | 0
215973 | 16.5-59.5 | 16.5 | -59.5 | 0 | 0 | 0
216694 | 16.5-60 | 16.5 | -60 | 0 | 0 | 0
217415 | 16.5-60.5 | 16.5 | -60.5 | 0 | 0 | 0
218136 | 16.5-61 | 16.5 | -61 | 0 | 0 | 0
218857 | 16.5-61.5 | 16.5 | -61.5 | 0 | 0 | 0
219578 | 16.5-62 | 16.5 | -62 | 0 | 0 | 0
220299 | 16.5-62.5 | 16.5 | -62.5 | 0 | 0 | 0
221020 | 16.5-63 | 16.5 | -63 | 0 | 0 | 0
221741 | 16.5-63.5 | 16.5 | -63.5 | 0 | 0 | 0
222462 | 16.5-64 | 16.5 | -64 | 0 | 0 | 0
223183 | 16.5-64.5 | 16.5 | -64.5 | 0 | 0 | 0
223904 | 16.5-65 | 16.5 | -65 | 0 | 0 | 0
224625 | 16.5-65.5 | 16.5 | -65.5 | 0 | 0 | 0
225346 | 16.5-66 | 16.5 | -66 | 0 | 0 | 0
226067 | 16.5-66.5 | 16.5 | -66.5 | 0 | 0 | 0
226788 | 16.5-67 | 16.5 | -67 | 0 | 0 | 0
227509 | 16.5-67.5 | 16.5 | -67.5 | 0 | 0 | 0
228230 | 16.5-68 | 16.5 | -68 | 0 | 0 | 0
228951 | 16.5-68.5 | 16.5 | -68.5 | 0 | 0 | 0
229672 | 16.5-69 | 16.5 | -69 | 0 | 0 | 0
230393 | 16.5-69.5 | 16.5 | -69.5 | 0 | 0 | 0
231114 | 16.5-70 | 16.5 | -70 | 0 | 0 | 0
231835 | 16.5-70.5 | 16.5 | -70.5 | 0 | 0 | 0
232556 | 16.5-71 | 16.5 | -71 | 0 | 0 | 0
233277 | 16.5-71.5 | 16.5 | -71.5 | 0 | 0 | 0
233998 | 16.5-72 | 16.5 | -72 | 0 | 0 | 0
234719 | 16.5-72.5 | 16.5 | -72.5 | 0 | 0 | 0
235440 | 16.5-73 | 16.5 | -73 | 0 | 0 | 0
236161 | 16.5-73.5 | 16.5 | -73.5 | 0 | 0 | 0
236882 | 16.5-74 | 16.5 | -74 | 0 | 0 | 0
237603 | 16.5-74.5 | 16.5 | -74.5 | 0 | 0 | 0
238324 | 16.5-75 | 16.5 | -75 | 0 | 0 | 0
239045 | 16.5-75.5 | 16.5 | -75.5 | 0 | 0 | 0
239766 | 16.5-76 | 16.5 | -76 | 0 | 0 | 0
240487 | 16.5-76.5 | 16.5 | -76.5 | 0 | 0 | 0
241208 | 16.5-77 | 16.5 | -77 | 0 | 0 | 0
241929 | 16.5-77.5 | 16.5 | -77.5 | 0 | 0 | 0
242650 | 16.5-78 | 16.5 | -78 | 0 | 0 | 0
243371 | 16.5-78.5 | 16.5 | -78.5 | 0 | 0 | 0
244092 | 16.5-79 | 16.5 | -79 | 0 | 0 | 0
244813 | 16.5-79.5 | 16.5 | -79.5 | 0 | 0 | 0
245534 | 16.5-80 | 16.5 | -80 | 0 | 0 | 0
246255 | 16.5-80.5 | 16.5 | -80.5 | 0 | 0 | 0
246976 | 16.5-81 | 16.5 | -81 | 0 | 0 | 0
247697 | 16.5-81.5 | 16.5 | -81.5 | 0 | 0 | 0
248418 | 16.5-82 | 16.5 | -82 | 0 | 0 | 0
249139 | 16.5-82.5 | 16.5 | -82.5 | 0 | 0 | 0
249860 | 16.5-83 | 16.5 | -83 | 0 | 0 | 0
250581 | 16.5-83.5 | 16.5 | -83.5 | 0 | 0 | 0
251302 | 16.5-84 | 16.5 | -84 | 0 | 0 | 0
252023 | 16.5-84.5 | 16.5 | -84.5 | 0 | 0 | 0
252744 | 16.5-85 | 16.5 | -85 | 0 | 0 | 0
253465 | 16.5-85.5 | 16.5 | -85.5 | 0 | 0 | 0
254186 | 16.5-86 | 16.5 | -86 | 0 | 0 | 0
254907 | 16.5-86.5 | 16.5 | -86.5 | 0 | 0 | 0
255628 | 16.5-87 | 16.5 | -87 | 0 | 0 | 0
256349 | 16.5-87.5 | 16.5 | -87.5 | 0 | 0 | 0
257070 | 16.5-88 | 16.5 | -88 | 0 | 0 | 0
257791 | 16.5-88.5 | 16.5 | -88.5 | 0 | 0 | 0
258512 | 16.5-89 | 16.5 | -89 | 0 | 0 | 0
259233 | 16.5-89.5 | 16.5 | -89.5 | 0 | 0 | 0
259954 | 16.5-90 | 16.5 | -90 | 0 | 0 | 0
215253 | 17-59 | 17 | -59 | 0 | 0 | 0
215974 | 17-59.5 | 17 | -59.5 | 0 | 0 | 0
216695 | 17-60 | 17 | -60 | 0 | 0 | 0
217416 | 17-60.5 | 17 | -60.5 | 0 | 0 | 0
218137 | 17-61 | 17 | -61 | 0 | 0 | 0
218858 | 17-61.5 | 17 | -61.5 | 0 | 0 | 0
219579 | 17-62 | 17 | -62 | 0 | 0 | 0
220300 | 17-62.5 | 17 | -62.5 | 0 | 0 | 0
221021 | 17-63 | 17 | -63 | 0 | 0 | 0
221742 | 17-63.5 | 17 | -63.5 | 0 | 0 | 0
222463 | 17-64 | 17 | -64 | 0 | 0 | 0
223184 | 17-64.5 | 17 | -64.5 | 0 | 0 | 0
223905 | 17-65 | 17 | -65 | 0 | 0 | 0
224626 | 17-65.5 | 17 | -65.5 | 0 | 0 | 0
225347 | 17-66 | 17 | -66 | 0 | 0 | 0
226068 | 17-66.5 | 17 | -66.5 | 0 | 0 | 0
226789 | 17-67 | 17 | -67 | 0 | 0 | 0
227510 | 17-67.5 | 17 | -67.5 | 0 | 0 | 0
228231 | 17-68 | 17 | -68 | 0 | 0 | 0
228952 | 17-68.5 | 17 | -68.5 | 0 | 0 | 0
229673 | 17-69 | 17 | -69 | 0 | 0 | 0
230394 | 17-69.5 | 17 | -69.5 | 0 | 0 | 0
231115 | 17-70 | 17 | -70 | 0 | 0 | 0
231836 | 17-70.5 | 17 | -70.5 | 0 | 0 | 0
232557 | 17-71 | 17 | -71 | 0 | 0 | 0
233278 | 17-71.5 | 17 | -71.5 | 0 | 0 | 0
233999 | 17-72 | 17 | -72 | 0 | 0 | 0
234720 | 17-72.5 | 17 | -72.5 | 0 | 0 | 0
235441 | 17-73 | 17 | -73 | 0 | 0 | 0
236162 | 17-73.5 | 17 | -73.5 | 0 | 0 | 0
236883 | 17-74 | 17 | -74 | 0 | 0 | 0
237604 | 17-74.5 | 17 | -74.5 | 0 | 0 | 0
238325 | 17-75 | 17 | -75 | 0 | 0 | 0
239046 | 17-75.5 | 17 | -75.5 | 0 | 0 | 0
239767 | 17-76 | 17 | -76 | 0 | 0 | 0
240488 | 17-76.5 | 17 | -76.5 | 0 | 0 | 0
241209 | 17-77 | 17 | -77 | 0 | 0 | 0
241930 | 17-77.5 | 17 | -77.5 | 0 | 0 | 0
242651 | 17-78 | 17 | -78 | 0 | 0 | 0
243372 | 17-78.5 | 17 | -78.5 | 0 | 0 | 0
244093 | 17-79 | 17 | -79 | 0 | 0 | 0
244814 | 17-79.5 | 17 | -79.5 | 0 | 0 | 0
245535 | 17-80 | 17 | -80 | 0 | 0 | 0
246256 | 17-80.5 | 17 | -80.5 | 0 | 0 | 0
246977 | 17-81 | 17 | -81 | 0 | 0 | 0
247698 | 17-81.5 | 17 | -81.5 | 0 | 0 | 0
248419 | 17-82 | 17 | -82 | 0 | 0 | 0
249140 | 17-82.5 | 17 | -82.5 | 0 | 0 | 0
249861 | 17-83 | 17 | -83 | 0 | 0 | 0
250582 | 17-83.5 | 17 | -83.5 | 0 | 0 | 0
251303 | 17-84 | 17 | -84 | 0 | 0 | 0
252024 | 17-84.5 | 17 | -84.5 | 0 | 0 | 0
252745 | 17-85 | 17 | -85 | 0 | 0 | 0
253466 | 17-85.5 | 17 | -85.5 | 0 | 0 | 0
254187 | 17-86 | 17 | -86 | 0 | 0 | 0
254908 | 17-86.5 | 17 | -86.5 | 0 | 0 | 0
255629 | 17-87 | 17 | -87 | 0 | 0 | 0
256350 | 17-87.5 | 17 | -87.5 | 0 | 0 | 0
257071 | 17-88 | 17 | -88 | 0 | 0 | 0
257792 | 17-88.5 | 17 | -88.5 | 0 | 0 | 0
258513 | 17-89 | 17 | -89 | 0 | 0 | 0
259234 | 17-89.5 | 17 | -89.5 | 0 | 0 | 0
259955 | 17-90 | 17 | -90 | 0 | 0 | 0
215254 | 17.5-59 | 17.5 | -59 | 0 | 0 | 0
215975 | 17.5-59.5 | 17.5 | -59.5 | 0 | 0 | 0
216696 | 17.5-60 | 17.5 | -60 | 0 | 0 | 0
217417 | 17.5-60.5 | 17.5 | -60.5 | 0 | 0 | 0
218138 | 17.5-61 | 17.5 | -61 | 0 | 0 | 0
218859 | 17.5-61.5 | 17.5 | -61.5 | 0 | 0 | 0
219580 | 17.5-62 | 17.5 | -62 | 0 | 0 | 0
220301 | 17.5-62.5 | 17.5 | -62.5 | 0 | 0 | 0
221022 | 17.5-63 | 17.5 | -63 | 0 | 0 | 0
221743 | 17.5-63.5 | 17.5 | -63.5 | 0 | 0 | 0
222464 | 17.5-64 | 17.5 | -64 | 0 | 0 | 0
223185 | 17.5-64.5 | 17.5 | -64.5 | 0 | 0 | 0
223906 | 17.5-65 | 17.5 | -65 | 0 | 0 | 0
224627 | 17.5-65.5 | 17.5 | -65.5 | 0 | 0 | 0
225348 | 17.5-66 | 17.5 | -66 | 0 | 0 | 0
226069 | 17.5-66.5 | 17.5 | -66.5 | 0 | 0 | 0
226790 | 17.5-67 | 17.5 | -67 | 0 | 0 | 0
227511 | 17.5-67.5 | 17.5 | -67.5 | 0 | 0 | 0
228232 | 17.5-68 | 17.5 | -68 | 0 | 0 | 0
228953 | 17.5-68.5 | 17.5 | -68.5 | 0 | 0 | 0
229674 | 17.5-69 | 17.5 | -69 | 0 | 0 | 0
230395 | 17.5-69.5 | 17.5 | -69.5 | 0 | 0 | 0
231116 | 17.5-70 | 17.5 | -70 | 0 | 0 | 0
231837 | 17.5-70.5 | 17.5 | -70.5 | 0 | 0 | 0
232558 | 17.5-71 | 17.5 | -71 | 0 | 0 | 0
233279 | 17.5-71.5 | 17.5 | -71.5 | 0 | 0 | 0
234000 | 17.5-72 | 17.5 | -72 | 0 | 0 | 0
234721 | 17.5-72.5 | 17.5 | -72.5 | 0 | 0 | 0
235442 | 17.5-73 | 17.5 | -73 | 0 | 0 | 0
236163 | 17.5-73.5 | 17.5 | -73.5 | 0 | 0 | 0
236884 | 17.5-74 | 17.5 | -74 | 0 | 0 | 0
237605 | 17.5-74.5 | 17.5 | -74.5 | 0 | 0 | 0
238326 | 17.5-75 | 17.5 | -75 | 0 | 0 | 0
239047 | 17.5-75.5 | 17.5 | -75.5 | 0 | 0 | 0
239768 | 17.5-76 | 17.5 | -76 | 0 | 0 | 0
240489 | 17.5-76.5 | 17.5 | -76.5 | 0 | 0 | 0
241210 | 17.5-77 | 17.5 | -77 | 0 | 0 | 0
241931 | 17.5-77.5 | 17.5 | -77.5 | 0 | 0 | 0
242652 | 17.5-78 | 17.5 | -78 | 0 | 0 | 0
243373 | 17.5-78.5 | 17.5 | -78.5 | 0 | 0 | 0
244094 | 17.5-79 | 17.5 | -79 | 0 | 0 | 0
244815 | 17.5-79.5 | 17.5 | -79.5 | 0 | 0 | 0
245536 | 17.5-80 | 17.5 | -80 | 0 | 0 | 0
246257 | 17.5-80.5 | 17.5 | -80.5 | 0 | 0 | 0
246978 | 17.5-81 | 17.5 | -81 | 0 | 0 | 0
247699 | 17.5-81.5 | 17.5 | -81.5 | 0 | 0 | 0
248420 | 17.5-82 | 17.5 | -82 | 0 | 0 | 0
249141 | 17.5-82.5 | 17.5 | -82.5 | 0 | 0 | 0
249862 | 17.5-83 | 17.5 | -83 | 0 | 0 | 0
250583 | 17.5-83.5 | 17.5 | -83.5 | 0 | 0 | 0
251304 | 17.5-84 | 17.5 | -84 | 0 | 0 | 0
252025 | 17.5-84.5 | 17.5 | -84.5 | 0 | 0 | 0
252746 | 17.5-85 | 17.5 | -85 | 0 | 0 | 0
253467 | 17.5-85.5 | 17.5 | -85.5 | 0 | 0 | 0
254188 | 17.5-86 | 17.5 | -86 | 0 | 0 | 0
254909 | 17.5-86.5 | 17.5 | -86.5 | 0 | 0 | 0
255630 | 17.5-87 | 17.5 | -87 | 0 | 0 | 0
256351 | 17.5-87.5 | 17.5 | -87.5 | 0 | 0 | 0
257072 | 17.5-88 | 17.5 | -88 | 0 | 0 | 0
257793 | 17.5-88.5 | 17.5 | -88.5 | 0 | 0 | 0
258514 | 17.5-89 | 17.5 | -89 | 0 | 0 | 0
259235 | 17.5-89.5 | 17.5 | -89.5 | 0 | 0 | 0
259956 | 17.5-90 | 17.5 | -90 | 0 | 0 | 0
215255 | 18-59 | 18 | -59 | 0 | 0 | 0
215976 | 18-59.5 | 18 | -59.5 | 0 | 0 | 0
216697 | 18-60 | 18 | -60 | 0 | 0 | 0
217418 | 18-60.5 | 18 | -60.5 | 0 | 0 | 0
218139 | 18-61 | 18 | -61 | 0 | 0 | 0
218860 | 18-61.5 | 18 | -61.5 | 0 | 0 | 0
219581 | 18-62 | 18 | -62 | 0 | 0 | 0
220302 | 18-62.5 | 18 | -62.5 | 0 | 0 | 0
221023 | 18-63 | 18 | -63 | 0 | 0 | 0
221744 | 18-63.5 | 18 | -63.5 | 0 | 0 | 0
222465 | 18-64 | 18 | -64 | 0 | 0 | 0
223186 | 18-64.5 | 18 | -64.5 | 0 | 0 | 0
223907 | 18-65 | 18 | -65 | 0 | 0 | 0
224628 | 18-65.5 | 18 | -65.5 | 0 | 0 | 0
225349 | 18-66 | 18 | -66 | 0 | 0 | 0
226070 | 18-66.5 | 18 | -66.5 | 0 | 0 | 0
226791 | 18-67 | 18 | -67 | 0 | 0 | 0
227512 | 18-67.5 | 18 | -67.5 | 0 | 0 | 0
228233 | 18-68 | 18 | -68 | 0 | 0 | 0
228954 | 18-68.5 | 18 | -68.5 | 0 | 0 | 0
229675 | 18-69 | 18 | -69 | 0 | 0 | 0
230396 | 18-69.5 | 18 | -69.5 | 0 | 0 | 0
231117 | 18-70 | 18 | -70 | 0 | 0 | 0
231838 | 18-70.5 | 18 | -70.5 | 0 | 0 | 0
232559 | 18-71 | 18 | -71 | 0 | 0 | 0
233280 | 18-71.5 | 18 | -71.5 | 0 | 0 | 0
234001 | 18-72 | 18 | -72 | 0 | 0 | 0
234722 | 18-72.5 | 18 | -72.5 | 0 | 0 | 0
235443 | 18-73 | 18 | -73 | 0 | 0 | 0
236164 | 18-73.5 | 18 | -73.5 | 0 | 0 | 0
236885 | 18-74 | 18 | -74 | 0 | 0 | 0
237606 | 18-74.5 | 18 | -74.5 | 0 | 0 | 0
238327 | 18-75 | 18 | -75 | 0 | 0 | 0
239048 | 18-75.5 | 18 | -75.5 | 0 | 0 | 0
239769 | 18-76 | 18 | -76 | 0 | 0 | 0
240490 | 18-76.5 | 18 | -76.5 | 0 | 0 | 0
241211 | 18-77 | 18 | -77 | 0 | 0 | 0
241932 | 18-77.5 | 18 | -77.5 | 0 | 0 | 0
242653 | 18-78 | 18 | -78 | 0 | 0 | 0
243374 | 18-78.5 | 18 | -78.5 | 0 | 0 | 0
244095 | 18-79 | 18 | -79 | 0 | 0 | 0
244816 | 18-79.5 | 18 | -79.5 | 0 | 0 | 0
245537 | 18-80 | 18 | -80 | 0 | 0 | 0
246258 | 18-80.5 | 18 | -80.5 | 0 | 0 | 0
246979 | 18-81 | 18 | -81 | 0 | 0 | 0
247700 | 18-81.5 | 18 | -81.5 | 0 | 0 | 0
248421 | 18-82 | 18 | -82 | 0 | 0 | 0
249142 | 18-82.5 | 18 | -82.5 | 0 | 0 | 0
249863 | 18-83 | 18 | -83 | 0 | 0 | 0
250584 | 18-83.5 | 18 | -83.5 | 0 | 0 | 0
251305 | 18-84 | 18 | -84 | 0 | 0 | 0
252026 | 18-84.5 | 18 | -84.5 | 0 | 0 | 0
252747 | 18-85 | 18 | -85 | 0 | 0 | 0
253468 | 18-85.5 | 18 | -85.5 | 0 | 0 | 0
254189 | 18-86 | 18 | -86 | 0 | 0 | 0
254910 | 18-86.5 | 18 | -86.5 | 0 | 0 | 0
255631 | 18-87 | 18 | -87 | 0 | 0 | 0
256352 | 18-87.5 | 18 | -87.5 | 0 | 0 | 0
257073 | 18-88 | 18 | -88 | 0 | 0 | 0
257794 | 18-88.5 | 18 | -88.5 | 0 | 0 | 0
258515 | 18-89 | 18 | -89 | 0 | 0 | 0
259236 | 18-89.5 | 18 | -89.5 | 0 | 0 | 0
259957 | 18-90 | 18 | -90 | 0 | 0 | 0
215256 | 18.5-59 | 18.5 | -59 | 0 | 0 | 0
215977 | 18.5-59.5 | 18.5 | -59.5 | 0 | 0 | 0
216698 | 18.5-60 | 18.5 | -60 | 0 | 0 | 0
217419 | 18.5-60.5 | 18.5 | -60.5 | 0 | 0 | 0
218140 | 18.5-61 | 18.5 | -61 | 0 | 0 | 0
218861 | 18.5-61.5 | 18.5 | -61.5 | 0 | 0 | 0
219582 | 18.5-62 | 18.5 | -62 | 0 | 0 | 0
220303 | 18.5-62.5 | 18.5 | -62.5 | 0 | 0 | 0
221024 | 18.5-63 | 18.5 | -63 | 0 | 0 | 0
221745 | 18.5-63.5 | 18.5 | -63.5 | 0 | 0 | 0
222466 | 18.5-64 | 18.5 | -64 | 0 | 0 | 0
223187 | 18.5-64.5 | 18.5 | -64.5 | 0 | 0 | 0
223908 | 18.5-65 | 18.5 | -65 | 0 | 0 | 0
224629 | 18.5-65.5 | 18.5 | -65.5 | 0 | 0 | 0
225350 | 18.5-66 | 18.5 | -66 | 0 | 0 | 0
226071 | 18.5-66.5 | 18.5 | -66.5 | 0 | 0 | 0
226792 | 18.5-67 | 18.5 | -67 | 0 | 0 | 0
227513 | 18.5-67.5 | 18.5 | -67.5 | 0 | 0 | 0
228234 | 18.5-68 | 18.5 | -68 | 0 | 0 | 0
228955 | 18.5-68.5 | 18.5 | -68.5 | 0 | 0 | 0
229676 | 18.5-69 | 18.5 | -69 | 0 | 0 | 0
230397 | 18.5-69.5 | 18.5 | -69.5 | 0 | 0 | 0
231118 | 18.5-70 | 18.5 | -70 | 0 | 0 | 0
231839 | 18.5-70.5 | 18.5 | -70.5 | 0 | 0 | 0
232560 | 18.5-71 | 18.5 | -71 | 0 | 0 | 0
233281 | 18.5-71.5 | 18.5 | -71.5 | 0 | 0 | 0
234002 | 18.5-72 | 18.5 | -72 | 0 | 0 | 0
234723 | 18.5-72.5 | 18.5 | -72.5 | 0 | 0 | 0
235444 | 18.5-73 | 18.5 | -73 | 0 | 0 | 0
236165 | 18.5-73.5 | 18.5 | -73.5 | 0 | 0 | 0
236886 | 18.5-74 | 18.5 | -74 | 0 | 0 | 0
237607 | 18.5-74.5 | 18.5 | -74.5 | 0 | 0 | 0
238328 | 18.5-75 | 18.5 | -75 | 0 | 0 | 0
239049 | 18.5-75.5 | 18.5 | -75.5 | 0 | 0 | 0
239770 | 18.5-76 | 18.5 | -76 | 0 | 0 | 0
240491 | 18.5-76.5 | 18.5 | -76.5 | 0 | 0 | 0
241212 | 18.5-77 | 18.5 | -77 | 0 | 0 | 0
241933 | 18.5-77.5 | 18.5 | -77.5 | 0 | 0 | 0
242654 | 18.5-78 | 18.5 | -78 | 0 | 0 | 0
243375 | 18.5-78.5 | 18.5 | -78.5 | 0 | 0 | 0
244096 | 18.5-79 | 18.5 | -79 | 0 | 0 | 0
244817 | 18.5-79.5 | 18.5 | -79.5 | 0 | 0 | 0
245538 | 18.5-80 | 18.5 | -80 | 0 | 0 | 0
246259 | 18.5-80.5 | 18.5 | -80.5 | 0 | 0 | 0
246980 | 18.5-81 | 18.5 | -81 | 0 | 0 | 0
247701 | 18.5-81.5 | 18.5 | -81.5 | 0 | 0 | 0
248422 | 18.5-82 | 18.5 | -82 | 0 | 0 | 0
249143 | 18.5-82.5 | 18.5 | -82.5 | 0 | 0 | 0
249864 | 18.5-83 | 18.5 | -83 | 0 | 0 | 0
250585 | 18.5-83.5 | 18.5 | -83.5 | 0 | 0 | 0
251306 | 18.5-84 | 18.5 | -84 | 0 | 0 | 0
252027 | 18.5-84.5 | 18.5 | -84.5 | 0 | 0 | 0
252748 | 18.5-85 | 18.5 | -85 | 0 | 0 | 0
253469 | 18.5-85.5 | 18.5 | -85.5 | 0 | 0 | 0
254190 | 18.5-86 | 18.5 | -86 | 0 | 0 | 0
254911 | 18.5-86.5 | 18.5 | -86.5 | 0 | 0 | 0
255632 | 18.5-87 | 18.5 | -87 | 0 | 0 | 0
256353 | 18.5-87.5 | 18.5 | -87.5 | 0 | 0 | 0
257074 | 18.5-88 | 18.5 | -88 | 0 | 0 | 0
257795 | 18.5-88.5 | 18.5 | -88.5 | 0 | 0 | 0
258516 | 18.5-89 | 18.5 | -89 | 0 | 0 | 0
259237 | 18.5-89.5 | 18.5 | -89.5 | 0 | 0 | 0
259958 | 18.5-90 | 18.5 | -90 | 0 | 0 | 0
215257 | 19-59 | 19 | -59 | 0 | 0 | 0
215978 | 19-59.5 | 19 | -59.5 | 0 | 0 | 0
216699 | 19-60 | 19 | -60 | 0 | 0 | 0
217420 | 19-60.5 | 19 | -60.5 | 0 | 0 | 0
218141 | 19-61 | 19 | -61 | 0 | 0 | 0
218862 | 19-61.5 | 19 | -61.5 | 0 | 0 | 0
219583 | 19-62 | 19 | -62 | 0 | 0 | 0
220304 | 19-62.5 | 19 | -62.5 | 0 | 0 | 0
221025 | 19-63 | 19 | -63 | 0 | 0 | 0
221746 | 19-63.5 | 19 | -63.5 | 0 | 0 | 0
222467 | 19-64 | 19 | -64 | 0 | 0 | 0
223188 | 19-64.5 | 19 | -64.5 | 0 | 0 | 0
223909 | 19-65 | 19 | -65 | 0 | 0 | 0
224630 | 19-65.5 | 19 | -65.5 | 0 | 0 | 0
225351 | 19-66 | 19 | -66 | 0 | 0 | 0
226072 | 19-66.5 | 19 | -66.5 | 0 | 0 | 0
226793 | 19-67 | 19 | -67 | 0 | 0 | 0
227514 | 19-67.5 | 19 | -67.5 | 0 | 0 | 0
228235 | 19-68 | 19 | -68 | 0 | 0 | 0
228956 | 19-68.5 | 19 | -68.5 | 0 | 0 | 0
229677 | 19-69 | 19 | -69 | 0 | 0 | 0
230398 | 19-69.5 | 19 | -69.5 | 0 | 0 | 0
231119 | 19-70 | 19 | -70 | 0 | 0 | 0
231840 | 19-70.5 | 19 | -70.5 | 0 | 0 | 0
232561 | 19-71 | 19 | -71 | 0 | 0 | 0
233282 | 19-71.5 | 19 | -71.5 | 0 | 0 | 0
234003 | 19-72 | 19 | -72 | 0 | 0 | 0
234724 | 19-72.5 | 19 | -72.5 | 0 | 0 | 0
235445 | 19-73 | 19 | -73 | 0 | 0 | 0
236166 | 19-73.5 | 19 | -73.5 | 0 | 0 | 0
236887 | 19-74 | 19 | -74 | 0 | 0 | 0
237608 | 19-74.5 | 19 | -74.5 | 0 | 0 | 0
238329 | 19-75 | 19 | -75 | 0 | 0 | 0
239050 | 19-75.5 | 19 | -75.5 | 0 | 0 | 0
239771 | 19-76 | 19 | -76 | 0 | 0 | 0
240492 | 19-76.5 | 19 | -76.5 | 0 | 0 | 0
241213 | 19-77 | 19 | -77 | 0 | 0 | 0
241934 | 19-77.5 | 19 | -77.5 | 0 | 0 | 0
242655 | 19-78 | 19 | -78 | 0 | 0 | 0
243376 | 19-78.5 | 19 | -78.5 | 0 | 0 | 0
244097 | 19-79 | 19 | -79 | 0 | 0 | 0
244818 | 19-79.5 | 19 | -79.5 | 0 | 0 | 0
245539 | 19-80 | 19 | -80 | 0 | 0 | 0
246260 | 19-80.5 | 19 | -80.5 | 0 | 0 | 0
246981 | 19-81 | 19 | -81 | 0 | 0 | 0
247702 | 19-81.5 | 19 | -81.5 | 0 | 0 | 0
248423 | 19-82 | 19 | -82 | 0 | 0 | 0
249144 | 19-82.5 | 19 | -82.5 | 0 | 0 | 0
249865 | 19-83 | 19 | -83 | 0 | 0 | 0
250586 | 19-83.5 | 19 | -83.5 | 0 | 0 | 0
251307 | 19-84 | 19 | -84 | 0 | 0 | 0
252028 | 19-84.5 | 19 | -84.5 | 0 | 0 | 0
252749 | 19-85 | 19 | -85 | 0 | 0 | 0
253470 | 19-85.5 | 19 | -85.5 | 0 | 0 | 0
254191 | 19-86 | 19 | -86 | 0 | 0 | 0
254912 | 19-86.5 | 19 | -86.5 | 0 | 0 | 0
255633 | 19-87 | 19 | -87 | 0 | 0 | 0
256354 | 19-87.5 | 19 | -87.5 | 0 | 0 | 0
257075 | 19-88 | 19 | -88 | 0 | 0 | 0
257796 | 19-88.5 | 19 | -88.5 | 0 | 0 | 0
258517 | 19-89 | 19 | -89 | 0 | 0 | 0
259238 | 19-89.5 | 19 | -89.5 | 0 | 0 | 0
259959 | 19-90 | 19 | -90 | 0 | 0 | 0
215258 | 19.5-59 | 19.5 | -59 | 0 | 0 | 0
215979 | 19.5-59.5 | 19.5 | -59.5 | 0 | 0 | 0
216700 | 19.5-60 | 19.5 | -60 | 0 | 0 | 0
217421 | 19.5-60.5 | 19.5 | -60.5 | 0 | 0 | 0
218142 | 19.5-61 | 19.5 | -61 | 0 | 0 | 0
218863 | 19.5-61.5 | 19.5 | -61.5 | 0 | 0 | 0
219584 | 19.5-62 | 19.5 | -62 | 0 | 0 | 0
220305 | 19.5-62.5 | 19.5 | -62.5 | 0 | 0 | 0
221026 | 19.5-63 | 19.5 | -63 | 0 | 0 | 0
221747 | 19.5-63.5 | 19.5 | -63.5 | 0 | 0 | 0
222468 | 19.5-64 | 19.5 | -64 | 0 | 0 | 0
223189 | 19.5-64.5 | 19.5 | -64.5 | 0 | 0 | 0
223910 | 19.5-65 | 19.5 | -65 | 0 | 0 | 0
224631 | 19.5-65.5 | 19.5 | -65.5 | 0 | 0 | 0
225352 | 19.5-66 | 19.5 | -66 | 0 | 0 | 0
226073 | 19.5-66.5 | 19.5 | -66.5 | 0 | 0 | 0
226794 | 19.5-67 | 19.5 | -67 | 0 | 0 | 0
227515 | 19.5-67.5 | 19.5 | -67.5 | 0 | 0 | 0
228236 | 19.5-68 | 19.5 | -68 | 0 | 0 | 0
228957 | 19.5-68.5 | 19.5 | -68.5 | 0 | 0 | 0
229678 | 19.5-69 | 19.5 | -69 | 0 | 0 | 0
230399 | 19.5-69.5 | 19.5 | -69.5 | 0 | 0 | 0
231120 | 19.5-70 | 19.5 | -70 | 0 | 0 | 0
231841 | 19.5-70.5 | 19.5 | -70.5 | 0 | 0 | 0
232562 | 19.5-71 | 19.5 | -71 | 0 | 0 | 0
233283 | 19.5-71.5 | 19.5 | -71.5 | 0 | 0 | 0
234004 | 19.5-72 | 19.5 | -72 | 0 | 0 | 0
234725 | 19.5-72.5 | 19.5 | -72.5 | 0 | 0 | 0
235446 | 19.5-73 | 19.5 | -73 | 0 | 0 | 0
236167 | 19.5-73.5 | 19.5 | -73.5 | 0 | 0 | 0
236888 | 19.5-74 | 19.5 | -74 | 0 | 0 | 0
237609 | 19.5-74.5 | 19.5 | -74.5 | 0 | 0 | 0
238330 | 19.5-75 | 19.5 | -75 | 0 | 0 | 0
239051 | 19.5-75.5 | 19.5 | -75.5 | 0 | 0 | 0
239772 | 19.5-76 | 19.5 | -76 | 0 | 0 | 0
240493 | 19.5-76.5 | 19.5 | -76.5 | 0 | 0 | 0
241214 | 19.5-77 | 19.5 | -77 | 0 | 0 | 0
241935 | 19.5-77.5 | 19.5 | -77.5 | 0 | 0 | 0
242656 | 19.5-78 | 19.5 | -78 | 0 | 0 | 0
243377 | 19.5-78.5 | 19.5 | -78.5 | 0 | 0 | 0
244098 | 19.5-79 | 19.5 | -79 | 0 | 0 | 0
244819 | 19.5-79.5 | 19.5 | -79.5 | 0 | 0 | 0
245540 | 19.5-80 | 19.5 | -80 | 0 | 0 | 0
246261 | 19.5-80.5 | 19.5 | -80.5 | 0 | 0 | 0
246982 | 19.5-81 | 19.5 | -81 | 0 | 0 | 0
247703 | 19.5-81.5 | 19.5 | -81.5 | 0 | 0 | 0
248424 | 19.5-82 | 19.5 | -82 | 0 | 0 | 0
249145 | 19.5-82.5 | 19.5 | -82.5 | 0 | 0 | 0
249866 | 19.5-83 | 19.5 | -83 | 0 | 0 | 0
250587 | 19.5-83.5 | 19.5 | -83.5 | 0 | 0 | 0
251308 | 19.5-84 | 19.5 | -84 | 0 | 0 | 0
252029 | 19.5-84.5 | 19.5 | -84.5 | 0 | 0 | 0
252750 | 19.5-85 | 19.5 | -85 | 0 | 0 | 0
253471 | 19.5-85.5 | 19.5 | -85.5 | 0 | 0 | 0
254192 | 19.5-86 | 19.5 | -86 | 0 | 0 | 0
254913 | 19.5-86.5 | 19.5 | -86.5 | 0 | 0 | 0
255634 | 19.5-87 | 19.5 | -87 | 0 | 0 | 0
256355 | 19.5-87.5 | 19.5 | -87.5 | 0 | 0 | 0
257076 | 19.5-88 | 19.5 | -88 | 0 | 0 | 0
257797 | 19.5-88.5 | 19.5 | -88.5 | 0 | 0 | 0
258518 | 19.5-89 | 19.5 | -89 | 0 | 0 | 0
259239 | 19.5-89.5 | 19.5 | -89.5 | 0 | 0 | 0
259960 | 19.5-90 | 19.5 | -90 | 0 | 0 | 0
215259 | 20-59 | 20 | -59 | 0 | 0 | 0
215980 | 20-59.5 | 20 | -59.5 | 0 | 0 | 0
216701 | 20-60 | 20 | -60 | 0 | 0 | 0
217422 | 20-60.5 | 20 | -60.5 | 0 | 0 | 0
218143 | 20-61 | 20 | -61 | 0 | 0 | 0
218864 | 20-61.5 | 20 | -61.5 | 0 | 0 | 0
219585 | 20-62 | 20 | -62 | 0 | 0 | 0
220306 | 20-62.5 | 20 | -62.5 | 0 | 0 | 0
221027 | 20-63 | 20 | -63 | 0 | 0 | 0
221748 | 20-63.5 | 20 | -63.5 | 0 | 0 | 0
222469 | 20-64 | 20 | -64 | 0 | 0 | 0
223190 | 20-64.5 | 20 | -64.5 | 0 | 0 | 0
223911 | 20-65 | 20 | -65 | 0 | 0 | 0
224632 | 20-65.5 | 20 | -65.5 | 0 | 0 | 0
225353 | 20-66 | 20 | -66 | 0 | 0 | 0
226074 | 20-66.5 | 20 | -66.5 | 0 | 0 | 0
226795 | 20-67 | 20 | -67 | 0 | 0 | 0
227516 | 20-67.5 | 20 | -67.5 | 0 | 0 | 0
228237 | 20-68 | 20 | -68 | 0 | 0 | 0
228958 | 20-68.5 | 20 | -68.5 | 0 | 0 | 0
229679 | 20-69 | 20 | -69 | 0 | 0 | 0
230400 | 20-69.5 | 20 | -69.5 | 0 | 0 | 0
231121 | 20-70 | 20 | -70 | 0 | 0 | 0
231842 | 20-70.5 | 20 | -70.5 | 0 | 0 | 0
232563 | 20-71 | 20 | -71 | 0 | 0 | 0
233284 | 20-71.5 | 20 | -71.5 | 0 | 0 | 0
234005 | 20-72 | 20 | -72 | 0 | 0 | 0
234726 | 20-72.5 | 20 | -72.5 | 0 | 0 | 0
235447 | 20-73 | 20 | -73 | 0 | 0 | 0
236168 | 20-73.5 | 20 | -73.5 | 0 | 0 | 0
236889 | 20-74 | 20 | -74 | 0 | 0 | 0
237610 | 20-74.5 | 20 | -74.5 | 0 | 0 | 0
238331 | 20-75 | 20 | -75 | 0 | 0 | 0
239052 | 20-75.5 | 20 | -75.5 | 0 | 0 | 0
239773 | 20-76 | 20 | -76 | 0 | 0 | 0
240494 | 20-76.5 | 20 | -76.5 | 0 | 0 | 0
241215 | 20-77 | 20 | -77 | 0 | 0 | 0
241936 | 20-77.5 | 20 | -77.5 | 0 | 0 | 0
242657 | 20-78 | 20 | -78 | 0 | 0 | 0
243378 | 20-78.5 | 20 | -78.5 | 0 | 0 | 0
244099 | 20-79 | 20 | -79 | 0 | 0 | 0
244820 | 20-79.5 | 20 | -79.5 | 0 | 0 | 0
245541 | 20-80 | 20 | -80 | 0 | 0 | 0
246262 | 20-80.5 | 20 | -80.5 | 0 | 0 | 0
246983 | 20-81 | 20 | -81 | 0 | 0 | 0
247704 | 20-81.5 | 20 | -81.5 | 0 | 0 | 0
248425 | 20-82 | 20 | -82 | 0 | 0 | 0
249146 | 20-82.5 | 20 | -82.5 | 0 | 0 | 0
249867 | 20-83 | 20 | -83 | 0 | 0 | 0
250588 | 20-83.5 | 20 | -83.5 | 0 | 0 | 0
251309 | 20-84 | 20 | -84 | 0 | 0 | 0
252030 | 20-84.5 | 20 | -84.5 | 0 | 0 | 0
252751 | 20-85 | 20 | -85 | 0 | 0 | 0
253472 | 20-85.5 | 20 | -85.5 | 0 | 0 | 0
254193 | 20-86 | 20 | -86 | 0 | 0 | 0
254914 | 20-86.5 | 20 | -86.5 | 0 | 0 | 0
255635 | 20-87 | 20 | -87 | 0 | 0 | 0
256356 | 20-87.5 | 20 | -87.5 | 0 | 0 | 0
257077 | 20-88 | 20 | -88 | 0 | 0 | 0
257798 | 20-88.5 | 20 | -88.5 | 0 | 0 | 0
258519 | 20-89 | 20 | -89 | 0 | 0 | 0
259240 | 20-89.5 | 20 | -89.5 | 0 | 0 | 0
259961 | 20-90 | 20 | -90 | 0 | 0 | 0
215260 | 20.5-59 | 20.5 | -59 | 0 | 0 | 0
215981 | 20.5-59.5 | 20.5 | -59.5 | 0 | 0 | 0
216702 | 20.5-60 | 20.5 | -60 | 0 | 0 | 0
217423 | 20.5-60.5 | 20.5 | -60.5 | 0 | 0 | 0
218144 | 20.5-61 | 20.5 | -61 | 0 | 0 | 0
218865 | 20.5-61.5 | 20.5 | -61.5 | 0 | 0 | 0
219586 | 20.5-62 | 20.5 | -62 | 0 | 0 | 0
220307 | 20.5-62.5 | 20.5 | -62.5 | 0 | 0 | 0
221028 | 20.5-63 | 20.5 | -63 | 0 | 0 | 0
221749 | 20.5-63.5 | 20.5 | -63.5 | 0 | 0 | 0
222470 | 20.5-64 | 20.5 | -64 | 0 | 0 | 0
223191 | 20.5-64.5 | 20.5 | -64.5 | 0 | 0 | 0
223912 | 20.5-65 | 20.5 | -65 | 0 | 0 | 0
224633 | 20.5-65.5 | 20.5 | -65.5 | 0 | 0 | 0
225354 | 20.5-66 | 20.5 | -66 | 0 | 0 | 0
226075 | 20.5-66.5 | 20.5 | -66.5 | 0 | 0 | 0
226796 | 20.5-67 | 20.5 | -67 | 0 | 0 | 0
227517 | 20.5-67.5 | 20.5 | -67.5 | 0 | 0 | 0
228238 | 20.5-68 | 20.5 | -68 | 0 | 0 | 0
228959 | 20.5-68.5 | 20.5 | -68.5 | 0 | 0 | 0
229680 | 20.5-69 | 20.5 | -69 | 0 | 0 | 0
230401 | 20.5-69.5 | 20.5 | -69.5 | 0 | 0 | 0
231122 | 20.5-70 | 20.5 | -70 | 0 | 0 | 0
231843 | 20.5-70.5 | 20.5 | -70.5 | 0 | 0 | 0
232564 | 20.5-71 | 20.5 | -71 | 0 | 0 | 0
233285 | 20.5-71.5 | 20.5 | -71.5 | 0 | 0 | 0
234006 | 20.5-72 | 20.5 | -72 | 0 | 0 | 0
234727 | 20.5-72.5 | 20.5 | -72.5 | 0 | 0 | 0
235448 | 20.5-73 | 20.5 | -73 | 0 | 0 | 0
236169 | 20.5-73.5 | 20.5 | -73.5 | 0 | 0 | 0
236890 | 20.5-74 | 20.5 | -74 | 0 | 0 | 0
237611 | 20.5-74.5 | 20.5 | -74.5 | 0 | 0 | 0
238332 | 20.5-75 | 20.5 | -75 | 0 | 0 | 0
239053 | 20.5-75.5 | 20.5 | -75.5 | 0 | 0 | 0
239774 | 20.5-76 | 20.5 | -76 | 0 | 0 | 0
240495 | 20.5-76.5 | 20.5 | -76.5 | 0 | 0 | 0
241216 | 20.5-77 | 20.5 | -77 | 0 | 0 | 0
241937 | 20.5-77.5 | 20.5 | -77.5 | 0 | 0 | 0
242658 | 20.5-78 | 20.5 | -78 | 0 | 0 | 0
243379 | 20.5-78.5 | 20.5 | -78.5 | 0 | 0 | 0
244100 | 20.5-79 | 20.5 | -79 | 0 | 0 | 0
244821 | 20.5-79.5 | 20.5 | -79.5 | 0 | 0 | 0
245542 | 20.5-80 | 20.5 | -80 | 0 | 0 | 0
246263 | 20.5-80.5 | 20.5 | -80.5 | 0 | 0 | 0
246984 | 20.5-81 | 20.5 | -81 | 0 | 0 | 0
247705 | 20.5-81.5 | 20.5 | -81.5 | 0 | 0 | 0
248426 | 20.5-82 | 20.5 | -82 | 0 | 0 | 0
249147 | 20.5-82.5 | 20.5 | -82.5 | 0 | 0 | 0
249868 | 20.5-83 | 20.5 | -83 | 0 | 0 | 0
250589 | 20.5-83.5 | 20.5 | -83.5 | 0 | 0 | 0
251310 | 20.5-84 | 20.5 | -84 | 0 | 0 | 0
252031 | 20.5-84.5 | 20.5 | -84.5 | 0 | 0 | 0
252752 | 20.5-85 | 20.5 | -85 | 0 | 0 | 0
253473 | 20.5-85.5 | 20.5 | -85.5 | 0 | 0 | 0
254194 | 20.5-86 | 20.5 | -86 | 0 | 0 | 0
254915 | 20.5-86.5 | 20.5 | -86.5 | 0 | 0 | 0
255636 | 20.5-87 | 20.5 | -87 | 0 | 0 | 0
256357 | 20.5-87.5 | 20.5 | -87.5 | 0 | 0 | 0
257078 | 20.5-88 | 20.5 | -88 | 0 | 0 | 0
257799 | 20.5-88.5 | 20.5 | -88.5 | 0 | 0 | 0
258520 | 20.5-89 | 20.5 | -89 | 0 | 0 | 0
259241 | 20.5-89.5 | 20.5 | -89.5 | 0 | 0 | 0
259962 | 20.5-90 | 20.5 | -90 | 0 | 0 | 0
215261 | 21-59 | 21 | -59 | 0 | 0 | 0
215982 | 21-59.5 | 21 | -59.5 | 0 | 0 | 0
216703 | 21-60 | 21 | -60 | 0 | 0 | 0
217424 | 21-60.5 | 21 | -60.5 | 0 | 0 | 0
218145 | 21-61 | 21 | -61 | 0 | 0 | 0
218866 | 21-61.5 | 21 | -61.5 | 0 | 0 | 0
219587 | 21-62 | 21 | -62 | 0 | 0 | 0
220308 | 21-62.5 | 21 | -62.5 | 0 | 0 | 0
221029 | 21-63 | 21 | -63 | 0 | 0 | 0
221750 | 21-63.5 | 21 | -63.5 | 0 | 0 | 0
222471 | 21-64 | 21 | -64 | 0 | 0 | 0
223192 | 21-64.5 | 21 | -64.5 | 0 | 0 | 0
223913 | 21-65 | 21 | -65 | 0 | 0 | 0
224634 | 21-65.5 | 21 | -65.5 | 0 | 0 | 0
225355 | 21-66 | 21 | -66 | 0 | 0 | 0
226076 | 21-66.5 | 21 | -66.5 | 0 | 0 | 0
226797 | 21-67 | 21 | -67 | 0 | 0 | 0
227518 | 21-67.5 | 21 | -67.5 | 0 | 0 | 0
228239 | 21-68 | 21 | -68 | 0 | 0 | 0
228960 | 21-68.5 | 21 | -68.5 | 0 | 0 | 0
229681 | 21-69 | 21 | -69 | 0 | 0 | 0
230402 | 21-69.5 | 21 | -69.5 | 0 | 0 | 0
231123 | 21-70 | 21 | -70 | 0 | 0 | 0
231844 | 21-70.5 | 21 | -70.5 | 0 | 0 | 0
232565 | 21-71 | 21 | -71 | 0 | 0 | 0
233286 | 21-71.5 | 21 | -71.5 | 0 | 0 | 0
234007 | 21-72 | 21 | -72 | 0 | 0 | 0
234728 | 21-72.5 | 21 | -72.5 | 0 | 0 | 0
235449 | 21-73 | 21 | -73 | 0 | 0 | 0
236170 | 21-73.5 | 21 | -73.5 | 0 | 0 | 0
236891 | 21-74 | 21 | -74 | 0 | 0 | 0
237612 | 21-74.5 | 21 | -74.5 | 0 | 0 | 0
238333 | 21-75 | 21 | -75 | 0 | 0 | 0
239054 | 21-75.5 | 21 | -75.5 | 0 | 0 | 0
239775 | 21-76 | 21 | -76 | 0 | 0 | 0
240496 | 21-76.5 | 21 | -76.5 | 0 | 0 | 0
241217 | 21-77 | 21 | -77 | 0 | 0 | 0
241938 | 21-77.5 | 21 | -77.5 | 0 | 0 | 0
242659 | 21-78 | 21 | -78 | 0 | 0 | 0
243380 | 21-78.5 | 21 | -78.5 | 0 | 0 | 0
244101 | 21-79 | 21 | -79 | 0 | 0 | 0
244822 | 21-79.5 | 21 | -79.5 | 0 | 0 | 0
245543 | 21-80 | 21 | -80 | 0 | 0 | 0
246264 | 21-80.5 | 21 | -80.5 | 0 | 0 | 0
246985 | 21-81 | 21 | -81 | 0 | 0 | 0
247706 | 21-81.5 | 21 | -81.5 | 0 | 0 | 0
248427 | 21-82 | 21 | -82 | 0 | 0 | 0
249148 | 21-82.5 | 21 | -82.5 | 0 | 0 | 0
249869 | 21-83 | 21 | -83 | 0 | 0 | 0
250590 | 21-83.5 | 21 | -83.5 | 0 | 0 | 0
251311 | 21-84 | 21 | -84 | 0 | 0 | 0
252032 | 21-84.5 | 21 | -84.5 | 0 | 0 | 0
252753 | 21-85 | 21 | -85 | 0 | 0 | 0
253474 | 21-85.5 | 21 | -85.5 | 0 | 0 | 0
254195 | 21-86 | 21 | -86 | 0 | 0 | 0
254916 | 21-86.5 | 21 | -86.5 | 0 | 0 | 0
255637 | 21-87 | 21 | -87 | 0 | 0 | 0
256358 | 21-87.5 | 21 | -87.5 | 0 | 0 | 0
257079 | 21-88 | 21 | -88 | 0 | 0 | 0
257800 | 21-88.5 | 21 | -88.5 | 0 | 0 | 0
258521 | 21-89 | 21 | -89 | 0 | 0 | 0
259242 | 21-89.5 | 21 | -89.5 | 0 | 0 | 0
259963 | 21-90 | 21 | -90 | 0 | 0 | 0
215262 | 21.5-59 | 21.5 | -59 | 0 | 0 | 0
215983 | 21.5-59.5 | 21.5 | -59.5 | 0 | 0 | 0
216704 | 21.5-60 | 21.5 | -60 | 0 | 0 | 0
217425 | 21.5-60.5 | 21.5 | -60.5 | 0 | 0 | 0
218146 | 21.5-61 | 21.5 | -61 | 0 | 0 | 0
218867 | 21.5-61.5 | 21.5 | -61.5 | 0 | 0 | 0
219588 | 21.5-62 | 21.5 | -62 | 0 | 0 | 0
220309 | 21.5-62.5 | 21.5 | -62.5 | 0 | 0 | 0
221030 | 21.5-63 | 21.5 | -63 | 0 | 0 | 0
221751 | 21.5-63.5 | 21.5 | -63.5 | 0 | 0 | 0
222472 | 21.5-64 | 21.5 | -64 | 0 | 0 | 0
223193 | 21.5-64.5 | 21.5 | -64.5 | 0 | 0 | 0
223914 | 21.5-65 | 21.5 | -65 | 0 | 0 | 0
224635 | 21.5-65.5 | 21.5 | -65.5 | 0 | 0 | 0
225356 | 21.5-66 | 21.5 | -66 | 0 | 0 | 0
226077 | 21.5-66.5 | 21.5 | -66.5 | 0 | 0 | 0
226798 | 21.5-67 | 21.5 | -67 | 0 | 0 | 0
227519 | 21.5-67.5 | 21.5 | -67.5 | 0 | 0 | 0
228240 | 21.5-68 | 21.5 | -68 | 0 | 0 | 0
228961 | 21.5-68.5 | 21.5 | -68.5 | 0 | 0 | 0
229682 | 21.5-69 | 21.5 | -69 | 0 | 0 | 0
230403 | 21.5-69.5 | 21.5 | -69.5 | 0 | 0 | 0
231124 | 21.5-70 | 21.5 | -70 | 0 | 0 | 0
231845 | 21.5-70.5 | 21.5 | -70.5 | 0 | 0 | 0
232566 | 21.5-71 | 21.5 | -71 | 0 | 0 | 0
233287 | 21.5-71.5 | 21.5 | -71.5 | 0 | 0 | 0
234008 | 21.5-72 | 21.5 | -72 | 0 | 0 | 0
234729 | 21.5-72.5 | 21.5 | -72.5 | 0 | 0 | 0
235450 | 21.5-73 | 21.5 | -73 | 0 | 0 | 0
236171 | 21.5-73.5 | 21.5 | -73.5 | 0 | 0 | 0
236892 | 21.5-74 | 21.5 | -74 | 0 | 0 | 0
237613 | 21.5-74.5 | 21.5 | -74.5 | 0 | 0 | 0
238334 | 21.5-75 | 21.5 | -75 | 0 | 0 | 0
239055 | 21.5-75.5 | 21.5 | -75.5 | 0 | 0 | 0
239776 | 21.5-76 | 21.5 | -76 | 0 | 0 | 0
240497 | 21.5-76.5 | 21.5 | -76.5 | 0 | 0 | 0
241218 | 21.5-77 | 21.5 | -77 | 0 | 0 | 0
241939 | 21.5-77.5 | 21.5 | -77.5 | 0 | 0 | 0
242660 | 21.5-78 | 21.5 | -78 | 0 | 0 | 0
243381 | 21.5-78.5 | 21.5 | -78.5 | 0 | 0 | 0
244102 | 21.5-79 | 21.5 | -79 | 0 | 0 | 0
244823 | 21.5-79.5 | 21.5 | -79.5 | 0 | 0 | 0
245544 | 21.5-80 | 21.5 | -80 | 0 | 0 | 0
246265 | 21.5-80.5 | 21.5 | -80.5 | 0 | 0 | 0
246986 | 21.5-81 | 21.5 | -81 | 0 | 0 | 0
247707 | 21.5-81.5 | 21.5 | -81.5 | 0 | 0 | 0
248428 | 21.5-82 | 21.5 | -82 | 0 | 0 | 0
249149 | 21.5-82.5 | 21.5 | -82.5 | 0 | 0 | 0
249870 | 21.5-83 | 21.5 | -83 | 0 | 0 | 0
250591 | 21.5-83.5 | 21.5 | -83.5 | 0 | 0 | 0
251312 | 21.5-84 | 21.5 | -84 | 0 | 0 | 0
252033 | 21.5-84.5 | 21.5 | -84.5 | 0 | 0 | 0
252754 | 21.5-85 | 21.5 | -85 | 0 | 0 | 0
253475 | 21.5-85.5 | 21.5 | -85.5 | 0 | 0 | 0
254196 | 21.5-86 | 21.5 | -86 | 0 | 0 | 0
254917 | 21.5-86.5 | 21.5 | -86.5 | 0 | 0 | 0
255638 | 21.5-87 | 21.5 | -87 | 0 | 0 | 0
256359 | 21.5-87.5 | 21.5 | -87.5 | 0 | 0 | 0
257080 | 21.5-88 | 21.5 | -88 | 0 | 0 | 0
257801 | 21.5-88.5 | 21.5 | -88.5 | 0 | 0 | 0
258522 | 21.5-89 | 21.5 | -89 | 0 | 0 | 0
259243 | 21.5-89.5 | 21.5 | -89.5 | 0 | 0 | 0
259964 | 21.5-90 | 21.5 | -90 | 0 | 0 | 0
215263 | 22-59 | 22 | -59 | 0 | 0 | 0
215984 | 22-59.5 | 22 | -59.5 | 0 | 0 | 0
216705 | 22-60 | 22 | -60 | 0 | 0 | 0
217426 | 22-60.5 | 22 | -60.5 | 0 | 0 | 0
218147 | 22-61 | 22 | -61 | 0 | 0 | 0
218868 | 22-61.5 | 22 | -61.5 | 0 | 0 | 0
219589 | 22-62 | 22 | -62 | 0 | 0 | 0
220310 | 22-62.5 | 22 | -62.5 | 0 | 0 | 0
221031 | 22-63 | 22 | -63 | 0 | 0 | 0
221752 | 22-63.5 | 22 | -63.5 | 0 | 0 | 0
222473 | 22-64 | 22 | -64 | 0 | 0 | 0
223194 | 22-64.5 | 22 | -64.5 | 0 | 0 | 0
223915 | 22-65 | 22 | -65 | 0 | 0 | 0
224636 | 22-65.5 | 22 | -65.5 | 0 | 0 | 0
225357 | 22-66 | 22 | -66 | 0 | 0 | 0
226078 | 22-66.5 | 22 | -66.5 | 0 | 0 | 0
226799 | 22-67 | 22 | -67 | 0 | 0 | 0
227520 | 22-67.5 | 22 | -67.5 | 0 | 0 | 0
228241 | 22-68 | 22 | -68 | 0 | 0 | 0
228962 | 22-68.5 | 22 | -68.5 | 0 | 0 | 0
229683 | 22-69 | 22 | -69 | 0 | 0 | 0
230404 | 22-69.5 | 22 | -69.5 | 0 | 0 | 0
231125 | 22-70 | 22 | -70 | 0 | 0 | 0
231846 | 22-70.5 | 22 | -70.5 | 0 | 0 | 0
232567 | 22-71 | 22 | -71 | 0 | 0 | 0
233288 | 22-71.5 | 22 | -71.5 | 0 | 0 | 0
234009 | 22-72 | 22 | -72 | 0 | 0 | 0
234730 | 22-72.5 | 22 | -72.5 | 0 | 0 | 0
235451 | 22-73 | 22 | -73 | 0 | 0 | 0
236172 | 22-73.5 | 22 | -73.5 | 0 | 0 | 0
236893 | 22-74 | 22 | -74 | 0 | 0 | 0
237614 | 22-74.5 | 22 | -74.5 | 0 | 0 | 0
238335 | 22-75 | 22 | -75 | 0 | 0 | 0
239056 | 22-75.5 | 22 | -75.5 | 0 | 0 | 0
239777 | 22-76 | 22 | -76 | 0 | 0 | 0
240498 | 22-76.5 | 22 | -76.5 | 0 | 0 | 0
241219 | 22-77 | 22 | -77 | 0 | 0 | 0
241940 | 22-77.5 | 22 | -77.5 | 0 | 0 | 0
242661 | 22-78 | 22 | -78 | 0 | 0 | 0
243382 | 22-78.5 | 22 | -78.5 | 0 | 0 | 0
244103 | 22-79 | 22 | -79 | 0 | 0 | 0
244824 | 22-79.5 | 22 | -79.5 | 0 | 0 | 0
245545 | 22-80 | 22 | -80 | 0 | 0 | 0
246266 | 22-80.5 | 22 | -80.5 | 0 | 0 | 0
246987 | 22-81 | 22 | -81 | 0 | 0 | 0
247708 | 22-81.5 | 22 | -81.5 | 0 | 0 | 0
248429 | 22-82 | 22 | -82 | 0 | 0 | 0
249150 | 22-82.5 | 22 | -82.5 | 0 | 0 | 0
249871 | 22-83 | 22 | -83 | 0 | 0 | 0
250592 | 22-83.5 | 22 | -83.5 | 0 | 0 | 0
251313 | 22-84 | 22 | -84 | 0 | 0 | 0
252034 | 22-84.5 | 22 | -84.5 | 0 | 0 | 0
252755 | 22-85 | 22 | -85 | 0 | 0 | 0
253476 | 22-85.5 | 22 | -85.5 | 0 | 0 | 0
254197 | 22-86 | 22 | -86 | 0 | 0 | 0
254918 | 22-86.5 | 22 | -86.5 | 0 | 0 | 0
255639 | 22-87 | 22 | -87 | 0 | 0 | 0
256360 | 22-87.5 | 22 | -87.5 | 0 | 0 | 0
257081 | 22-88 | 22 | -88 | 0 | 0 | 0
257802 | 22-88.5 | 22 | -88.5 | 0 | 0 | 0
258523 | 22-89 | 22 | -89 | 0 | 0 | 0
259244 | 22-89.5 | 22 | -89.5 | 0 | 0 | 0
259965 | 22-90 | 22 | -90 | 0 | 0 | 0
215264 | 22.5-59 | 22.5 | -59 | 0 | 0 | 0
215985 | 22.5-59.5 | 22.5 | -59.5 | 0 | 0 | 0
216706 | 22.5-60 | 22.5 | -60 | 0 | 0 | 0
217427 | 22.5-60.5 | 22.5 | -60.5 | 0 | 0 | 0
218148 | 22.5-61 | 22.5 | -61 | 0 | 0 | 0
218869 | 22.5-61.5 | 22.5 | -61.5 | 0 | 0 | 0
219590 | 22.5-62 | 22.5 | -62 | 0 | 0 | 0
220311 | 22.5-62.5 | 22.5 | -62.5 | 0 | 0 | 0
221032 | 22.5-63 | 22.5 | -63 | 0 | 0 | 0
221753 | 22.5-63.5 | 22.5 | -63.5 | 0 | 0 | 0
222474 | 22.5-64 | 22.5 | -64 | 0 | 0 | 0
223195 | 22.5-64.5 | 22.5 | -64.5 | 0 | 0 | 0
223916 | 22.5-65 | 22.5 | -65 | 0 | 0 | 0
224637 | 22.5-65.5 | 22.5 | -65.5 | 0 | 0 | 0
225358 | 22.5-66 | 22.5 | -66 | 0 | 0 | 0
226079 | 22.5-66.5 | 22.5 | -66.5 | 0 | 0 | 0
226800 | 22.5-67 | 22.5 | -67 | 0 | 0 | 0
227521 | 22.5-67.5 | 22.5 | -67.5 | 0 | 0 | 0
228242 | 22.5-68 | 22.5 | -68 | 0 | 0 | 0
228963 | 22.5-68.5 | 22.5 | -68.5 | 0 | 0 | 0
229684 | 22.5-69 | 22.5 | -69 | 0 | 0 | 0
230405 | 22.5-69.5 | 22.5 | -69.5 | 0 | 0 | 0
231126 | 22.5-70 | 22.5 | -70 | 0 | 0 | 0
231847 | 22.5-70.5 | 22.5 | -70.5 | 0 | 0 | 0
232568 | 22.5-71 | 22.5 | -71 | 0 | 0 | 0
233289 | 22.5-71.5 | 22.5 | -71.5 | 0 | 0 | 0
234010 | 22.5-72 | 22.5 | -72 | 0 | 0 | 0
234731 | 22.5-72.5 | 22.5 | -72.5 | 0 | 0 | 0
235452 | 22.5-73 | 22.5 | -73 | 0 | 0 | 0
236173 | 22.5-73.5 | 22.5 | -73.5 | 0 | 0 | 0
236894 | 22.5-74 | 22.5 | -74 | 0 | 0 | 0
237615 | 22.5-74.5 | 22.5 | -74.5 | 0 | 0 | 0
238336 | 22.5-75 | 22.5 | -75 | 0 | 0 | 0
239057 | 22.5-75.5 | 22.5 | -75.5 | 0 | 0 | 0
239778 | 22.5-76 | 22.5 | -76 | 0 | 0 | 0
240499 | 22.5-76.5 | 22.5 | -76.5 | 0 | 0 | 0
241220 | 22.5-77 | 22.5 | -77 | 0 | 0 | 0
241941 | 22.5-77.5 | 22.5 | -77.5 | 0 | 0 | 0
242662 | 22.5-78 | 22.5 | -78 | 0 | 0 | 0
243383 | 22.5-78.5 | 22.5 | -78.5 | 0 | 0 | 0
244104 | 22.5-79 | 22.5 | -79 | 0 | 0 | 0
244825 | 22.5-79.5 | 22.5 | -79.5 | 0 | 0 | 0
245546 | 22.5-80 | 22.5 | -80 | 0 | 0 | 0
246267 | 22.5-80.5 | 22.5 | -80.5 | 0 | 0 | 0
246988 | 22.5-81 | 22.5 | -81 | 0 | 0 | 0
247709 | 22.5-81.5 | 22.5 | -81.5 | 0 | 0 | 0
248430 | 22.5-82 | 22.5 | -82 | 0 | 0 | 0
249151 | 22.5-82.5 | 22.5 | -82.5 | 0 | 0 | 0
249872 | 22.5-83 | 22.5 | -83 | 0 | 0 | 0
250593 | 22.5-83.5 | 22.5 | -83.5 | 0 | 0 | 0
251314 | 22.5-84 | 22.5 | -84 | 0 | 0 | 0
252035 | 22.5-84.5 | 22.5 | -84.5 | 0 | 0 | 0
252756 | 22.5-85 | 22.5 | -85 | 0 | 0 | 0
253477 | 22.5-85.5 | 22.5 | -85.5 | 0 | 0 | 0
254198 | 22.5-86 | 22.5 | -86 | 0 | 0 | 0
254919 | 22.5-86.5 | 22.5 | -86.5 | 0 | 0 | 0
255640 | 22.5-87 | 22.5 | -87 | 0 | 0 | 0
256361 | 22.5-87.5 | 22.5 | -87.5 | 0 | 0 | 0
257082 | 22.5-88 | 22.5 | -88 | 0 | 0 | 0
257803 | 22.5-88.5 | 22.5 | -88.5 | 0 | 0 | 0
258524 | 22.5-89 | 22.5 | -89 | 0 | 0 | 0
259245 | 22.5-89.5 | 22.5 | -89.5 | 0 | 0 | 0
259966 | 22.5-90 | 22.5 | -90 | 0 | 0 | 0
215265 | 23-59 | 23 | -59 | 0 | 0 | 0
215986 | 23-59.5 | 23 | -59.5 | 0 | 0 | 0
216707 | 23-60 | 23 | -60 | 0 | 0 | 0
217428 | 23-60.5 | 23 | -60.5 | 0 | 0 | 0
218149 | 23-61 | 23 | -61 | 0 | 0 | 0
218870 | 23-61.5 | 23 | -61.5 | 0 | 0 | 0
219591 | 23-62 | 23 | -62 | 0 | 0 | 0
220312 | 23-62.5 | 23 | -62.5 | 0 | 0 | 0
221033 | 23-63 | 23 | -63 | 0 | 0 | 0
221754 | 23-63.5 | 23 | -63.5 | 0 | 0 | 0
222475 | 23-64 | 23 | -64 | 0 | 0 | 0
223196 | 23-64.5 | 23 | -64.5 | 0 | 0 | 0
223917 | 23-65 | 23 | -65 | 0 | 0 | 0
224638 | 23-65.5 | 23 | -65.5 | 0 | 0 | 0
225359 | 23-66 | 23 | -66 | 0 | 0 | 0
226080 | 23-66.5 | 23 | -66.5 | 0 | 0 | 0
226801 | 23-67 | 23 | -67 | 0 | 0 | 0
227522 | 23-67.5 | 23 | -67.5 | 0 | 0 | 0
228243 | 23-68 | 23 | -68 | 0 | 0 | 0
228964 | 23-68.5 | 23 | -68.5 | 0 | 0 | 0
229685 | 23-69 | 23 | -69 | 0 | 0 | 0
230406 | 23-69.5 | 23 | -69.5 | 0 | 0 | 0
231127 | 23-70 | 23 | -70 | 0 | 0 | 0
231848 | 23-70.5 | 23 | -70.5 | 0 | 0 | 0
232569 | 23-71 | 23 | -71 | 0 | 0 | 0
233290 | 23-71.5 | 23 | -71.5 | 0 | 0 | 0
234011 | 23-72 | 23 | -72 | 0 | 0 | 0
234732 | 23-72.5 | 23 | -72.5 | 0 | 0 | 0
235453 | 23-73 | 23 | -73 | 0 | 0 | 0
236174 | 23-73.5 | 23 | -73.5 | 0 | 0 | 0
236895 | 23-74 | 23 | -74 | 0 | 0 | 0
237616 | 23-74.5 | 23 | -74.5 | 0 | 0 | 0
238337 | 23-75 | 23 | -75 | 0 | 0 | 0
239058 | 23-75.5 | 23 | -75.5 | 0 | 0 | 0
239779 | 23-76 | 23 | -76 | 0 | 0 | 0
240500 | 23-76.5 | 23 | -76.5 | 0 | 0 | 0
241221 | 23-77 | 23 | -77 | 0 | 0 | 0
241942 | 23-77.5 | 23 | -77.5 | 0 | 0 | 0
242663 | 23-78 | 23 | -78 | 0 | 0 | 0
243384 | 23-78.5 | 23 | -78.5 | 0 | 0 | 0
244105 | 23-79 | 23 | -79 | 0 | 0 | 0
244826 | 23-79.5 | 23 | -79.5 | 0 | 0 | 0
245547 | 23-80 | 23 | -80 | 0 | 0 | 0
246268 | 23-80.5 | 23 | -80.5 | 0 | 0 | 0
246989 | 23-81 | 23 | -81 | 0 | 0 | 0
247710 | 23-81.5 | 23 | -81.5 | 0 | 0 | 0
248431 | 23-82 | 23 | -82 | 0 | 0 | 0
249152 | 23-82.5 | 23 | -82.5 | 0 | 0 | 0
249873 | 23-83 | 23 | -83 | 0 | 0 | 0
250594 | 23-83.5 | 23 | -83.5 | 0 | 0 | 0
251315 | 23-84 | 23 | -84 | 0 | 0 | 0
252036 | 23-84.5 | 23 | -84.5 | 0 | 0 | 0
252757 | 23-85 | 23 | -85 | 0 | 0 | 0
253478 | 23-85.5 | 23 | -85.5 | 0 | 0 | 0
254199 | 23-86 | 23 | -86 | 0 | 0 | 0
254920 | 23-86.5 | 23 | -86.5 | 0 | 0 | 0
255641 | 23-87 | 23 | -87 | 0 | 0 | 0
256362 | 23-87.5 | 23 | -87.5 | 0 | 0 | 0
257083 | 23-88 | 23 | -88 | 0 | 0 | 0
257804 | 23-88.5 | 23 | -88.5 | 0 | 0 | 0
258525 | 23-89 | 23 | -89 | 0 | 0 | 0
259246 | 23-89.5 | 23 | -89.5 | 0 | 0 | 0
259967 | 23-90 | 23 | -90 | 0 | 0 | 0
215266 | 23.5-59 | 23.5 | -59 | 0 | 0 | 0
215987 | 23.5-59.5 | 23.5 | -59.5 | 0 | 0 | 0
216708 | 23.5-60 | 23.5 | -60 | 0 | 0 | 0
217429 | 23.5-60.5 | 23.5 | -60.5 | 0 | 0 | 0
218150 | 23.5-61 | 23.5 | -61 | 0 | 0 | 0
218871 | 23.5-61.5 | 23.5 | -61.5 | 0 | 0 | 0
219592 | 23.5-62 | 23.5 | -62 | 0 | 0 | 0
220313 | 23.5-62.5 | 23.5 | -62.5 | 0 | 0 | 0
221034 | 23.5-63 | 23.5 | -63 | 0 | 0 | 0
221755 | 23.5-63.5 | 23.5 | -63.5 | 0 | 0 | 0
222476 | 23.5-64 | 23.5 | -64 | 0 | 0 | 0
223197 | 23.5-64.5 | 23.5 | -64.5 | 0 | 0 | 0
223918 | 23.5-65 | 23.5 | -65 | 0 | 0 | 0
224639 | 23.5-65.5 | 23.5 | -65.5 | 0 | 0 | 0
225360 | 23.5-66 | 23.5 | -66 | 0 | 0 | 0
226081 | 23.5-66.5 | 23.5 | -66.5 | 0 | 0 | 0
226802 | 23.5-67 | 23.5 | -67 | 0 | 0 | 0
227523 | 23.5-67.5 | 23.5 | -67.5 | 0 | 0 | 0
228244 | 23.5-68 | 23.5 | -68 | 0 | 0 | 0
228965 | 23.5-68.5 | 23.5 | -68.5 | 0 | 0 | 0
229686 | 23.5-69 | 23.5 | -69 | 0 | 0 | 0
230407 | 23.5-69.5 | 23.5 | -69.5 | 0 | 0 | 0
231128 | 23.5-70 | 23.5 | -70 | 0 | 0 | 0
231849 | 23.5-70.5 | 23.5 | -70.5 | 0 | 0 | 0
232570 | 23.5-71 | 23.5 | -71 | 0 | 0 | 0
233291 | 23.5-71.5 | 23.5 | -71.5 | 0 | 0 | 0
234012 | 23.5-72 | 23.5 | -72 | 0 | 0 | 0
234733 | 23.5-72.5 | 23.5 | -72.5 | 0 | 0 | 0
235454 | 23.5-73 | 23.5 | -73 | 0 | 0 | 0
236175 | 23.5-73.5 | 23.5 | -73.5 | 0 | 0 | 0
236896 | 23.5-74 | 23.5 | -74 | 0 | 0 | 0
237617 | 23.5-74.5 | 23.5 | -74.5 | 0 | 0 | 0
238338 | 23.5-75 | 23.5 | -75 | 0 | 0 | 0
239059 | 23.5-75.5 | 23.5 | -75.5 | 0 | 0 | 0
239780 | 23.5-76 | 23.5 | -76 | 0 | 0 | 0
240501 | 23.5-76.5 | 23.5 | -76.5 | 0 | 0 | 0
241222 | 23.5-77 | 23.5 | -77 | 0 | 0 | 0
241943 | 23.5-77.5 | 23.5 | -77.5 | 0 | 0 | 0
242664 | 23.5-78 | 23.5 | -78 | 0 | 0 | 0
243385 | 23.5-78.5 | 23.5 | -78.5 | 0 | 0 | 0
244106 | 23.5-79 | 23.5 | -79 | 0 | 0 | 0
244827 | 23.5-79.5 | 23.5 | -79.5 | 0 | 0 | 0
245548 | 23.5-80 | 23.5 | -80 | 0 | 0 | 0
246269 | 23.5-80.5 | 23.5 | -80.5 | 0 | 0 | 0
246990 | 23.5-81 | 23.5 | -81 | 0 | 0 | 0
247711 | 23.5-81.5 | 23.5 | -81.5 | 0 | 0 | 0
248432 | 23.5-82 | 23.5 | -82 | 0 | 0 | 0
249153 | 23.5-82.5 | 23.5 | -82.5 | 0 | 0 | 0
249874 | 23.5-83 | 23.5 | -83 | 0 | 0 | 0
250595 | 23.5-83.5 | 23.5 | -83.5 | 0 | 0 | 0
251316 | 23.5-84 | 23.5 | -84 | 0 | 0 | 0
252037 | 23.5-84.5 | 23.5 | -84.5 | 0 | 0 | 0
252758 | 23.5-85 | 23.5 | -85 | 0 | 0 | 0
253479 | 23.5-85.5 | 23.5 | -85.5 | 0 | 0 | 0
254200 | 23.5-86 | 23.5 | -86 | 0 | 0 | 0
254921 | 23.5-86.5 | 23.5 | -86.5 | 0 | 0 | 0
255642 | 23.5-87 | 23.5 | -87 | 0 | 0 | 0
256363 | 23.5-87.5 | 23.5 | -87.5 | 0 | 0 | 0
257084 | 23.5-88 | 23.5 | -88 | 0 | 0 | 0
257805 | 23.5-88.5 | 23.5 | -88.5 | 0 | 0 | 0
258526 | 23.5-89 | 23.5 | -89 | 0 | 0 | 0
259247 | 23.5-89.5 | 23.5 | -89.5 | 0 | 0 | 0
259968 | 23.5-90 | 23.5 | -90 | 0 | 0 | 0
215267 | 24-59 | 24 | -59 | 0 | 0 | 0
215988 | 24-59.5 | 24 | -59.5 | 0 | 0 | 0
216709 | 24-60 | 24 | -60 | 0 | 0 | 0
217430 | 24-60.5 | 24 | -60.5 | 0 | 0 | 0
218151 | 24-61 | 24 | -61 | 0 | 0 | 0
218872 | 24-61.5 | 24 | -61.5 | 0 | 0 | 0
219593 | 24-62 | 24 | -62 | 0 | 0 | 0
220314 | 24-62.5 | 24 | -62.5 | 0 | 0 | 0
221035 | 24-63 | 24 | -63 | 0 | 0 | 0
221756 | 24-63.5 | 24 | -63.5 | 0 | 0 | 0
222477 | 24-64 | 24 | -64 | 0 | 0 | 0
223198 | 24-64.5 | 24 | -64.5 | 0 | 0 | 0
223919 | 24-65 | 24 | -65 | 0 | 0 | 0
224640 | 24-65.5 | 24 | -65.5 | 0 | 0 | 0
225361 | 24-66 | 24 | -66 | 0 | 0 | 0
226082 | 24-66.5 | 24 | -66.5 | 0 | 0 | 0
226803 | 24-67 | 24 | -67 | 0 | 0 | 0
227524 | 24-67.5 | 24 | -67.5 | 0 | 0 | 0
228245 | 24-68 | 24 | -68 | 0 | 0 | 0
228966 | 24-68.5 | 24 | -68.5 | 0 | 0 | 0
229687 | 24-69 | 24 | -69 | 0 | 0 | 0
230408 | 24-69.5 | 24 | -69.5 | 0 | 0 | 0
231129 | 24-70 | 24 | -70 | 0 | 0 | 0
231850 | 24-70.5 | 24 | -70.5 | 0 | 0 | 0
232571 | 24-71 | 24 | -71 | 0 | 0 | 0
233292 | 24-71.5 | 24 | -71.5 | 0 | 0 | 0
234013 | 24-72 | 24 | -72 | 0 | 0 | 0
234734 | 24-72.5 | 24 | -72.5 | 0 | 0 | 0
235455 | 24-73 | 24 | -73 | 0 | 0 | 0
236176 | 24-73.5 | 24 | -73.5 | 0 | 0 | 0
236897 | 24-74 | 24 | -74 | 0 | 0 | 0
237618 | 24-74.5 | 24 | -74.5 | 0 | 0 | 0
238339 | 24-75 | 24 | -75 | 0 | 0 | 0
239060 | 24-75.5 | 24 | -75.5 | 0 | 0 | 0
239781 | 24-76 | 24 | -76 | 0 | 0 | 0
240502 | 24-76.5 | 24 | -76.5 | 0 | 0 | 0
241223 | 24-77 | 24 | -77 | 0 | 0 | 0
241944 | 24-77.5 | 24 | -77.5 | 0 | 0 | 0
242665 | 24-78 | 24 | -78 | 0 | 0 | 0
243386 | 24-78.5 | 24 | -78.5 | 0 | 0 | 0
244107 | 24-79 | 24 | -79 | 0 | 0 | 0
244828 | 24-79.5 | 24 | -79.5 | 0 | 0 | 0
245549 | 24-80 | 24 | -80 | 0 | 0 | 0
246270 | 24-80.5 | 24 | -80.5 | 0 | 0 | 0
246991 | 24-81 | 24 | -81 | 0 | 0 | 0
247712 | 24-81.5 | 24 | -81.5 | 0 | 0 | 0
248433 | 24-82 | 24 | -82 | 0 | 0 | 0
249154 | 24-82.5 | 24 | -82.5 | 0 | 0 | 0
249875 | 24-83 | 24 | -83 | 0 | 0 | 0
250596 | 24-83.5 | 24 | -83.5 | 0 | 0 | 0
251317 | 24-84 | 24 | -84 | 0 | 0 | 0
252038 | 24-84.5 | 24 | -84.5 | 0 | 0 | 0
252759 | 24-85 | 24 | -85 | 0 | 0 | 0
253480 | 24-85.5 | 24 | -85.5 | 0 | 0 | 0
254201 | 24-86 | 24 | -86 | 0 | 0 | 0
254922 | 24-86.5 | 24 | -86.5 | 0 | 0 | 0
255643 | 24-87 | 24 | -87 | 0 | 0 | 0
256364 | 24-87.5 | 24 | -87.5 | 0 | 0 | 0
257085 | 24-88 | 24 | -88 | 0 | 0 | 0
257806 | 24-88.5 | 24 | -88.5 | 0 | 0 | 0
258527 | 24-89 | 24 | -89 | 0 | 0 | 0
259248 | 24-89.5 | 24 | -89.5 | 0 | 0 | 0
259969 | 24-90 | 24 | -90 | 0 | 0 | 0
215268 | 24.5-59 | 24.5 | -59 | 0 | 0 | 0
215989 | 24.5-59.5 | 24.5 | -59.5 | 0 | 0 | 0
216710 | 24.5-60 | 24.5 | -60 | 0 | 0 | 0
217431 | 24.5-60.5 | 24.5 | -60.5 | 0 | 0 | 0
218152 | 24.5-61 | 24.5 | -61 | 0 | 0 | 0
218873 | 24.5-61.5 | 24.5 | -61.5 | 0 | 0 | 0
219594 | 24.5-62 | 24.5 | -62 | 0 | 0 | 0
220315 | 24.5-62.5 | 24.5 | -62.5 | 0 | 0 | 0
221036 | 24.5-63 | 24.5 | -63 | 0 | 0 | 0
221757 | 24.5-63.5 | 24.5 | -63.5 | 0 | 0 | 0
222478 | 24.5-64 | 24.5 | -64 | 0 | 0 | 0
223199 | 24.5-64.5 | 24.5 | -64.5 | 0 | 0 | 0
223920 | 24.5-65 | 24.5 | -65 | 0 | 0 | 0
224641 | 24.5-65.5 | 24.5 | -65.5 | 0 | 0 | 0
225362 | 24.5-66 | 24.5 | -66 | 0 | 0 | 0
226083 | 24.5-66.5 | 24.5 | -66.5 | 0 | 0 | 0
226804 | 24.5-67 | 24.5 | -67 | 0 | 0 | 0
227525 | 24.5-67.5 | 24.5 | -67.5 | 0 | 0 | 0
228246 | 24.5-68 | 24.5 | -68 | 0 | 0 | 0
228967 | 24.5-68.5 | 24.5 | -68.5 | 0 | 0 | 0
229688 | 24.5-69 | 24.5 | -69 | 0 | 0 | 0
230409 | 24.5-69.5 | 24.5 | -69.5 | 0 | 0 | 0
231130 | 24.5-70 | 24.5 | -70 | 0 | 0 | 0
231851 | 24.5-70.5 | 24.5 | -70.5 | 0 | 0 | 0
232572 | 24.5-71 | 24.5 | -71 | 0 | 0 | 0
233293 | 24.5-71.5 | 24.5 | -71.5 | 0 | 0 | 0
234014 | 24.5-72 | 24.5 | -72 | 0 | 0 | 0
234735 | 24.5-72.5 | 24.5 | -72.5 | 0 | 0 | 0
235456 | 24.5-73 | 24.5 | -73 | 0 | 0 | 0
236177 | 24.5-73.5 | 24.5 | -73.5 | 0 | 0 | 0
236898 | 24.5-74 | 24.5 | -74 | 0 | 0 | 0
237619 | 24.5-74.5 | 24.5 | -74.5 | 0 | 0 | 0
238340 | 24.5-75 | 24.5 | -75 | 0 | 0 | 0
239061 | 24.5-75.5 | 24.5 | -75.5 | 0 | 0 | 0
239782 | 24.5-76 | 24.5 | -76 | 0 | 0 | 0
240503 | 24.5-76.5 | 24.5 | -76.5 | 0 | 0 | 0
241224 | 24.5-77 | 24.5 | -77 | 0 | 0 | 0
241945 | 24.5-77.5 | 24.5 | -77.5 | 0 | 0 | 0
242666 | 24.5-78 | 24.5 | -78 | 0 | 0 | 0
243387 | 24.5-78.5 | 24.5 | -78.5 | 0 | 0 | 0
244108 | 24.5-79 | 24.5 | -79 | 0 | 0 | 0
244829 | 24.5-79.5 | 24.5 | -79.5 | 0 | 0 | 0
245550 | 24.5-80 | 24.5 | -80 | 0 | 0 | 0
246271 | 24.5-80.5 | 24.5 | -80.5 | 0 | 0 | 0
246992 | 24.5-81 | 24.5 | -81 | 0 | 0 | 0
247713 | 24.5-81.5 | 24.5 | -81.5 | 0 | 0 | 0
248434 | 24.5-82 | 24.5 | -82 | 0 | 0 | 0
249155 | 24.5-82.5 | 24.5 | -82.5 | 0 | 0 | 0
249876 | 24.5-83 | 24.5 | -83 | 0 | 0 | 0
250597 | 24.5-83.5 | 24.5 | -83.5 | 0 | 0 | 0
251318 | 24.5-84 | 24.5 | -84 | 0 | 0 | 0
252039 | 24.5-84.5 | 24.5 | -84.5 | 0 | 0 | 0
252760 | 24.5-85 | 24.5 | -85 | 0 | 0 | 0
253481 | 24.5-85.5 | 24.5 | -85.5 | 0 | 0 | 0
254202 | 24.5-86 | 24.5 | -86 | 0 | 0 | 0
254923 | 24.5-86.5 | 24.5 | -86.5 | 0 | 0 | 0
255644 | 24.5-87 | 24.5 | -87 | 0 | 0 | 0
256365 | 24.5-87.5 | 24.5 | -87.5 | 0 | 0 | 0
257086 | 24.5-88 | 24.5 | -88 | 0 | 0 | 0
257807 | 24.5-88.5 | 24.5 | -88.5 | 0 | 0 | 0
258528 | 24.5-89 | 24.5 | -89 | 0 | 0 | 0
259249 | 24.5-89.5 | 24.5 | -89.5 | 0 | 0 | 0
259970 | 24.5-90 | 24.5 | -90 | 0 | 0 | 0
215269 | 25-59 | 25 | -59 | 0 | 0 | 0
215990 | 25-59.5 | 25 | -59.5 | 0 | 0 | 0
216711 | 25-60 | 25 | -60 | 0 | 0 | 0
217432 | 25-60.5 | 25 | -60.5 | 0 | 0 | 0
218153 | 25-61 | 25 | -61 | 0 | 0 | 0
218874 | 25-61.5 | 25 | -61.5 | 0 | 0 | 0
219595 | 25-62 | 25 | -62 | 0 | 0 | 0
220316 | 25-62.5 | 25 | -62.5 | 0 | 0 | 0
221037 | 25-63 | 25 | -63 | 0 | 0 | 0
221758 | 25-63.5 | 25 | -63.5 | 0 | 0 | 0
222479 | 25-64 | 25 | -64 | 0 | 0 | 0
223200 | 25-64.5 | 25 | -64.5 | 0 | 0 | 0
223921 | 25-65 | 25 | -65 | 0 | 0 | 0
224642 | 25-65.5 | 25 | -65.5 | 0 | 0 | 0
225363 | 25-66 | 25 | -66 | 0 | 0 | 0
226084 | 25-66.5 | 25 | -66.5 | 0 | 0 | 0
226805 | 25-67 | 25 | -67 | 0 | 0 | 0
227526 | 25-67.5 | 25 | -67.5 | 0 | 0 | 0
228247 | 25-68 | 25 | -68 | 0 | 0 | 0
228968 | 25-68.5 | 25 | -68.5 | 0 | 0 | 0
229689 | 25-69 | 25 | -69 | 0 | 0 | 0
230410 | 25-69.5 | 25 | -69.5 | 0 | 0 | 0
231131 | 25-70 | 25 | -70 | 0 | 0 | 0
231852 | 25-70.5 | 25 | -70.5 | 0 | 0 | 0
232573 | 25-71 | 25 | -71 | 0 | 0 | 0
233294 | 25-71.5 | 25 | -71.5 | 0 | 0 | 0
234015 | 25-72 | 25 | -72 | 0 | 0 | 0
234736 | 25-72.5 | 25 | -72.5 | 0 | 0 | 0
235457 | 25-73 | 25 | -73 | 0 | 0 | 0
236178 | 25-73.5 | 25 | -73.5 | 0 | 0 | 0
236899 | 25-74 | 25 | -74 | 0 | 0 | 0
237620 | 25-74.5 | 25 | -74.5 | 0 | 0 | 0
238341 | 25-75 | 25 | -75 | 0 | 0 | 0
239062 | 25-75.5 | 25 | -75.5 | 0 | 0 | 0
239783 | 25-76 | 25 | -76 | 0 | 0 | 0
240504 | 25-76.5 | 25 | -76.5 | 0 | 0 | 0
241225 | 25-77 | 25 | -77 | 0 | 0 | 0
241946 | 25-77.5 | 25 | -77.5 | 0 | 0 | 0
242667 | 25-78 | 25 | -78 | 0 | 0 | 0
243388 | 25-78.5 | 25 | -78.5 | 0 | 0 | 0
244109 | 25-79 | 25 | -79 | 0 | 0 | 0
244830 | 25-79.5 | 25 | -79.5 | 0 | 0 | 0
245551 | 25-80 | 25 | -80 | 0 | 0 | 0
246272 | 25-80.5 | 25 | -80.5 | 0 | 0 | 0
246993 | 25-81 | 25 | -81 | 0 | 0 | 0
247714 | 25-81.5 | 25 | -81.5 | 0 | 0 | 0
248435 | 25-82 | 25 | -82 | 0 | 0 | 0
249156 | 25-82.5 | 25 | -82.5 | 0 | 0 | 0
249877 | 25-83 | 25 | -83 | 0 | 0 | 0
250598 | 25-83.5 | 25 | -83.5 | 0 | 0 | 0
251319 | 25-84 | 25 | -84 | 0 | 0 | 0
252040 | 25-84.5 | 25 | -84.5 | 0 | 0 | 0
252761 | 25-85 | 25 | -85 | 0 | 0 | 0
253482 | 25-85.5 | 25 | -85.5 | 0 | 0 | 0
254203 | 25-86 | 25 | -86 | 0 | 0 | 0
254924 | 25-86.5 | 25 | -86.5 | 0 | 0 | 0
255645 | 25-87 | 25 | -87 | 0 | 0 | 0
256366 | 25-87.5 | 25 | -87.5 | 0 | 0 | 0
257087 | 25-88 | 25 | -88 | 0 | 0 | 0
257808 | 25-88.5 | 25 | -88.5 | 0 | 0 | 0
258529 | 25-89 | 25 | -89 | 0 | 0 | 0
259250 | 25-89.5 | 25 | -89.5 | 0 | 0 | 0
259971 | 25-90 | 25 | -90 | 0 | 0 | 0
215270 | 25.5-59 | 25.5 | -59 | 0 | 0 | 0
215991 | 25.5-59.5 | 25.5 | -59.5 | 0 | 0 | 0
216712 | 25.5-60 | 25.5 | -60 | 0 | 0 | 0
217433 | 25.5-60.5 | 25.5 | -60.5 | 0 | 0 | 0
218154 | 25.5-61 | 25.5 | -61 | 0 | 0 | 0
218875 | 25.5-61.5 | 25.5 | -61.5 | 0 | 0 | 0
219596 | 25.5-62 | 25.5 | -62 | 0 | 0 | 0
220317 | 25.5-62.5 | 25.5 | -62.5 | 0 | 0 | 0
221038 | 25.5-63 | 25.5 | -63 | 0 | 0 | 0
221759 | 25.5-63.5 | 25.5 | -63.5 | 0 | 0 | 0
222480 | 25.5-64 | 25.5 | -64 | 0 | 0 | 0
223201 | 25.5-64.5 | 25.5 | -64.5 | 0 | 0 | 0
223922 | 25.5-65 | 25.5 | -65 | 0 | 0 | 0
224643 | 25.5-65.5 | 25.5 | -65.5 | 0 | 0 | 0
225364 | 25.5-66 | 25.5 | -66 | 0 | 0 | 0
226085 | 25.5-66.5 | 25.5 | -66.5 | 0 | 0 | 0
226806 | 25.5-67 | 25.5 | -67 | 0 | 0 | 0
227527 | 25.5-67.5 | 25.5 | -67.5 | 0 | 0 | 0
228248 | 25.5-68 | 25.5 | -68 | 0 | 0 | 0
228969 | 25.5-68.5 | 25.5 | -68.5 | 0 | 0 | 0
229690 | 25.5-69 | 25.5 | -69 | 0 | 0 | 0
230411 | 25.5-69.5 | 25.5 | -69.5 | 0 | 0 | 0
231132 | 25.5-70 | 25.5 | -70 | 0 | 0 | 0
231853 | 25.5-70.5 | 25.5 | -70.5 | 0 | 0 | 0
232574 | 25.5-71 | 25.5 | -71 | 0 | 0 | 0
233295 | 25.5-71.5 | 25.5 | -71.5 | 0 | 0 | 0
234016 | 25.5-72 | 25.5 | -72 | 0 | 0 | 0
234737 | 25.5-72.5 | 25.5 | -72.5 | 0 | 0 | 0
235458 | 25.5-73 | 25.5 | -73 | 0 | 0 | 0
236179 | 25.5-73.5 | 25.5 | -73.5 | 0 | 0 | 0
236900 | 25.5-74 | 25.5 | -74 | 0 | 0 | 0
237621 | 25.5-74.5 | 25.5 | -74.5 | 0 | 0 | 0
238342 | 25.5-75 | 25.5 | -75 | 0 | 0 | 0
239063 | 25.5-75.5 | 25.5 | -75.5 | 0 | 0 | 0
239784 | 25.5-76 | 25.5 | -76 | 0 | 0 | 0
240505 | 25.5-76.5 | 25.5 | -76.5 | 0 | 0 | 0
241226 | 25.5-77 | 25.5 | -77 | 0 | 0 | 0
241947 | 25.5-77.5 | 25.5 | -77.5 | 0 | 0 | 0
242668 | 25.5-78 | 25.5 | -78 | 0 | 0 | 0
243389 | 25.5-78.5 | 25.5 | -78.5 | 0 | 0 | 0
244110 | 25.5-79 | 25.5 | -79 | 0 | 0 | 0
244831 | 25.5-79.5 | 25.5 | -79.5 | 0 | 0 | 0
245552 | 25.5-80 | 25.5 | -80 | 0 | 0 | 0
246273 | 25.5-80.5 | 25.5 | -80.5 | 0 | 0 | 0
246994 | 25.5-81 | 25.5 | -81 | 0 | 0 | 0
247715 | 25.5-81.5 | 25.5 | -81.5 | 0 | 0 | 0
248436 | 25.5-82 | 25.5 | -82 | 0 | 0 | 0
249157 | 25.5-82.5 | 25.5 | -82.5 | 0 | 0 | 0
249878 | 25.5-83 | 25.5 | -83 | 0 | 0 | 0
250599 | 25.5-83.5 | 25.5 | -83.5 | 0 | 0 | 0
251320 | 25.5-84 | 25.5 | -84 | 0 | 0 | 0
252041 | 25.5-84.5 | 25.5 | -84.5 | 0 | 0 | 0
252762 | 25.5-85 | 25.5 | -85 | 0 | 0 | 0
253483 | 25.5-85.5 | 25.5 | -85.5 | 0 | 0 | 0
254204 | 25.5-86 | 25.5 | -86 | 0 | 0 | 0
254925 | 25.5-86.5 | 25.5 | -86.5 | 0 | 0 | 0
255646 | 25.5-87 | 25.5 | -87 | 0 | 0 | 0
256367 | 25.5-87.5 | 25.5 | -87.5 | 0 | 0 | 0
257088 | 25.5-88 | 25.5 | -88 | 0 | 0 | 0
257809 | 25.5-88.5 | 25.5 | -88.5 | 0 | 0 | 0
258530 | 25.5-89 | 25.5 | -89 | 0 | 0 | 0
259251 | 25.5-89.5 | 25.5 | -89.5 | 0 | 0 | 0
259972 | 25.5-90 | 25.5 | -90 | 0 | 0 | 0
215271 | 26-59 | 26 | -59 | 0 | 0 | 0
215992 | 26-59.5 | 26 | -59.5 | 0 | 0 | 0
216713 | 26-60 | 26 | -60 | 0 | 0 | 0
217434 | 26-60.5 | 26 | -60.5 | 0 | 0 | 0
218155 | 26-61 | 26 | -61 | 0 | 0 | 0
218876 | 26-61.5 | 26 | -61.5 | 0 | 0 | 0
219597 | 26-62 | 26 | -62 | 0 | 0 | 0
220318 | 26-62.5 | 26 | -62.5 | 0 | 0 | 0
221039 | 26-63 | 26 | -63 | 0 | 0 | 0
221760 | 26-63.5 | 26 | -63.5 | 0 | 0 | 0
222481 | 26-64 | 26 | -64 | 0 | 0 | 0
223202 | 26-64.5 | 26 | -64.5 | 0 | 0 | 0
223923 | 26-65 | 26 | -65 | 0 | 0 | 0
224644 | 26-65.5 | 26 | -65.5 | 0 | 0 | 0
225365 | 26-66 | 26 | -66 | 0 | 0 | 0
226086 | 26-66.5 | 26 | -66.5 | 0 | 0 | 0
226807 | 26-67 | 26 | -67 | 0 | 0 | 0
227528 | 26-67.5 | 26 | -67.5 | 0 | 0 | 0
228249 | 26-68 | 26 | -68 | 0 | 0 | 0
228970 | 26-68.5 | 26 | -68.5 | 0 | 0 | 0
229691 | 26-69 | 26 | -69 | 0 | 0 | 0
230412 | 26-69.5 | 26 | -69.5 | 0 | 0 | 0
231133 | 26-70 | 26 | -70 | 0 | 0 | 0
231854 | 26-70.5 | 26 | -70.5 | 0 | 0 | 0
232575 | 26-71 | 26 | -71 | 0 | 0 | 0
233296 | 26-71.5 | 26 | -71.5 | 0 | 0 | 0
234017 | 26-72 | 26 | -72 | 0 | 0 | 0
234738 | 26-72.5 | 26 | -72.5 | 0 | 0 | 0
235459 | 26-73 | 26 | -73 | 0 | 0 | 0
236180 | 26-73.5 | 26 | -73.5 | 0 | 0 | 0
236901 | 26-74 | 26 | -74 | 0 | 0 | 0
237622 | 26-74.5 | 26 | -74.5 | 0 | 0 | 0
238343 | 26-75 | 26 | -75 | 0 | 0 | 0
239064 | 26-75.5 | 26 | -75.5 | 0 | 0 | 0
239785 | 26-76 | 26 | -76 | 0 | 0 | 0
240506 | 26-76.5 | 26 | -76.5 | 0 | 0 | 0
241227 | 26-77 | 26 | -77 | 0 | 0 | 0
241948 | 26-77.5 | 26 | -77.5 | 0 | 0 | 0
242669 | 26-78 | 26 | -78 | 0 | 0 | 0
243390 | 26-78.5 | 26 | -78.5 | 0 | 0 | 0
244111 | 26-79 | 26 | -79 | 0 | 0 | 0
244832 | 26-79.5 | 26 | -79.5 | 0 | 0 | 0
245553 | 26-80 | 26 | -80 | 0 | 0 | 0
246274 | 26-80.5 | 26 | -80.5 | 0 | 0 | 0
246995 | 26-81 | 26 | -81 | 0 | 0 | 0
247716 | 26-81.5 | 26 | -81.5 | 0 | 0 | 0
248437 | 26-82 | 26 | -82 | 0 | 0 | 0
249158 | 26-82.5 | 26 | -82.5 | 0 | 0 | 0
249879 | 26-83 | 26 | -83 | 0 | 0 | 0
250600 | 26-83.5 | 26 | -83.5 | 0 | 0 | 0
251321 | 26-84 | 26 | -84 | 0 | 0 | 0
252042 | 26-84.5 | 26 | -84.5 | 0 | 0 | 0
252763 | 26-85 | 26 | -85 | 0 | 0 | 0
253484 | 26-85.5 | 26 | -85.5 | 0 | 0 | 0
254205 | 26-86 | 26 | -86 | 0 | 0 | 0
254926 | 26-86.5 | 26 | -86.5 | 0 | 0 | 0
255647 | 26-87 | 26 | -87 | 0 | 0 | 0
256368 | 26-87.5 | 26 | -87.5 | 0 | 0 | 0
257089 | 26-88 | 26 | -88 | 0 | 0 | 0
257810 | 26-88.5 | 26 | -88.5 | 0 | 0 | 0
258531 | 26-89 | 26 | -89 | 0 | 0 | 0
259252 | 26-89.5 | 26 | -89.5 | 0 | 0 | 0
259973 | 26-90 | 26 | -90 | 0 | 0 | 0
215272 | 26.5-59 | 26.5 | -59 | 0 | 0 | 0
215993 | 26.5-59.5 | 26.5 | -59.5 | 0 | 0 | 0
216714 | 26.5-60 | 26.5 | -60 | 0 | 0 | 0
217435 | 26.5-60.5 | 26.5 | -60.5 | 0 | 0 | 0
218156 | 26.5-61 | 26.5 | -61 | 0 | 0 | 0
218877 | 26.5-61.5 | 26.5 | -61.5 | 0 | 0 | 0
219598 | 26.5-62 | 26.5 | -62 | 0 | 0 | 0
220319 | 26.5-62.5 | 26.5 | -62.5 | 0 | 0 | 0
221040 | 26.5-63 | 26.5 | -63 | 0 | 0 | 0
221761 | 26.5-63.5 | 26.5 | -63.5 | 0 | 0 | 0
222482 | 26.5-64 | 26.5 | -64 | 0 | 0 | 0
223203 | 26.5-64.5 | 26.5 | -64.5 | 0 | 0 | 0
223924 | 26.5-65 | 26.5 | -65 | 0 | 0 | 0
224645 | 26.5-65.5 | 26.5 | -65.5 | 0 | 0 | 0
225366 | 26.5-66 | 26.5 | -66 | 0 | 0 | 0
226087 | 26.5-66.5 | 26.5 | -66.5 | 0 | 0 | 0
226808 | 26.5-67 | 26.5 | -67 | 0 | 0 | 0
227529 | 26.5-67.5 | 26.5 | -67.5 | 0 | 0 | 0
228250 | 26.5-68 | 26.5 | -68 | 0 | 0 | 0
228971 | 26.5-68.5 | 26.5 | -68.5 | 0 | 0 | 0
229692 | 26.5-69 | 26.5 | -69 | 0 | 0 | 0
230413 | 26.5-69.5 | 26.5 | -69.5 | 0 | 0 | 0
231134 | 26.5-70 | 26.5 | -70 | 0 | 0 | 0
231855 | 26.5-70.5 | 26.5 | -70.5 | 0 | 0 | 0
232576 | 26.5-71 | 26.5 | -71 | 0 | 0 | 0
233297 | 26.5-71.5 | 26.5 | -71.5 | 0 | 0 | 0
234018 | 26.5-72 | 26.5 | -72 | 0 | 0 | 0
234739 | 26.5-72.5 | 26.5 | -72.5 | 0 | 0 | 0
235460 | 26.5-73 | 26.5 | -73 | 0 | 0 | 0
236181 | 26.5-73.5 | 26.5 | -73.5 | 0 | 0 | 0
236902 | 26.5-74 | 26.5 | -74 | 0 | 0 | 0
237623 | 26.5-74.5 | 26.5 | -74.5 | 0 | 0 | 0
238344 | 26.5-75 | 26.5 | -75 | 0 | 0 | 0
239065 | 26.5-75.5 | 26.5 | -75.5 | 0 | 0 | 0
239786 | 26.5-76 | 26.5 | -76 | 0 | 0 | 0
240507 | 26.5-76.5 | 26.5 | -76.5 | 0 | 0 | 0
241228 | 26.5-77 | 26.5 | -77 | 0 | 0 | 0
241949 | 26.5-77.5 | 26.5 | -77.5 | 0 | 0 | 0
242670 | 26.5-78 | 26.5 | -78 | 0 | 0 | 0
243391 | 26.5-78.5 | 26.5 | -78.5 | 0 | 0 | 0
244112 | 26.5-79 | 26.5 | -79 | 0 | 0 | 0
244833 | 26.5-79.5 | 26.5 | -79.5 | 0 | 0 | 0
245554 | 26.5-80 | 26.5 | -80 | 0 | 0 | 0
246275 | 26.5-80.5 | 26.5 | -80.5 | 0 | 0 | 0
246996 | 26.5-81 | 26.5 | -81 | 0 | 0 | 0
247717 | 26.5-81.5 | 26.5 | -81.5 | 0 | 0 | 0
248438 | 26.5-82 | 26.5 | -82 | 0 | 0 | 0
249159 | 26.5-82.5 | 26.5 | -82.5 | 0 | 0 | 0
249880 | 26.5-83 | 26.5 | -83 | 0 | 0 | 0
250601 | 26.5-83.5 | 26.5 | -83.5 | 0 | 0 | 0
251322 | 26.5-84 | 26.5 | -84 | 0 | 0 | 0
252043 | 26.5-84.5 | 26.5 | -84.5 | 0 | 0 | 0
252764 | 26.5-85 | 26.5 | -85 | 0 | 0 | 0
253485 | 26.5-85.5 | 26.5 | -85.5 | 0 | 0 | 0
254206 | 26.5-86 | 26.5 | -86 | 0 | 0 | 0
254927 | 26.5-86.5 | 26.5 | -86.5 | 0 | 0 | 0
255648 | 26.5-87 | 26.5 | -87 | 0 | 0 | 0
256369 | 26.5-87.5 | 26.5 | -87.5 | 0 | 0 | 0
257090 | 26.5-88 | 26.5 | -88 | 0 | 0 | 0
257811 | 26.5-88.5 | 26.5 | -88.5 | 0 | 0 | 0
258532 | 26.5-89 | 26.5 | -89 | 0 | 0 | 0
259253 | 26.5-89.5 | 26.5 | -89.5 | 0 | 0 | 0
259974 | 26.5-90 | 26.5 | -90 | 0 | 0 | 0
215273 | 27-59 | 27 | -59 | 0 | 0 | 0
215994 | 27-59.5 | 27 | -59.5 | 0 | 0 | 0
216715 | 27-60 | 27 | -60 | 0 | 0 | 0
217436 | 27-60.5 | 27 | -60.5 | 0 | 0 | 0
218157 | 27-61 | 27 | -61 | 0 | 0 | 0
218878 | 27-61.5 | 27 | -61.5 | 0 | 0 | 0
219599 | 27-62 | 27 | -62 | 0 | 0 | 0
220320 | 27-62.5 | 27 | -62.5 | 0 | 0 | 0
221041 | 27-63 | 27 | -63 | 0 | 0 | 0
221762 | 27-63.5 | 27 | -63.5 | 0 | 0 | 0
222483 | 27-64 | 27 | -64 | 0 | 0 | 0
223204 | 27-64.5 | 27 | -64.5 | 0 | 0 | 0
223925 | 27-65 | 27 | -65 | 0 | 0 | 0
224646 | 27-65.5 | 27 | -65.5 | 0 | 0 | 0
225367 | 27-66 | 27 | -66 | 0 | 0 | 0
226088 | 27-66.5 | 27 | -66.5 | 0 | 0 | 0
226809 | 27-67 | 27 | -67 | 0 | 0 | 0
227530 | 27-67.5 | 27 | -67.5 | 0 | 0 | 0
228251 | 27-68 | 27 | -68 | 0 | 0 | 0
228972 | 27-68.5 | 27 | -68.5 | 0 | 0 | 0
229693 | 27-69 | 27 | -69 | 0 | 0 | 0
230414 | 27-69.5 | 27 | -69.5 | 0 | 0 | 0
231135 | 27-70 | 27 | -70 | 0 | 0 | 0
231856 | 27-70.5 | 27 | -70.5 | 0 | 0 | 0
232577 | 27-71 | 27 | -71 | 0 | 0 | 0
233298 | 27-71.5 | 27 | -71.5 | 0 | 0 | 0
234019 | 27-72 | 27 | -72 | 0 | 0 | 0
234740 | 27-72.5 | 27 | -72.5 | 0 | 0 | 0
235461 | 27-73 | 27 | -73 | 0 | 0 | 0
236182 | 27-73.5 | 27 | -73.5 | 0 | 0 | 0
236903 | 27-74 | 27 | -74 | 0 | 0 | 0
237624 | 27-74.5 | 27 | -74.5 | 0 | 0 | 0
238345 | 27-75 | 27 | -75 | 0 | 0 | 0
239066 | 27-75.5 | 27 | -75.5 | 0 | 0 | 0
239787 | 27-76 | 27 | -76 | 0 | 0 | 0
240508 | 27-76.5 | 27 | -76.5 | 0 | 0 | 0
241229 | 27-77 | 27 | -77 | 0 | 0 | 0
241950 | 27-77.5 | 27 | -77.5 | 0 | 0 | 0
242671 | 27-78 | 27 | -78 | 0 | 0 | 0
243392 | 27-78.5 | 27 | -78.5 | 0 | 0 | 0
244113 | 27-79 | 27 | -79 | 0 | 0 | 0
244834 | 27-79.5 | 27 | -79.5 | 0 | 0 | 0
245555 | 27-80 | 27 | -80 | 0 | 0 | 0
246276 | 27-80.5 | 27 | -80.5 | 0 | 0 | 0
246997 | 27-81 | 27 | -81 | 0 | 0 | 0
247718 | 27-81.5 | 27 | -81.5 | 0 | 0 | 0
248439 | 27-82 | 27 | -82 | 0 | 0 | 0
249160 | 27-82.5 | 27 | -82.5 | 0 | 0 | 0
249881 | 27-83 | 27 | -83 | 0 | 0 | 0
250602 | 27-83.5 | 27 | -83.5 | 0 | 0 | 0
251323 | 27-84 | 27 | -84 | 0 | 0 | 0
252044 | 27-84.5 | 27 | -84.5 | 0 | 0 | 0
252765 | 27-85 | 27 | -85 | 0 | 0 | 0
253486 | 27-85.5 | 27 | -85.5 | 0 | 0 | 0
254207 | 27-86 | 27 | -86 | 0 | 0 | 0
254928 | 27-86.5 | 27 | -86.5 | 0 | 0 | 0
255649 | 27-87 | 27 | -87 | 0 | 0 | 0
256370 | 27-87.5 | 27 | -87.5 | 0 | 0 | 0
257091 | 27-88 | 27 | -88 | 0 | 0 | 0
257812 | 27-88.5 | 27 | -88.5 | 0 | 0 | 0
258533 | 27-89 | 27 | -89 | 0 | 0 | 0
259254 | 27-89.5 | 27 | -89.5 | 0 | 0 | 0
259975 | 27-90 | 27 | -90 | 0 | 0 | 0
215274 | 27.5-59 | 27.5 | -59 | 0 | 0 | 0
215995 | 27.5-59.5 | 27.5 | -59.5 | 0 | 0 | 0
216716 | 27.5-60 | 27.5 | -60 | 0 | 0 | 0
217437 | 27.5-60.5 | 27.5 | -60.5 | 0 | 0 | 0
218158 | 27.5-61 | 27.5 | -61 | 0 | 0 | 0
218879 | 27.5-61.5 | 27.5 | -61.5 | 0 | 0 | 0
219600 | 27.5-62 | 27.5 | -62 | 0 | 0 | 0
220321 | 27.5-62.5 | 27.5 | -62.5 | 0 | 0 | 0
221042 | 27.5-63 | 27.5 | -63 | 0 | 0 | 0
221763 | 27.5-63.5 | 27.5 | -63.5 | 0 | 0 | 0
222484 | 27.5-64 | 27.5 | -64 | 0 | 0 | 0
223205 | 27.5-64.5 | 27.5 | -64.5 | 0 | 0 | 0
223926 | 27.5-65 | 27.5 | -65 | 0 | 0 | 0
224647 | 27.5-65.5 | 27.5 | -65.5 | 0 | 0 | 0
225368 | 27.5-66 | 27.5 | -66 | 0 | 0 | 0
226089 | 27.5-66.5 | 27.5 | -66.5 | 0 | 0 | 0
226810 | 27.5-67 | 27.5 | -67 | 0 | 0 | 0
227531 | 27.5-67.5 | 27.5 | -67.5 | 0 | 0 | 0
228252 | 27.5-68 | 27.5 | -68 | 0 | 0 | 0
228973 | 27.5-68.5 | 27.5 | -68.5 | 0 | 0 | 0
229694 | 27.5-69 | 27.5 | -69 | 0 | 0 | 0
230415 | 27.5-69.5 | 27.5 | -69.5 | 0 | 0 | 0
231136 | 27.5-70 | 27.5 | -70 | 0 | 0 | 0
231857 | 27.5-70.5 | 27.5 | -70.5 | 0 | 0 | 0
232578 | 27.5-71 | 27.5 | -71 | 0 | 0 | 0
233299 | 27.5-71.5 | 27.5 | -71.5 | 0 | 0 | 0
234020 | 27.5-72 | 27.5 | -72 | 0 | 0 | 0
234741 | 27.5-72.5 | 27.5 | -72.5 | 0 | 0 | 0
235462 | 27.5-73 | 27.5 | -73 | 0 | 0 | 0
236183 | 27.5-73.5 | 27.5 | -73.5 | 0 | 0 | 0
236904 | 27.5-74 | 27.5 | -74 | 0 | 0 | 0
237625 | 27.5-74.5 | 27.5 | -74.5 | 0 | 0 | 0
238346 | 27.5-75 | 27.5 | -75 | 0 | 0 | 0
239067 | 27.5-75.5 | 27.5 | -75.5 | 0 | 0 | 0
239788 | 27.5-76 | 27.5 | -76 | 0 | 0 | 0
240509 | 27.5-76.5 | 27.5 | -76.5 | 0 | 0 | 0
241230 | 27.5-77 | 27.5 | -77 | 0 | 0 | 0
241951 | 27.5-77.5 | 27.5 | -77.5 | 0 | 0 | 0
242672 | 27.5-78 | 27.5 | -78 | 0 | 0 | 0
243393 | 27.5-78.5 | 27.5 | -78.5 | 0 | 0 | 0
244114 | 27.5-79 | 27.5 | -79 | 0 | 0 | 0
244835 | 27.5-79.5 | 27.5 | -79.5 | 0 | 0 | 0
245556 | 27.5-80 | 27.5 | -80 | 0 | 0 | 0
246277 | 27.5-80.5 | 27.5 | -80.5 | 0 | 0 | 0
246998 | 27.5-81 | 27.5 | -81 | 0 | 0 | 0
247719 | 27.5-81.5 | 27.5 | -81.5 | 0 | 0 | 0
248440 | 27.5-82 | 27.5 | -82 | 0 | 0 | 0
249161 | 27.5-82.5 | 27.5 | -82.5 | 0 | 0 | 0
249882 | 27.5-83 | 27.5 | -83 | 0 | 0 | 0
250603 | 27.5-83.5 | 27.5 | -83.5 | 0 | 0 | 0
251324 | 27.5-84 | 27.5 | -84 | 0 | 0 | 0
252045 | 27.5-84.5 | 27.5 | -84.5 | 0 | 0 | 0
252766 | 27.5-85 | 27.5 | -85 | 0 | 0 | 0
253487 | 27.5-85.5 | 27.5 | -85.5 | 0 | 0 | 0
254208 | 27.5-86 | 27.5 | -86 | 0 | 0 | 0
254929 | 27.5-86.5 | 27.5 | -86.5 | 0 | 0 | 0
255650 | 27.5-87 | 27.5 | -87 | 0 | 0 | 0
256371 | 27.5-87.5 | 27.5 | -87.5 | 0 | 0 | 0
257092 | 27.5-88 | 27.5 | -88 | 0 | 0 | 0
257813 | 27.5-88.5 | 27.5 | -88.5 | 0 | 0 | 0
258534 | 27.5-89 | 27.5 | -89 | 0 | 0 | 0
259255 | 27.5-89.5 | 27.5 | -89.5 | 0 | 0 | 0
259976 | 27.5-90 | 27.5 | -90 | 0 | 0 | 0
215275 | 28-59 | 28 | -59 | 0 | 0 | 0
215996 | 28-59.5 | 28 | -59.5 | 0 | 0 | 0
216717 | 28-60 | 28 | -60 | 0 | 0 | 0
217438 | 28-60.5 | 28 | -60.5 | 0 | 0 | 0
218159 | 28-61 | 28 | -61 | 0 | 0 | 0
218880 | 28-61.5 | 28 | -61.5 | 0 | 0 | 0
219601 | 28-62 | 28 | -62 | 0 | 0 | 0
220322 | 28-62.5 | 28 | -62.5 | 0 | 0 | 0
221043 | 28-63 | 28 | -63 | 0 | 0 | 0
221764 | 28-63.5 | 28 | -63.5 | 0 | 0 | 0
222485 | 28-64 | 28 | -64 | 0 | 0 | 0
223206 | 28-64.5 | 28 | -64.5 | 0 | 0 | 0
223927 | 28-65 | 28 | -65 | 0 | 0 | 0
224648 | 28-65.5 | 28 | -65.5 | 0 | 0 | 0
225369 | 28-66 | 28 | -66 | 0 | 0 | 0
226090 | 28-66.5 | 28 | -66.5 | 0 | 0 | 0
226811 | 28-67 | 28 | -67 | 0 | 0 | 0
227532 | 28-67.5 | 28 | -67.5 | 0 | 0 | 0
228253 | 28-68 | 28 | -68 | 0 | 0 | 0
228974 | 28-68.5 | 28 | -68.5 | 0 | 0 | 0
229695 | 28-69 | 28 | -69 | 0 | 0 | 0
230416 | 28-69.5 | 28 | -69.5 | 0 | 0 | 0
231137 | 28-70 | 28 | -70 | 0 | 0 | 0
231858 | 28-70.5 | 28 | -70.5 | 0 | 0 | 0
232579 | 28-71 | 28 | -71 | 0 | 0 | 0
233300 | 28-71.5 | 28 | -71.5 | 0 | 0 | 0
234021 | 28-72 | 28 | -72 | 0 | 0 | 0
234742 | 28-72.5 | 28 | -72.5 | 0 | 0 | 0
235463 | 28-73 | 28 | -73 | 0 | 0 | 0
236184 | 28-73.5 | 28 | -73.5 | 0 | 0 | 0
236905 | 28-74 | 28 | -74 | 0 | 0 | 0
237626 | 28-74.5 | 28 | -74.5 | 0 | 0 | 0
238347 | 28-75 | 28 | -75 | 0 | 0 | 0
239068 | 28-75.5 | 28 | -75.5 | 0 | 0 | 0
239789 | 28-76 | 28 | -76 | 0 | 0 | 0
240510 | 28-76.5 | 28 | -76.5 | 0 | 0 | 0
241231 | 28-77 | 28 | -77 | 0 | 0 | 0
241952 | 28-77.5 | 28 | -77.5 | 0 | 0 | 0
242673 | 28-78 | 28 | -78 | 0 | 0 | 0
243394 | 28-78.5 | 28 | -78.5 | 0 | 0 | 0
244115 | 28-79 | 28 | -79 | 0 | 0 | 0
244836 | 28-79.5 | 28 | -79.5 | 0 | 0 | 0
245557 | 28-80 | 28 | -80 | 0 | 0 | 0
246278 | 28-80.5 | 28 | -80.5 | 0 | 0 | 0
246999 | 28-81 | 28 | -81 | 0 | 0 | 0
247720 | 28-81.5 | 28 | -81.5 | 0 | 0 | 0
248441 | 28-82 | 28 | -82 | 0 | 0 | 0
249162 | 28-82.5 | 28 | -82.5 | 0 | 0 | 0
249883 | 28-83 | 28 | -83 | 0 | 0 | 0
250604 | 28-83.5 | 28 | -83.5 | 0 | 0 | 0
251325 | 28-84 | 28 | -84 | 0 | 0 | 0
252046 | 28-84.5 | 28 | -84.5 | 0 | 0 | 0
252767 | 28-85 | 28 | -85 | 0 | 0 | 0
253488 | 28-85.5 | 28 | -85.5 | 0 | 0 | 0
254209 | 28-86 | 28 | -86 | 0 | 0 | 0
254930 | 28-86.5 | 28 | -86.5 | 0 | 0 | 0
255651 | 28-87 | 28 | -87 | 0 | 0 | 0
256372 | 28-87.5 | 28 | -87.5 | 0 | 0 | 0
257093 | 28-88 | 28 | -88 | 0 | 0 | 0
257814 | 28-88.5 | 28 | -88.5 | 0 | 0 | 0
258535 | 28-89 | 28 | -89 | 0 | 0 | 0
259256 | 28-89.5 | 28 | -89.5 | 0 | 0 | 0
259977 | 28-90 | 28 | -90 | 0 | 0 | 0
215276 | 28.5-59 | 28.5 | -59 | 0 | 0 | 0
215997 | 28.5-59.5 | 28.5 | -59.5 | 0 | 0 | 0
216718 | 28.5-60 | 28.5 | -60 | 0 | 0 | 0
217439 | 28.5-60.5 | 28.5 | -60.5 | 0 | 0 | 0
218160 | 28.5-61 | 28.5 | -61 | 0 | 0 | 0
218881 | 28.5-61.5 | 28.5 | -61.5 | 0 | 0 | 0
219602 | 28.5-62 | 28.5 | -62 | 0 | 0 | 0
220323 | 28.5-62.5 | 28.5 | -62.5 | 0 | 0 | 0
221044 | 28.5-63 | 28.5 | -63 | 0 | 0 | 0
221765 | 28.5-63.5 | 28.5 | -63.5 | 0 | 0 | 0
222486 | 28.5-64 | 28.5 | -64 | 0 | 0 | 0
223207 | 28.5-64.5 | 28.5 | -64.5 | 0 | 0 | 0
223928 | 28.5-65 | 28.5 | -65 | 0 | 0 | 0
224649 | 28.5-65.5 | 28.5 | -65.5 | 0 | 0 | 0
225370 | 28.5-66 | 28.5 | -66 | 0 | 0 | 0
226091 | 28.5-66.5 | 28.5 | -66.5 | 0 | 0 | 0
226812 | 28.5-67 | 28.5 | -67 | 0 | 0 | 0
227533 | 28.5-67.5 | 28.5 | -67.5 | 0 | 0 | 0
228254 | 28.5-68 | 28.5 | -68 | 0 | 0 | 0
228975 | 28.5-68.5 | 28.5 | -68.5 | 0 | 0 | 0
229696 | 28.5-69 | 28.5 | -69 | 0 | 0 | 0
230417 | 28.5-69.5 | 28.5 | -69.5 | 0 | 0 | 0
231138 | 28.5-70 | 28.5 | -70 | 0 | 0 | 0
231859 | 28.5-70.5 | 28.5 | -70.5 | 0 | 0 | 0
232580 | 28.5-71 | 28.5 | -71 | 0 | 0 | 0
233301 | 28.5-71.5 | 28.5 | -71.5 | 0 | 0 | 0
234022 | 28.5-72 | 28.5 | -72 | 0 | 0 | 0
234743 | 28.5-72.5 | 28.5 | -72.5 | 0 | 0 | 0
235464 | 28.5-73 | 28.5 | -73 | 0 | 0 | 0
236185 | 28.5-73.5 | 28.5 | -73.5 | 0 | 0 | 0
236906 | 28.5-74 | 28.5 | -74 | 0 | 0 | 0
237627 | 28.5-74.5 | 28.5 | -74.5 | 0 | 0 | 0
238348 | 28.5-75 | 28.5 | -75 | 0 | 0 | 0
239069 | 28.5-75.5 | 28.5 | -75.5 | 0 | 0 | 0
239790 | 28.5-76 | 28.5 | -76 | 0 | 0 | 0
240511 | 28.5-76.5 | 28.5 | -76.5 | 0 | 0 | 0
241232 | 28.5-77 | 28.5 | -77 | 0 | 0 | 0
241953 | 28.5-77.5 | 28.5 | -77.5 | 0 | 0 | 0
242674 | 28.5-78 | 28.5 | -78 | 0 | 0 | 0
243395 | 28.5-78.5 | 28.5 | -78.5 | 0 | 0 | 0
244116 | 28.5-79 | 28.5 | -79 | 0 | 0 | 0
244837 | 28.5-79.5 | 28.5 | -79.5 | 0 | 0 | 0
245558 | 28.5-80 | 28.5 | -80 | 0 | 0 | 0
246279 | 28.5-80.5 | 28.5 | -80.5 | 0 | 0 | 0
247000 | 28.5-81 | 28.5 | -81 | 0 | 0 | 0
247721 | 28.5-81.5 | 28.5 | -81.5 | 0 | 0 | 0
248442 | 28.5-82 | 28.5 | -82 | 0 | 0 | 0
249163 | 28.5-82.5 | 28.5 | -82.5 | 0 | 0 | 0
249884 | 28.5-83 | 28.5 | -83 | 0 | 0 | 0
250605 | 28.5-83.5 | 28.5 | -83.5 | 0 | 0 | 0
251326 | 28.5-84 | 28.5 | -84 | 0 | 0 | 0
252047 | 28.5-84.5 | 28.5 | -84.5 | 0 | 0 | 0
252768 | 28.5-85 | 28.5 | -85 | 0 | 0 | 0
253489 | 28.5-85.5 | 28.5 | -85.5 | 0 | 0 | 0
254210 | 28.5-86 | 28.5 | -86 | 0 | 0 | 0
254931 | 28.5-86.5 | 28.5 | -86.5 | 0 | 0 | 0
255652 | 28.5-87 | 28.5 | -87 | 0 | 0 | 0
256373 | 28.5-87.5 | 28.5 | -87.5 | 0 | 0 | 0
257094 | 28.5-88 | 28.5 | -88 | 0 | 0 | 0
257815 | 28.5-88.5 | 28.5 | -88.5 | 0 | 0 | 0
258536 | 28.5-89 | 28.5 | -89 | 0 | 0 | 0
259257 | 28.5-89.5 | 28.5 | -89.5 | 0 | 0 | 0
259978 | 28.5-90 | 28.5 | -90 | 0 | 0 | 0
215277 | 29-59 | 29 | -59 | 0 | 0 | 0
215998 | 29-59.5 | 29 | -59.5 | 0 | 0 | 0
216719 | 29-60 | 29 | -60 | 0 | 0 | 0
217440 | 29-60.5 | 29 | -60.5 | 0 | 0 | 0
218161 | 29-61 | 29 | -61 | 0 | 0 | 0
218882 | 29-61.5 | 29 | -61.5 | 0 | 0 | 0
219603 | 29-62 | 29 | -62 | 0 | 0 | 0
220324 | 29-62.5 | 29 | -62.5 | 0 | 0 | 0
221045 | 29-63 | 29 | -63 | 0 | 0 | 0
221766 | 29-63.5 | 29 | -63.5 | 0 | 0 | 0
222487 | 29-64 | 29 | -64 | 0 | 0 | 0
223208 | 29-64.5 | 29 | -64.5 | 0 | 0 | 0
223929 | 29-65 | 29 | -65 | 0 | 0 | 0
224650 | 29-65.5 | 29 | -65.5 | 0 | 0 | 0
225371 | 29-66 | 29 | -66 | 0 | 0 | 0
226092 | 29-66.5 | 29 | -66.5 | 0 | 0 | 0
226813 | 29-67 | 29 | -67 | 0 | 0 | 0
227534 | 29-67.5 | 29 | -67.5 | 0 | 0 | 0
228255 | 29-68 | 29 | -68 | 0 | 0 | 0
228976 | 29-68.5 | 29 | -68.5 | 0 | 0 | 0
229697 | 29-69 | 29 | -69 | 0 | 0 | 0
230418 | 29-69.5 | 29 | -69.5 | 0 | 0 | 0
231139 | 29-70 | 29 | -70 | 0 | 0 | 0
231860 | 29-70.5 | 29 | -70.5 | 0 | 0 | 0
232581 | 29-71 | 29 | -71 | 0 | 0 | 0
233302 | 29-71.5 | 29 | -71.5 | 0 | 0 | 0
234023 | 29-72 | 29 | -72 | 0 | 0 | 0
234744 | 29-72.5 | 29 | -72.5 | 0 | 0 | 0
235465 | 29-73 | 29 | -73 | 0 | 0 | 0
236186 | 29-73.5 | 29 | -73.5 | 0 | 0 | 0
236907 | 29-74 | 29 | -74 | 0 | 0 | 0
237628 | 29-74.5 | 29 | -74.5 | 0 | 0 | 0
238349 | 29-75 | 29 | -75 | 0 | 0 | 0
239070 | 29-75.5 | 29 | -75.5 | 0 | 0 | 0
239791 | 29-76 | 29 | -76 | 0 | 0 | 0
240512 | 29-76.5 | 29 | -76.5 | 0 | 0 | 0
241233 | 29-77 | 29 | -77 | 0 | 0 | 0
241954 | 29-77.5 | 29 | -77.5 | 0 | 0 | 0
242675 | 29-78 | 29 | -78 | 0 | 0 | 0
243396 | 29-78.5 | 29 | -78.5 | 0 | 0 | 0
244117 | 29-79 | 29 | -79 | 0 | 0 | 0
244838 | 29-79.5 | 29 | -79.5 | 0 | 0 | 0
245559 | 29-80 | 29 | -80 | 0 | 0 | 0
246280 | 29-80.5 | 29 | -80.5 | 0 | 0 | 0
247001 | 29-81 | 29 | -81 | 0 | 0 | 0
247722 | 29-81.5 | 29 | -81.5 | 0 | 0 | 0
248443 | 29-82 | 29 | -82 | 0 | 0 | 0
249164 | 29-82.5 | 29 | -82.5 | 0 | 0 | 0
249885 | 29-83 | 29 | -83 | 0 | 0 | 0
250606 | 29-83.5 | 29 | -83.5 | 0 | 0 | 0
251327 | 29-84 | 29 | -84 | 0 | 0 | 0
252048 | 29-84.5 | 29 | -84.5 | 0 | 0 | 0
252769 | 29-85 | 29 | -85 | 0 | 0 | 0
253490 | 29-85.5 | 29 | -85.5 | 0 | 0 | 0
254211 | 29-86 | 29 | -86 | 0 | 0 | 0
254932 | 29-86.5 | 29 | -86.5 | 0 | 0 | 0
255653 | 29-87 | 29 | -87 | 0 | 0 | 0
256374 | 29-87.5 | 29 | -87.5 | 0 | 0 | 0
257095 | 29-88 | 29 | -88 | 0 | 0 | 0
257816 | 29-88.5 | 29 | -88.5 | 0 | 0 | 0
258537 | 29-89 | 29 | -89 | 0 | 0 | 0
259258 | 29-89.5 | 29 | -89.5 | 0 | 0 | 0
259979 | 29-90 | 29 | -90 | 0 | 0 | 0
215278 | 29.5-59 | 29.5 | -59 | 0 | 0 | 0
215999 | 29.5-59.5 | 29.5 | -59.5 | 0 | 0 | 0
216720 | 29.5-60 | 29.5 | -60 | 0 | 0 | 0
217441 | 29.5-60.5 | 29.5 | -60.5 | 0 | 0 | 0
218162 | 29.5-61 | 29.5 | -61 | 0 | 0 | 0
218883 | 29.5-61.5 | 29.5 | -61.5 | 0 | 0 | 0
219604 | 29.5-62 | 29.5 | -62 | 0 | 0 | 0
220325 | 29.5-62.5 | 29.5 | -62.5 | 0 | 0 | 0
221046 | 29.5-63 | 29.5 | -63 | 0 | 0 | 0
221767 | 29.5-63.5 | 29.5 | -63.5 | 0 | 0 | 0
222488 | 29.5-64 | 29.5 | -64 | 0 | 0 | 0
223209 | 29.5-64.5 | 29.5 | -64.5 | 0 | 0 | 0
223930 | 29.5-65 | 29.5 | -65 | 0 | 0 | 0
224651 | 29.5-65.5 | 29.5 | -65.5 | 0 | 0 | 0
225372 | 29.5-66 | 29.5 | -66 | 0 | 0 | 0
226093 | 29.5-66.5 | 29.5 | -66.5 | 0 | 0 | 0
226814 | 29.5-67 | 29.5 | -67 | 0 | 0 | 0
227535 | 29.5-67.5 | 29.5 | -67.5 | 0 | 0 | 0
228256 | 29.5-68 | 29.5 | -68 | 0 | 0 | 0
228977 | 29.5-68.5 | 29.5 | -68.5 | 0 | 0 | 0
229698 | 29.5-69 | 29.5 | -69 | 0 | 0 | 0
230419 | 29.5-69.5 | 29.5 | -69.5 | 0 | 0 | 0
231140 | 29.5-70 | 29.5 | -70 | 0 | 0 | 0
231861 | 29.5-70.5 | 29.5 | -70.5 | 0 | 0 | 0
232582 | 29.5-71 | 29.5 | -71 | 0 | 0 | 0
233303 | 29.5-71.5 | 29.5 | -71.5 | 0 | 0 | 0
234024 | 29.5-72 | 29.5 | -72 | 0 | 0 | 0
234745 | 29.5-72.5 | 29.5 | -72.5 | 0 | 0 | 0
235466 | 29.5-73 | 29.5 | -73 | 0 | 0 | 0
236187 | 29.5-73.5 | 29.5 | -73.5 | 0 | 0 | 0
236908 | 29.5-74 | 29.5 | -74 | 0 | 0 | 0
237629 | 29.5-74.5 | 29.5 | -74.5 | 0 | 0 | 0
238350 | 29.5-75 | 29.5 | -75 | 0 | 0 | 0
239071 | 29.5-75.5 | 29.5 | -75.5 | 0 | 0 | 0
239792 | 29.5-76 | 29.5 | -76 | 0 | 0 | 0
240513 | 29.5-76.5 | 29.5 | -76.5 | 0 | 0 | 0
241234 | 29.5-77 | 29.5 | -77 | 0 | 0 | 0
241955 | 29.5-77.5 | 29.5 | -77.5 | 0 | 0 | 0
242676 | 29.5-78 | 29.5 | -78 | 0 | 0 | 0
243397 | 29.5-78.5 | 29.5 | -78.5 | 0 | 0 | 0
244118 | 29.5-79 | 29.5 | -79 | 0 | 0 | 0
244839 | 29.5-79.5 | 29.5 | -79.5 | 0 | 0 | 0
245560 | 29.5-80 | 29.5 | -80 | 0 | 0 | 0
246281 | 29.5-80.5 | 29.5 | -80.5 | 0 | 0 | 0
247002 | 29.5-81 | 29.5 | -81 | 0 | 0 | 0
247723 | 29.5-81.5 | 29.5 | -81.5 | 0 | 0 | 0
248444 | 29.5-82 | 29.5 | -82 | 0 | 0 | 0
249165 | 29.5-82.5 | 29.5 | -82.5 | 0 | 0 | 0
249886 | 29.5-83 | 29.5 | -83 | 0 | 0 | 0
250607 | 29.5-83.5 | 29.5 | -83.5 | 0 | 0 | 0
251328 | 29.5-84 | 29.5 | -84 | 0 | 0 | 0
252049 | 29.5-84.5 | 29.5 | -84.5 | 0 | 0 | 0
252770 | 29.5-85 | 29.5 | -85 | 0 | 0 | 0
253491 | 29.5-85.5 | 29.5 | -85.5 | 0 | 0 | 0
254212 | 29.5-86 | 29.5 | -86 | 0 | 0 | 0
254933 | 29.5-86.5 | 29.5 | -86.5 | 0 | 0 | 0
255654 | 29.5-87 | 29.5 | -87 | 0 | 0 | 0
256375 | 29.5-87.5 | 29.5 | -87.5 | 0 | 0 | 0
257096 | 29.5-88 | 29.5 | -88 | 0 | 0 | 0
257817 | 29.5-88.5 | 29.5 | -88.5 | 0 | 0 | 0
258538 | 29.5-89 | 29.5 | -89 | 0 | 0 | 0
259259 | 29.5-89.5 | 29.5 | -89.5 | 0 | 0 | 0
259980 | 29.5-90 | 29.5 | -90 | 0 | 0 | 0
215279 | 30-59 | 30 | -59 | 0 | 0 | 0
216000 | 30-59.5 | 30 | -59.5 | 0 | 0 | 0
216721 | 30-60 | 30 | -60 | 0 | 0 | 0
217442 | 30-60.5 | 30 | -60.5 | 0 | 0 | 0
218163 | 30-61 | 30 | -61 | 0 | 0 | 0
218884 | 30-61.5 | 30 | -61.5 | 0 | 0 | 0
219605 | 30-62 | 30 | -62 | 0 | 0 | 0
220326 | 30-62.5 | 30 | -62.5 | 0 | 0 | 0
221047 | 30-63 | 30 | -63 | 0 | 0 | 0
221768 | 30-63.5 | 30 | -63.5 | 0 | 0 | 0
222489 | 30-64 | 30 | -64 | 0 | 0 | 0
223210 | 30-64.5 | 30 | -64.5 | 0 | 0 | 0
223931 | 30-65 | 30 | -65 | 0 | 0 | 0
224652 | 30-65.5 | 30 | -65.5 | 0 | 0 | 0
225373 | 30-66 | 30 | -66 | 0 | 0 | 0
226094 | 30-66.5 | 30 | -66.5 | 0 | 0 | 0
226815 | 30-67 | 30 | -67 | 0 | 0 | 0
227536 | 30-67.5 | 30 | -67.5 | 0 | 0 | 0
228257 | 30-68 | 30 | -68 | 0 | 0 | 0
228978 | 30-68.5 | 30 | -68.5 | 0 | 0 | 0
229699 | 30-69 | 30 | -69 | 0 | 0 | 0
230420 | 30-69.5 | 30 | -69.5 | 0 | 0 | 0
231141 | 30-70 | 30 | -70 | 0 | 0 | 0
231862 | 30-70.5 | 30 | -70.5 | 0 | 0 | 0
232583 | 30-71 | 30 | -71 | 0 | 0 | 0
233304 | 30-71.5 | 30 | -71.5 | 0 | 0 | 0
234025 | 30-72 | 30 | -72 | 0 | 0 | 0
234746 | 30-72.5 | 30 | -72.5 | 0 | 0 | 0
235467 | 30-73 | 30 | -73 | 0 | 0 | 0
236188 | 30-73.5 | 30 | -73.5 | 0 | 0 | 0
236909 | 30-74 | 30 | -74 | 0 | 0 | 0
237630 | 30-74.5 | 30 | -74.5 | 0 | 0 | 0
238351 | 30-75 | 30 | -75 | 0 | 0 | 0
239072 | 30-75.5 | 30 | -75.5 | 0 | 0 | 0
239793 | 30-76 | 30 | -76 | 0 | 0 | 0
240514 | 30-76.5 | 30 | -76.5 | 0 | 0 | 0
241235 | 30-77 | 30 | -77 | 0 | 0 | 0
241956 | 30-77.5 | 30 | -77.5 | 0 | 0 | 0
242677 | 30-78 | 30 | -78 | 0 | 0 | 0
243398 | 30-78.5 | 30 | -78.5 | 0 | 0 | 0
244119 | 30-79 | 30 | -79 | 0 | 0 | 0
244840 | 30-79.5 | 30 | -79.5 | 0 | 0 | 0
245561 | 30-80 | 30 | -80 | 0 | 0 | 0
246282 | 30-80.5 | 30 | -80.5 | 0 | 0 | 0
247003 | 30-81 | 30 | -81 | 0 | 0 | 0
247724 | 30-81.5 | 30 | -81.5 | 0 | 0 | 0
248445 | 30-82 | 30 | -82 | 0 | 0 | 0
249166 | 30-82.5 | 30 | -82.5 | 0 | 0 | 0
249887 | 30-83 | 30 | -83 | 0 | 0 | 0
250608 | 30-83.5 | 30 | -83.5 | 0 | 0 | 0
251329 | 30-84 | 30 | -84 | 0 | 0 | 0
252050 | 30-84.5 | 30 | -84.5 | 0 | 0 | 0
252771 | 30-85 | 30 | -85 | 0 | 0 | 0
253492 | 30-85.5 | 30 | -85.5 | 0 | 0 | 0
254213 | 30-86 | 30 | -86 | 0 | 0 | 0
254934 | 30-86.5 | 30 | -86.5 | 0 | 0 | 0
255655 | 30-87 | 30 | -87 | 0 | 0 | 0
256376 | 30-87.5 | 30 | -87.5 | 0 | 0 | 0
257097 | 30-88 | 30 | -88 | 0 | 0 | 0
257818 | 30-88.5 | 30 | -88.5 | 0 | 0 | 0
258539 | 30-89 | 30 | -89 | 0 | 0 | 0
259260 | 30-89.5 | 30 | -89.5 | 0 | 0 | 0
259981 | 30-90 | 30 | -90 | 0 | 0 | 0
212338 | 1.5-57 | 1.5 | -57 | 0 | 0 | 0
212339 | 2-57 | 2 | -57 | 0 | 0 | 0
212340 | 2.5-57 | 2.5 | -57 | 0 | 0 | 0
212341 | 3-57 | 3 | -57 | 0 | 0 | 0
212342 | 3.5-57 | 3.5 | -57 | 0 | 0 | 0
212343 | 4-57 | 4 | -57 | 0 | 0 | 0
212344 | 4.5-57 | 4.5 | -57 | 0 | 0 | 0
212345 | 5-57 | 5 | -57 | 0 | 0 | 0
212346 | 5.5-57 | 5.5 | -57 | 0 | 0 | 0
212347 | 6-57 | 6 | -57 | 0 | 0 | 0
212348 | 6.5-57 | 6.5 | -57 | 0 | 0 | 0
212349 | 7-57 | 7 | -57 | 0 | 0 | 0
212350 | 7.5-57 | 7.5 | -57 | 0 | 0 | 0
212351 | 8-57 | 8 | -57 | 0 | 0 | 0
213059 | 1.5-57.5 | 1.5 | -57.5 | 0 | 0 | 0
213060 | 2-57.5 | 2 | -57.5 | 0 | 0 | 0
213061 | 2.5-57.5 | 2.5 | -57.5 | 0 | 0 | 0
213062 | 3-57.5 | 3 | -57.5 | 0 | 0 | 0
213063 | 3.5-57.5 | 3.5 | -57.5 | 0 | 0 | 0
213064 | 4-57.5 | 4 | -57.5 | 0 | 0 | 0
213065 | 4.5-57.5 | 4.5 | -57.5 | 0 | 0 | 0
213066 | 5-57.5 | 5 | -57.5 | 0 | 0 | 0
213067 | 5.5-57.5 | 5.5 | -57.5 | 0 | 0 | 0
213068 | 6-57.5 | 6 | -57.5 | 0 | 0 | 0
213069 | 6.5-57.5 | 6.5 | -57.5 | 0 | 0 | 0
213070 | 7-57.5 | 7 | -57.5 | 0 | 0 | 0
213071 | 7.5-57.5 | 7.5 | -57.5 | 0 | 0 | 0
213072 | 8-57.5 | 8 | -57.5 | 0 | 0 | 0
213780 | 1.5-58 | 1.5 | -58 | 0 | 0 | 0
213781 | 2-58 | 2 | -58 | 0 | 0 | 0
213782 | 2.5-58 | 2.5 | -58 | 0 | 0 | 0
213783 | 3-58 | 3 | -58 | 0 | 0 | 0
213784 | 3.5-58 | 3.5 | -58 | 0 | 0 | 0
213785 | 4-58 | 4 | -58 | 0 | 0 | 0
213786 | 4.5-58 | 4.5 | -58 | 0 | 0 | 0
213787 | 5-58 | 5 | -58 | 0 | 0 | 0
213788 | 5.5-58 | 5.5 | -58 | 0 | 0 | 0
213789 | 6-58 | 6 | -58 | 0 | 0 | 0
213790 | 6.5-58 | 6.5 | -58 | 0 | 0 | 0
213791 | 7-58 | 7 | -58 | 0 | 0 | 0
213792 | 7.5-58 | 7.5 | -58 | 0 | 0 | 0
213793 | 8-58 | 8 | -58 | 0 | 0 | 0
214501 | 1.5-58.5 | 1.5 | -58.5 | 0 | 0 | 0
214502 | 2-58.5 | 2 | -58.5 | 0 | 0 | 0
214503 | 2.5-58.5 | 2.5 | -58.5 | 0 | 0 | 0
214504 | 3-58.5 | 3 | -58.5 | 0 | 0 | 0
214505 | 3.5-58.5 | 3.5 | -58.5 | 0 | 0 | 0
214506 | 4-58.5 | 4 | -58.5 | 0 | 0 | 0
214507 | 4.5-58.5 | 4.5 | -58.5 | 0 | 0 | 0
214508 | 5-58.5 | 5 | -58.5 | 0 | 0 | 0
214509 | 5.5-58.5 | 5.5 | -58.5 | 0 | 0 | 0
214510 | 6-58.5 | 6 | -58.5 | 0 | 0 | 0
214511 | 6.5-58.5 | 6.5 | -58.5 | 0 | 0 | 0
214512 | 7-58.5 | 7 | -58.5 | 0 | 0 | 0
214513 | 7.5-58.5 | 7.5 | -58.5 | 0 | 0 | 0
214514 | 8-58.5 | 8 | -58.5 | 0 | 0 | 0
215222 | 1.5-59 | 1.5 | -59 | 0 | 0 | 0
215223 | 2-59 | 2 | -59 | 0 | 0 | 0
215224 | 2.5-59 | 2.5 | -59 | 0 | 0 | 0
215225 | 3-59 | 3 | -59 | 0 | 0 | 0
215226 | 3.5-59 | 3.5 | -59 | 0 | 0 | 0
215227 | 4-59 | 4 | -59 | 0 | 0 | 0
215228 | 4.5-59 | 4.5 | -59 | 0 | 0 | 0
215229 | 5-59 | 5 | -59 | 0 | 0 | 0
215230 | 5.5-59 | 5.5 | -59 | 0 | 0 | 0
215231 | 6-59 | 6 | -59 | 0 | 0 | 0
215232 | 6.5-59 | 6.5 | -59 | 0 | 0 | 0
215233 | 7-59 | 7 | -59 | 0 | 0 | 0
215234 | 7.5-59 | 7.5 | -59 | 0 | 0 | 0
215235 | 8-59 | 8 | -59 | 0 | 0 | 0
215943 | 1.5-59.5 | 1.5 | -59.5 | 0 | 0 | 0
215944 | 2-59.5 | 2 | -59.5 | 0 | 0 | 0
215945 | 2.5-59.5 | 2.5 | -59.5 | 0 | 0 | 0
215946 | 3-59.5 | 3 | -59.5 | 0 | 0 | 0
215947 | 3.5-59.5 | 3.5 | -59.5 | 0 | 0 | 0
215948 | 4-59.5 | 4 | -59.5 | 0 | 0 | 0
215949 | 4.5-59.5 | 4.5 | -59.5 | 0 | 0 | 0
215950 | 5-59.5 | 5 | -59.5 | 0 | 0 | 0
215951 | 5.5-59.5 | 5.5 | -59.5 | 0 | 0 | 0
215952 | 6-59.5 | 6 | -59.5 | 0 | 0 | 0
215953 | 6.5-59.5 | 6.5 | -59.5 | 0 | 0 | 0
215954 | 7-59.5 | 7 | -59.5 | 0 | 0 | 0
215955 | 7.5-59.5 | 7.5 | -59.5 | 0 | 0 | 0
215956 | 8-59.5 | 8 | -59.5 | 0 | 0 | 0
216664 | 1.5-60 | 1.5 | -60 | 0 | 0 | 0
216665 | 2-60 | 2 | -60 | 0 | 0 | 0
216666 | 2.5-60 | 2.5 | -60 | 0 | 0 | 0
216667 | 3-60 | 3 | -60 | 0 | 0 | 0
216668 | 3.5-60 | 3.5 | -60 | 0 | 0 | 0
216669 | 4-60 | 4 | -60 | 0 | 0 | 0
216670 | 4.5-60 | 4.5 | -60 | 0 | 0 | 0
216671 | 5-60 | 5 | -60 | 0 | 0 | 0
216672 | 5.5-60 | 5.5 | -60 | 0 | 0 | 0
216673 | 6-60 | 6 | -60 | 0 | 0 | 0
216674 | 6.5-60 | 6.5 | -60 | 0 | 0 | 0
216675 | 7-60 | 7 | -60 | 0 | 0 | 0
216676 | 7.5-60 | 7.5 | -60 | 0 | 0 | 0
216677 | 8-60 | 8 | -60 | 0 | 0 | 0
217385 | 1.5-60.5 | 1.5 | -60.5 | 0 | 0 | 0
217386 | 2-60.5 | 2 | -60.5 | 0 | 0 | 0
217387 | 2.5-60.5 | 2.5 | -60.5 | 0 | 0 | 0
217388 | 3-60.5 | 3 | -60.5 | 0 | 0 | 0
217389 | 3.5-60.5 | 3.5 | -60.5 | 0 | 0 | 0
217390 | 4-60.5 | 4 | -60.5 | 0 | 0 | 0
217391 | 4.5-60.5 | 4.5 | -60.5 | 0 | 0 | 0
217392 | 5-60.5 | 5 | -60.5 | 0 | 0 | 0
217393 | 5.5-60.5 | 5.5 | -60.5 | 0 | 0 | 0
217394 | 6-60.5 | 6 | -60.5 | 0 | 0 | 0
217395 | 6.5-60.5 | 6.5 | -60.5 | 0 | 0 | 0
217396 | 7-60.5 | 7 | -60.5 | 0 | 0 | 0
217397 | 7.5-60.5 | 7.5 | -60.5 | 0 | 0 | 0
217398 | 8-60.5 | 8 | -60.5 | 0 | 0 | 0
218106 | 1.5-61 | 1.5 | -61 | 0 | 0 | 0
218107 | 2-61 | 2 | -61 | 0 | 0 | 0
218108 | 2.5-61 | 2.5 | -61 | 0 | 0 | 0
218109 | 3-61 | 3 | -61 | 0 | 0 | 0
218110 | 3.5-61 | 3.5 | -61 | 0 | 0 | 0
218111 | 4-61 | 4 | -61 | 0 | 0 | 0
218112 | 4.5-61 | 4.5 | -61 | 0 | 0 | 0
218113 | 5-61 | 5 | -61 | 0 | 0 | 0
218114 | 5.5-61 | 5.5 | -61 | 0 | 0 | 0
218115 | 6-61 | 6 | -61 | 0 | 0 | 0
218116 | 6.5-61 | 6.5 | -61 | 0 | 0 | 0
218117 | 7-61 | 7 | -61 | 0 | 0 | 0
218118 | 7.5-61 | 7.5 | -61 | 0 | 0 | 0
218119 | 8-61 | 8 | -61 | 0 | 0 | 0
257069 | 16-88 | 16 | -88 | 0 | 0 | 0
257070 | 16.5-88 | 16.5 | -88 | 0 | 0 | 0
257071 | 17-88 | 17 | -88 | 0 | 0 | 0
257072 | 17.5-88 | 17.5 | -88 | 0 | 0 | 0
257073 | 18-88 | 18 | -88 | 0 | 0 | 0
257074 | 18.5-88 | 18.5 | -88 | 0 | 0 | 0
257790 | 16-88.5 | 16 | -88.5 | 0 | 0 | 0
257791 | 16.5-88.5 | 16.5 | -88.5 | 0 | 0 | 0
257792 | 17-88.5 | 17 | -88.5 | 0 | 0 | 0
257793 | 17.5-88.5 | 17.5 | -88.5 | 0 | 0 | 0
257794 | 18-88.5 | 18 | -88.5 | 0 | 0 | 0
257795 | 18.5-88.5 | 18.5 | -88.5 | 0 | 0 | 0
258511 | 16-89 | 16 | -89 | 0 | 0 | 0
258512 | 16.5-89 | 16.5 | -89 | 0 | 0 | 0
258513 | 17-89 | 17 | -89 | 0 | 0 | 0
258514 | 17.5-89 | 17.5 | -89 | 0 | 0 | 0
258515 | 18-89 | 18 | -89 | 0 | 0 | 0
258516 | 18.5-89 | 18.5 | -89 | 0 | 0 | 0

## H1-Earthquakes (hidden)
|  |  | 0.4% | 0.2105% | 0.1026% | 0.06667% | 0.0404%
|  | 10.7005 | PGA - 250 yrs | PGA - 475 yrs | PGA - 975 yrs | PGA - 1500 yrs | PGA - 2475 yrs
Longitudes (x) | Latitudes (y) | Distance | cm/seg2 | cm/seg2 | cm/seg2 | cm/seg2 | cm/seg2 | Probability
-90 | 9 | 2029.6199 | 8.3719 | 10.732 | 13.3183 | 14.9926 | 17.2275 | 0.007291%
-89.5 | 9 | 1996.7554 | 9.9858 | 12.5531 | 15.4371 | 17.5063 | 20.2905 | 0.01156%
-89 | 9 | 1963.9173 | 12.0641 | 14.5935 | 18.2277 | 20.8675 | 24.4565 | 0.02061%
-88.5 | 9 | 1931.107 | 14.0414 | 17.3017 | 22.0813 | 25.6129 | 29.2169 | 0.03912%
-88 | 9 | 1898.326 | 16.8055 | 21.2863 | 27.3994 | 30.91 | 35.607 | 0.07237%
-87.5 | 9 | 1865.5761 | 21.123 | 27.2591 | 34.0009 | 38.8928 | 45.5375 | 0.1467%
-87 | 9 | 1832.8591 | 27.8197 | 34.5355 | 44.4608 | 51.8451 | 61.1977 | 0.3199%
-86.5 | 9 | 1800.1768 | 36.6939 | 47.7427 | 63.2606 | 72.9775 | 86.2989 | 0.7109%
-86 | 9 | 1767.5314 | 59.4568 | 78.5816 | 108.847 | 132.5075 | 162.7325 | 1.874%
-85.5 | 9 | 1734.925 | 85.0914 | 117.086 | 161.9981 | 194.8798 | 242.0694 | 4.079%
-85 | 9 | 1702.36 | 122.7044 | 163.144 | 222.6304 | 268.97 | 326.4485 | 10.8%
-84.5 | 9 | 1669.8389 | 165.2127 | 221.8017 | 308.7654 | 362.7509 | 438.2507 | 22.05%
-84 | 9 | 1637.3645 | 176.8032 | 235.0614 | 319.5294 | 372.1938 | 445.1602 | 33.17%
-83.5 | 9 | 1604.9398 | 168.0469 | 219.5259 | 298.8553 | 345.4461 | 409.4582 | 33.19%
-83 | 9 | 1572.5679 | 147.1881 | 185.952 | 244.3486 | 288.5038 | 336.1487 | 31.2%
-82.5 | 9 | 1540.2524 | 131.5803 | 165.457 | 216.231 | 254.457 | 304.9669 | 22.02%
-82 | 9 | 1507.9968 | 104.3012 | 139.8631 | 184.6123 | 218.5686 | 266.4583 | 8.912%
-81.5 | 9 | 1475.8054 | 75.5115 | 101.338 | 141.4128 | 169.9517 | 210.8656 | 3.158%
-81 | 9 | 1443.6825 | 54.5192 | 72.6908 | 100.0677 | 121.5418 | 151.0773 | 1.535%
-80.5 | 9 | 1411.6329 | 49.7846 | 67.0761 | 91.1407 | 109.8234 | 136.0507 | 1.298%
-80 | 9 | 1379.6618 | 58.872 | 76.5352 | 103.9885 | 125.3012 | 150.6685 | 2.04%
-79.5 | 9 | 1347.775 | 69.7798 | 91.7081 | 126.1978 | 147.7355 | 175.914 | 3.244%
-79 | 9 | 1315.9787 | 80.7914 | 107.3986 | 144.6704 | 168.0524 | 200.351 | 5.042%
-78.5 | 9 | 1284.2798 | 89.969 | 120.58 | 158.0086 | 183.6541 | 219.1023 | 7.247%
-78 | 9 | 1252.6856 | 96.3102 | 129.8679 | 166.9749 | 194.2488 | 231.9843 | 9.207%
-77.5 | 9 | 1221.2046 | 99.0838 | 133.5974 | 172.6684 | 201.8268 | 242.3791 | 9.338%
-77 | 9 | 1189.8458 | 93.7241 | 127.9185 | 169.7324 | 200.8928 | 244.8254 | 6.506%
-76.5 | 9 | 1158.6192 | 82.8143 | 113.181 | 156.7911 | 188.1499 | 233.0324 | 3.909%
-76 | 9 | 1127.5359 | 75.5196 | 103.1635 | 145.494 | 175.099 | 217.6054 | 3.003%
-75.5 | 9 | 1096.6083 | 75.8602 | 104.9865 | 149.928 | 182.5477 | 229.982 | 2.765%
-75 | 9 | 1065.8499 | 79.1824 | 110.8278 | 158.6875 | 194.4098 | 246.7077 | 2.895%
-74.5 | 9 | 1035.2761 | 79.4769 | 111.3093 | 159.0835 | 194.6021 | 246.5162 | 2.946%
-74 | 9 | 1004.9037 | 76.265 | 106.0912 | 151.5969 | 184.4156 | 232.093 | 2.79%
-73.5 | 9 | 974.7518 | 76.6663 | 107.6341 | 155.2699 | 190.5847 | 242.3935 | 2.642%
-73 | 9 | 944.8414 | 80.2058 | 114.606 | 166.9507 | 207.4268 | 267.6017 | 2.659%
-72.5 | 9 | 915.1965 | 89.3002 | 131.1079 | 191.5976 | 241.3255 | 314.1702 | 3.029%
-72 | 9 | 885.8437 | 105.228 | 154.287 | 230.6363 | 294.5262 | 379.9367 | 3.816%
-71.5 | 9 | 856.8133 | 126.6797 | 183.1252 | 279.4264 | 352.0915 | 457.9675 | 5.217%
-71 | 9 | 828.1391 | 148.0645 | 216.4066 | 331.0881 | 417.8535 | 549.0745 | 6.58%
-70.5 | 9 | 799.8597 | 157.2679 | 231.005 | 351.4778 | 443.9887 | 584.0375 | 7.345%
-70 | 9 | 772.0185 | 152.9403 | 225.1097 | 344.8876 | 436.9607 | 576.8007 | 6.745%
-69.5 | 9 | 744.6648 | 123.2176 | 180.2633 | 277.7439 | 352.4584 | 462.0405 | 4.645%
-69 | 9 | 717.8544 | 86.3339 | 125.8329 | 183.325 | 229.5694 | 298.4248 | 2.924%
-68.5 | 9 | 691.6506 | 56.2271 | 76.7112 | 109.1495 | 134.5632 | 166.0988 | 1.51%
-68 | 9 | 666.125 | 38.0551 | 52.6852 | 71.9121 | 85.6263 | 105.0889 | 0.7181%
-67.5 | 9 | 641.3588 | 31.1498 | 41.9918 | 59.1901 | 69.5514 | 84.0447 | 0.4505%
-67 | 9 | 617.4435 | 27.2568 | 36.4613 | 51.221 | 61.9494 | 75.0875 | 0.3274%
-66.5 | 9 | 594.4817 | 24.1131 | 32.4727 | 44.8576 | 54.5986 | 66.4816 | 0.2492%
-66 | 9 | 572.5883 | 22.7953 | 30.6071 | 41.1606 | 49.2874 | 60.1715 | 0.2144%
-65.5 | 9 | 551.8906 | 24.9029 | 32.4007 | 43.4103 | 51.8636 | 62.315 | 0.2543%
-65 | 9 | 532.5281 | 28.7244 | 37.1911 | 50.2922 | 59.7584 | 69.6601 | 0.3652%
-64.5 | 9 | 514.6516 | 34.6225 | 45.9252 | 61.9608 | 70.9592 | 83.1978 | 0.6125%
-64 | 9 | 498.421 | 43.9542 | 59.9245 | 76.8209 | 89.3496 | 106.6799 | 1.167%
-63.5 | 9 | 484.0021 | 56.1676 | 72.5058 | 96.3055 | 114.4545 | 137.6784 | 1.989%
-63 | 9 | 471.561 | 60.0729 | 76.6145 | 101.7924 | 120.9967 | 143.7952 | 2.436%
-62.5 | 9 | 461.2579 | 62.8371 | 80.8753 | 108.6062 | 129.9367 | 153.8484 | 2.603%
-62 | 9 | 453.2387 | 65.8152 | 85.6069 | 116.3862 | 138.2394 | 164.16 | 2.838%
-61.5 | 9 | 447.6261 | 65.4072 | 84.9722 | 115.3584 | 137.1499 | 162.568 | 2.811%
-61 | 9 | 444.5114 | 65.214 | 84.8249 | 115.3229 | 137.202 | 162.7239 | 2.768%
-60.5 | 9 | 443.9471 | 60.1811 | 77.9507 | 105.4589 | 126.7424 | 151.2651 | 2.221%
-60 | 9 | 445.943 | 42.129 | 57.7106 | 75.8375 | 89.4377 | 108.5371 | 0.9702%
-59.5 | 9 | 450.4649 | 28.8429 | 37.6432 | 51.3796 | 61.1665 | 72.6248 | 0.369%
-59 | 9 | 457.438 | 19.0427 | 26.1957 | 34.741 | 41.2496 | 50.4578 | 0.1428%
-90 | 9.5 | 2020.6258 | 11.1135 | 13.4953 | 16.6928 | 18.9976 | 22.1108 | 0.01454%
-89.5 | 9.5 | 1987.6729 | 12.9483 | 15.7654 | 19.8416 | 22.8204 | 26.6224 | 0.02777%
-89 | 9.5 | 1954.7424 | 15.2656 | 18.9935 | 24.5165 | 27.8575 | 31.8563 | 0.05174%
-88.5 | 9.5 | 1921.8356 | 18.6707 | 24.0326 | 30.1577 | 34.1737 | 39.573 | 0.0995%
-88 | 9.5 | 1888.9537 | 24.5624 | 30.4633 | 38.3489 | 44.1125 | 51.9894 | 0.2181%
-87.5 | 9.5 | 1856.0983 | 32.2266 | 40.697 | 53.4515 | 61.9399 | 72.0127 | 0.4985%
-87 | 9.5 | 1823.2708 | 47.969 | 63.7956 | 84.2479 | 99.7732 | 121.6762 | 1.317%
-86.5 | 9.5 | 1790.4731 | 73.0566 | 97.7467 | 136.2501 | 161.7593 | 197.8452 | 3.128%
-86 | 9.5 | 1757.7069 | 112.4757 | 157.2871 | 224.4474 | 278.6369 | 350.0074 | 5.833%
-85.5 | 9.5 | 1724.9741 | 124.3174 | 167.6744 | 234.2055 | 286.9922 | 352.4582 | 9.009%
-85 | 9.5 | 1692.2768 | 145.5329 | 194.0709 | 271.6372 | 325.2721 | 394.009 | 14.81%
-84.5 | 9.5 | 1659.6172 | 141.0375 | 178.6503 | 235.4755 | 278.5469 | 328.0405 | 25.58%
-84 | 9.5 | 1626.9977 | 145.4133 | 184.1765 | 242.7339 | 287.1146 | 335.4623 | 28.68%
-83.5 | 9.5 | 1594.421 | 143.5018 | 181.5153 | 238.8577 | 282.2644 | 330.7723 | 27.92%
-83 | 9.5 | 1561.8897 | 144.2072 | 183.8231 | 244.0888 | 290.0349 | 339.4171 | 25.32%
-82.5 | 9.5 | 1529.407 | 165.2669 | 232.2225 | 339.5464 | 420.9201 | 541.5991 | 10.86%
-82 | 9.5 | 1496.9761 | 121.4637 | 168.3302 | 242.0784 | 301.3233 | 381.1946 | 6.573%
-81.5 | 9.5 | 1464.6007 | 81.4775 | 114.9029 | 166.7109 | 207.2503 | 267.5577 | 2.784%
-81 | 9.5 | 1432.2845 | 53.3306 | 70.8155 | 95.9538 | 115.4273 | 140.9478 | 1.572%
-80.5 | 9.5 | 1400.0318 | 53.2551 | 70.7855 | 95.8872 | 115.3281 | 140.6801 | 1.57%
-80 | 9.5 | 1367.8473 | 66.3658 | 87.4673 | 120.759 | 143.0057 | 170.4794 | 2.743%
-79.5 | 9.5 | 1335.736 | 78.8264 | 105.2454 | 142.9425 | 166.1978 | 198.3536 | 4.546%
-79 | 9.5 | 1303.7035 | 90.1479 | 121.9942 | 160.0898 | 186.5001 | 223.0965 | 6.978%
-78.5 | 9.5 | 1271.7557 | 96.7924 | 131.6544 | 169.4275 | 197.5217 | 236.4826 | 8.941%
-78 | 9.5 | 1239.8994 | 97.7459 | 132.4659 | 170.3053 | 198.427 | 237.4008 | 9.34%
-77.5 | 9.5 | 1208.142 | 92.8333 | 125.4765 | 163.0789 | 189.8018 | 226.7931 | 7.905%
-77 | 9.5 | 1176.4915 | 83.691 | 112.076 | 150.0296 | 174.6458 | 208.7277 | 5.493%
-76.5 | 9.5 | 1144.957 | 71.9551 | 95.1092 | 131.5828 | 152.9901 | 182.5906 | 3.469%
-76 | 9.5 | 1113.5484 | 64.7871 | 85.165 | 117.224 | 139.8228 | 167.1349 | 2.555%
-75.5 | 9.5 | 1082.2769 | 64.6839 | 85.6462 | 118.8859 | 142.1676 | 171.367 | 2.427%
-75 | 9.5 | 1051.1547 | 69.34 | 92.9574 | 130.9185 | 154.4847 | 187.5597 | 2.774%
-74.5 | 9.5 | 1020.1957 | 72.6596 | 98.2104 | 137.8602 | 163.5274 | 199.8019 | 3.013%
-74 | 9.5 | 989.4153 | 74.0299 | 100.8106 | 142.0099 | 169.8721 | 209.6121 | 2.973%
-73.5 | 9.5 | 958.8308 | 75.1246 | 103.7848 | 148.1863 | 180.2024 | 226.6959 | 2.729%
-73 | 9.5 | 928.4617 | 75.9853 | 106.6592 | 154.7363 | 190.9867 | 244.4918 | 2.509%
-72.5 | 9.5 | 898.33 | 79.3213 | 113.9822 | 167.9559 | 210.3515 | 273.9337 | 2.46%
-72 | 9.5 | 868.4605 | 86.5548 | 127.0267 | 187.6662 | 237.3211 | 311.071 | 2.75%
-71.5 | 9.5 | 838.8812 | 109.6016 | 161.1095 | 244.3051 | 312.7144 | 408.597 | 3.861%
-71 | 9.5 | 809.6242 | 148.9094 | 218.7225 | 337.3379 | 430.5912 | 573.3831 | 6.123%
-70.5 | 9.5 | 780.7258 | 160.8463 | 231.6066 | 346.5673 | 434.7265 | 567.1677 | 8.575%
-70 | 9.5 | 752.2274 | 165.7872 | 240.035 | 360.3539 | 454.6946 | 597.34 | 8.61%
-69.5 | 9.5 | 724.1763 | 158.2632 | 232.7341 | 358.1723 | 459.4366 | 615.3309 | 6.66%
-69 | 9.5 | 696.6267 | 110.2851 | 159.0265 | 237.4901 | 302.7255 | 397.6091 | 4.12%
-68.5 | 9.5 | 669.6407 | 74.5614 | 102.2997 | 145.0147 | 174.804 | 217.6506 | 2.853%
-68 | 9.5 | 643.2891 | 53.2086 | 71.5189 | 97.8836 | 118.4691 | 144.9521 | 1.506%
-67.5 | 9.5 | 617.6535 | 44.8237 | 63.181 | 86.9717 | 105.632 | 132.4028 | 0.9796%
-67 | 9.5 | 592.8266 | 40.2297 | 58.3238 | 80.9378 | 98.7885 | 124.8157 | 0.7665%
-66.5 | 9.5 | 568.9145 | 37.7725 | 55.6784 | 81.8104 | 102.9312 | 134.0621 | 0.6261%
-66 | 9.5 | 546.0376 | 36.6322 | 51.8867 | 72.171 | 86.6259 | 107.3201 | 0.6451%
-65.5 | 9.5 | 524.3313 | 41.3743 | 59.016 | 80.4857 | 97.2024 | 121.296 | 0.8423%
-65 | 9.5 | 503.9471 | 48.7163 | 66.7942 | 90.9615 | 109.7573 | 135.7384 | 1.226%
-64.5 | 9.5 | 485.0518 | 63.7846 | 83.8879 | 115.5314 | 138.1226 | 164.5403 | 2.457%
-64 | 9.5 | 467.8258 | 85.1009 | 115.8408 | 154.4762 | 179.8618 | 215.0173 | 5.628%
-63.5 | 9.5 | 452.46 | 124.1469 | 164.0725 | 222.3494 | 267.4994 | 320.9441 | 12.21%
-63 | 9.5 | 439.1496 | 104.6643 | 139.7105 | 179.3195 | 208.7176 | 249.4151 | 11.84%
-62.5 | 9.5 | 428.0866 | 86.1498 | 113.0413 | 148.8741 | 172.1418 | 204.1217 | 6.88%
-62 | 9.5 | 419.4488 | 89.2277 | 119.2295 | 157.2664 | 183.4304 | 219.7331 | 6.782%
-61.5 | 9.5 | 413.3884 | 84.5684 | 111.9953 | 148.8728 | 172.7646 | 205.732 | 6.037%
-61 | 9.5 | 410.0195 | 85.3143 | 113.3772 | 150.5652 | 174.8862 | 208.4792 | 6.12%
-60.5 | 9.5 | 409.4088 | 83.6192 | 111.3774 | 148.948 | 173.3011 | 207.0005 | 5.573%
-60 | 9.5 | 411.5684 | 65.2102 | 84.6781 | 114.8985 | 136.6714 | 161.8671 | 2.796%
-59.5 | 9.5 | 416.4553 | 38.7971 | 52.2273 | 69.575 | 81.4835 | 98.0809 | 0.7933%
-59 | 9.5 | 423.9751 | 24.2257 | 31.5859 | 42.0844 | 50.11 | 60.7606 | 0.2372%
-90 | 10 | 2012.1356 | 14.0165 | 17.2045 | 21.8584 | 25.2849 | 28.8904 | 0.03749%
-89.5 | 10 | 1979.1037 | 16.6662 | 20.9779 | 26.9817 | 30.3713 | 34.8954 | 0.06858%
-89 | 10 | 1946.0904 | 21.009 | 27.0338 | 33.5704 | 38.2966 | 44.6975 | 0.1419%
-88.5 | 10 | 1913.0967 | 28.0978 | 34.7384 | 44.5091 | 51.7509 | 61.0077 | 0.3278%
-88 | 10 | 1880.124 | 37.8623 | 49.0377 | 64.4442 | 74.3841 | 88.0194 | 0.7786%
-87.5 | 10 | 1847.1733 | 59.1284 | 75.7603 | 101.204 | 120.6942 | 145.3695 | 2.22%
-87 | 10 | 1814.2461 | 104.946 | 146.4411 | 205.5609 | 252.6501 | 317.4601 | 5.502%
-86.5 | 10 | 1781.3438 | 131.4531 | 173.9445 | 241.2766 | 294.4067 | 355.0518 | 11.61%
-86 | 10 | 1748.4679 | 150.4015 | 205.186 | 294.9428 | 354.6425 | 440.1657 | 12.39%
-85.5 | 10 | 1715.6202 | 120.0795 | 155.5514 | 203.9511 | 240.4837 | 291.7786 | 14.74%
-85 | 10 | 1682.8023 | 116.4488 | 150.8385 | 195.5208 | 228.9439 | 275.5173 | 15.42%
-84.5 | 10 | 1650.0162 | 129.3927 | 163.5532 | 213.9694 | 251.9578 | 302.8934 | 20.27%
-84 | 10 | 1617.2641 | 134.6944 | 170.6702 | 225.0413 | 266.2648 | 317.2365 | 21.53%
-83.5 | 10 | 1584.548 | 146.3249 | 193.5178 | 268.2552 | 321.9229 | 391.6707 | 15.65%
-83 | 10 | 1551.8705 | 169.5128 | 239.4397 | 350.1706 | 434.5179 | 559.7415 | 11.23%
-82.5 | 10 | 1519.2341 | 133.4454 | 176.8074 | 245.6154 | 299.1533 | 363.015 | 11.8%
-82 | 10 | 1486.6417 | 94.3883 | 129.0522 | 168.1867 | 197.059 | 237.3183 | 7.573%
-81.5 | 10 | 1454.0964 | 67.7877 | 89.3575 | 123.3947 | 145.4795 | 173.6157 | 2.913%
-81 | 10 | 1421.6016 | 48.7492 | 65.685 | 88.0025 | 105.1376 | 129.5442 | 1.292%
-80.5 | 10 | 1389.1609 | 50.6703 | 68.1084 | 92.0313 | 110.523 | 135.7513 | 1.389%
-80 | 10 | 1356.7784 | 64.3097 | 84.6818 | 116.7912 | 139.3522 | 166.0817 | 2.504%
-79.5 | 10 | 1324.4584 | 75.247 | 100.1086 | 137.4136 | 159.6416 | 190.35 | 3.951%
-79 | 10 | 1292.2058 | 84.5409 | 113.6362 | 151.6477 | 176.4005 | 210.6441 | 5.687%
-78.5 | 10 | 1260.0258 | 89.0214 | 120.2072 | 158.1513 | 184.0552 | 219.9105 | 6.767%
-78 | 10 | 1227.9244 | 87.5822 | 117.8607 | 155.6791 | 181.0389 | 216.1115 | 6.469%
-77.5 | 10 | 1195.9079 | 80.1802 | 106.6787 | 143.9039 | 166.9515 | 198.7445 | 4.951%
-77 | 10 | 1163.9835 | 70.7973 | 93.0471 | 128.0431 | 149.0603 | 176.9729 | 3.436%
-76.5 | 10 | 1132.1592 | 61.8459 | 80.2516 | 108.8007 | 130.9261 | 154.767 | 2.39%
-76 | 10 | 1100.4437 | 58.3911 | 75.6131 | 102.2663 | 122.8833 | 147.3697 | 2.049%
-75.5 | 10 | 1068.8469 | 60.9583 | 79.6095 | 108.7428 | 131.3596 | 155.9873 | 2.215%
-75 | 10 | 1037.3796 | 65.8106 | 86.6549 | 119.5074 | 141.7462 | 168.7329 | 2.694%
-74.5 | 10 | 1006.0543 | 71.2551 | 94.6924 | 131.7651 | 153.4075 | 183.3769 | 3.285%
-74 | 10 | 974.8847 | 75.1521 | 100.7114 | 139.0682 | 162.7211 | 195.6537 | 3.686%
-73.5 | 10 | 943.8864 | 75.5457 | 101.7914 | 141.1668 | 166.4392 | 201.9205 | 3.52%
-73 | 10 | 913.0769 | 74.2265 | 100.6048 | 140.999 | 167.8069 | 205.8312 | 3.117%
-72.5 | 10 | 882.4761 | 72.2153 | 98.7174 | 140.3877 | 169.2138 | 210.6717 | 2.654%
-72 | 10 | 852.1066 | 74.0055 | 103.53 | 150.8614 | 186.9778 | 240.5272 | 2.33%
-71.5 | 10 | 821.9943 | 90.2931 | 129.9484 | 189.5465 | 238.3305 | 311.2859 | 3.15%
-71 | 10 | 792.1685 | 127.4072 | 176.4827 | 256.3946 | 321.5105 | 418.6034 | 6.435%
-70.5 | 10 | 762.663 | 169.6948 | 225.8033 | 310.0334 | 360.593 | 430.5288 | 28.54%
-70 | 10 | 733.5165 | 174.5793 | 228.1653 | 307.8007 | 355.4165 | 420.7625 | 39.23%
-69.5 | 10 | 704.7738 | 191.6295 | 262.6271 | 351.9102 | 411.5282 | 494.4844 | 38.07%
-69 | 10 | 676.4864 | 147.6934 | 194.0827 | 267.0359 | 317.606 | 379.2459 | 18.65%
-68.5 | 10 | 648.7139 | 105.9499 | 144.9557 | 192.8062 | 229.336 | 281.1182 | 8.313%
-68 | 10 | 621.5255 | 79.2328 | 111.0215 | 155.1165 | 185.1693 | 227.9375 | 3.451%
-67.5 | 10 | 595.0014 | 67.6901 | 93.4438 | 134.7328 | 158.954 | 192.9829 | 2.418%
-67 | 10 | 569.2346 | 64.2257 | 90.0584 | 132.9008 | 157.5944 | 192.4808 | 1.998%
-66.5 | 10 | 544.3328 | 58.7601 | 82.1335 | 121.4581 | 147.8373 | 181.9934 | 1.575%
-66 | 10 | 520.4201 | 65.5202 | 91.8766 | 134.8104 | 159.9163 | 195.3992 | 2.104%
-65.5 | 10 | 497.6394 | 70.7471 | 97.7693 | 139.1663 | 163.7492 | 198.1863 | 2.774%
-65 | 10 | 476.1531 | 81.4572 | 114.3117 | 158.2839 | 188.6321 | 231.7412 | 3.78%
-64.5 | 10 | 456.1444 | 98.7044 | 135.9616 | 177.265 | 208.3031 | 251.7203 | 8.142%
-64 | 10 | 437.816 | 136.621 | 172.6386 | 226.9106 | 267.9552 | 315.6866 | 24.3%
-63.5 | 10 | 421.3872 | 182.1875 | 242.5342 | 322.7083 | 367.9861 | 429.2793 | 51.23%
-63 | 10 | 407.0881 | 132.3566 | 161.4933 | 203.7516 | 234.6929 | 277.0416 | 39.35%
-62.5 | 10 | 395.1501 | 94.6962 | 122.5832 | 155.0464 | 176.8169 | 206.2909 | 12.72%
-62 | 10 | 385.7925 | 93.9724 | 122.9895 | 157.4153 | 181.0209 | 213.2711 | 10.48%
-61.5 | 10 | 379.2064 | 97.4808 | 130.126 | 166.1633 | 192.5721 | 228.9595 | 10.4%
-61 | 10 | 375.5377 | 102.3069 | 136.143 | 174.3478 | 202.6533 | 241.7796 | 11.49%
-60.5 | 10 | 374.8719 | 104.9343 | 139.4647 | 179.6213 | 209.5071 | 250.9744 | 11.65%
-60 | 10 | 377.2251 | 88.2627 | 118.3066 | 156.2475 | 182.0047 | 217.6923 | 6.58%
-59.5 | 10 | 382.5415 | 53.0144 | 69.5166 | 92.3122 | 109.6921 | 133.6126 | 1.671%
-59 | 10 | 390.7002 | 29.3695 | 38.1012 | 51.6416 | 61.238 | 72.5549 | 0.385%
-90 | 10.5 | 2004.1558 | 18.5255 | 23.7164 | 29.7993 | 33.7259 | 38.9981 | 0.0957%
-89.5 | 10.5 | 1971.0544 | 23.9215 | 29.8352 | 37.4139 | 42.9363 | 50.4643 | 0.2022%
-89 | 10.5 | 1937.9681 | 31.9089 | 40.1713 | 52.5708 | 61.1393 | 71.2785 | 0.4823%
-88.5 | 10.5 | 1904.8979 | 50.1951 | 67.0363 | 90.7665 | 109.1386 | 135.1579 | 1.338%
-88 | 10.5 | 1871.8446 | 76.6654 | 103.0548 | 143.099 | 170.5812 | 209.6305 | 3.443%
-87.5 | 10.5 | 1838.8093 | 114.9174 | 155.7325 | 214.3462 | 260.3153 | 321.0388 | 8.133%
-87 | 10.5 | 1805.7933 | 141.0729 | 184.5621 | 252.6239 | 303.6326 | 363.0898 | 16.42%
-86.5 | 10.5 | 1772.7977 | 149.4454 | 194.6582 | 265.0789 | 314.2431 | 373.0556 | 21.56%
-86 | 10.5 | 1739.8238 | 133.8086 | 167.883 | 218.8288 | 257.105 | 307.0531 | 24.16%
-85.5 | 10.5 | 1706.873 | 124.2611 | 158.141 | 205.3932 | 240.7941 | 290.1884 | 18.88%
-85 | 10.5 | 1673.9469 | 114.3829 | 148.8253 | 192.8056 | 225.6894 | 271.4946 | 14.61%
-84.5 | 10.5 | 1641.047 | 112.4222 | 148.0553 | 193.8411 | 228.3612 | 276.7835 | 12.11%
-84 | 10.5 | 1608.1751 | 137.7323 | 187.8103 | 269.8123 | 330.7527 | 414.3457 | 9.4%
-83.5 | 10.5 | 1575.3331 | 138.6774 | 190.2244 | 275.1815 | 335.8582 | 418.5801 | 9.457%
-83 | 10.5 | 1542.5231 | 132.5931 | 181.9968 | 263.4794 | 325.5772 | 410.6473 | 8.015%
-82.5 | 10.5 | 1509.7473 | 94.8532 | 129.6489 | 168.5365 | 197.3201 | 237.4226 | 7.793%
-82 | 10.5 | 1477.0081 | 74.0051 | 97.8111 | 134.3531 | 155.8401 | 185.4737 | 3.851%
-81.5 | 10.5 | 1444.3081 | 51.8642 | 68.8417 | 92.1457 | 110.0251 | 134.5387 | 1.526%
-81 | 10.5 | 1411.6501 | 38.9879 | 52.8787 | 71.072 | 83.9488 | 102.0633 | 0.7809%
-80.5 | 10.5 | 1379.0374 | 40.5245 | 55.8042 | 75.0927 | 89.4359 | 109.7967 | 0.8395%
-80 | 10.5 | 1346.4734 | 50.3988 | 68.034 | 92.1896 | 110.9027 | 136.2961 | 1.358%
-79.5 | 10.5 | 1313.9617 | 60.4835 | 78.9836 | 107.8786 | 130.4034 | 154.8371 | 2.171%
-79 | 10.5 | 1281.5066 | 66.8769 | 87.8666 | 120.8694 | 142.725 | 169.4763 | 2.873%
-78.5 | 10.5 | 1249.1125 | 69.2731 | 91.1258 | 125.5312 | 146.8781 | 174.4007 | 3.195%
-78 | 10.5 | 1216.7845 | 66.7927 | 87.3856 | 119.6151 | 141.3245 | 167.4732 | 2.924%
-77.5 | 10.5 | 1184.5281 | 60.8616 | 78.8217 | 106.6209 | 128.1268 | 152.0561 | 2.307%
-77 | 10.5 | 1152.3495 | 53.7962 | 70.8137 | 94.9327 | 113.46 | 137.9157 | 1.68%
-76.5 | 10.5 | 1120.2555 | 50.498 | 67.6705 | 90.8684 | 108.7113 | 133.5195 | 1.404%
-76 | 10.5 | 1088.2537 | 50.7445 | 68.1085 | 91.8086 | 110.0931 | 135.1428 | 1.405%
-75.5 | 10.5 | 1056.3526 | 55.1478 | 72.7317 | 98.6253 | 118.6959 | 143.7341 | 1.724%
-75 | 10.5 | 1024.5618 | 61.8695 | 80.871 | 110.5804 | 133.1176 | 157.9429 | 2.311%
-74.5 | 10.5 | 992.8921 | 68.204 | 89.8619 | 124.0198 | 145.6818 | 173.1736 | 3.014%
-74 | 10.5 | 961.3554 | 72.6487 | 96.2832 | 133.0827 | 154.4093 | 183.8308 | 3.588%
-73.5 | 10.5 | 929.9655 | 74.2071 | 98.6515 | 135.8613 | 157.856 | 188.246 | 3.779%
-73 | 10.5 | 898.7379 | 72.4056 | 96.194 | 133.2916 | 155.0591 | 185.175 | 3.473%
-72.5 | 10.5 | 867.6902 | 68.1387 | 90.1395 | 124.9916 | 147.3017 | 176.3641 | 2.891%
-72 | 10.5 | 836.8426 | 66.0814 | 87.0416 | 120.0893 | 142.8288 | 171.4073 | 2.659%
-71.5 | 10.5 | 806.2182 | 83.119 | 114.3698 | 155.5087 | 183.217 | 222.0875 | 4.558%
-71 | 10.5 | 775.8435 | 121.1341 | 158.9917 | 211.2205 | 251.0547 | 303.9666 | 13.22%
-70.5 | 10.5 | 745.7492 | 150.4874 | 191.1999 | 252.9122 | 298.3061 | 340.6841 | 33.78%
-70 | 10.5 | 715.9708 | 165.0534 | 209.4849 | 276.7568 | 315.9531 | 359.2737 | 56.43%
-69.5 | 10.5 | 686.5494 | 173.6604 | 224.0734 | 299.4677 | 336.497 | 385.826 | 59.16%
-69 | 10.5 | 657.5332 | 150.031 | 189.5941 | 249.2122 | 294.3021 | 335.1368 | 35.85%
-68.5 | 10.5 | 628.9783 | 124.2428 | 159.1816 | 207.431 | 243.6737 | 294.3539 | 17.8%
-68 | 10.5 | 600.9506 | 98.8463 | 137.3291 | 180.2256 | 212.6281 | 258.1519 | 7.598%
-67.5 | 10.5 | 573.5276 | 82.735 | 115.8117 | 157.1521 | 184.6444 | 223.0963 | 4.484%
-67 | 10.5 | 546.8003 | 72.1584 | 100.0554 | 141.5398 | 166.0568 | 200.2925 | 2.971%
-66.5 | 10.5 | 520.876 | 69.7629 | 97.234 | 139.507 | 164.5453 | 199.7128 | 2.592%
-66 | 10.5 | 495.8806 | 78.8669 | 110.5536 | 152.4162 | 179.1308 | 216.5067 | 3.815%
-65.5 | 10.5 | 471.962 | 90.3993 | 127.6482 | 167.6284 | 196.7537 | 237.4444 | 6.107%
-65 | 10.5 | 449.2923 | 97.8752 | 135.7021 | 176.9315 | 207.9145 | 251.2556 | 7.855%
-64.5 | 10.5 | 428.0699 | 120.0551 | 155.1882 | 201.2464 | 235.7105 | 283.7483 | 16.75%
-64 | 10.5 | 408.5206 | 149.9237 | 188.447 | 246.1601 | 289.5942 | 330.3173 | 38.99%
-63.5 | 10.5 | 390.8956 | 188.5587 | 245.2103 | 318.527 | 357.9695 | 410.5222 | 91.61%
-63 | 10.5 | 375.466 | 169.2061 | 211.2997 | 273.9136 | 311.583 | 351.3773 | 83.21%
-62.5 | 10.5 | 362.5124 | 100.3656 | 130.4839 | 160.9115 | 182.6401 | 211.906 | 18.25%
-62 | 10.5 | 352.308 | 91.4906 | 117.8829 | 150.8036 | 172.2482 | 201.3307 | 10.8%
-61.5 | 10.5 | 345.0969 | 98.1419 | 129.8703 | 164.4833 | 189.6087 | 224.0266 | 11.85%
-61 | 10.5 | 341.0689 | 109.2498 | 142.8625 | 182.6522 | 212.0935 | 252.7455 | 14.72%
-60.5 | 10.5 | 340.3371 | 111.5524 | 145.5291 | 186.7584 | 217.3553 | 259.7079 | 15.05%
-60 | 10.5 | 342.9226 | 97.5562 | 131.6999 | 169.2235 | 197.0979 | 235.7142 | 9.435%
-59.5 | 10.5 | 348.7516 | 61.7318 | 79.3477 | 106.3904 | 127.1662 | 150.6648 | 2.506%
-59 | 10.5 | 357.6656 | 33.0987 | 43.5101 | 59.4856 | 69.1047 | 82.3931 | 0.5271%
-90 | 11 | 1996.6926 | 27.828 | 34.3301 | 43.8743 | 50.9341 | 60.1918 | 0.3174%
-89.5 | 11 | 1963.5316 | 36.6609 | 47.1362 | 62.2113 | 71.8624 | 85.1128 | 0.7075%
-89 | 11 | 1930.3825 | 57.4103 | 74.0529 | 99.296 | 118.6901 | 144.0552 | 1.995%
-88.5 | 11 | 1897.2459 | 99.2452 | 139.2154 | 195.9083 | 241.1535 | 305.9291 | 4.721%
-88 | 11 | 1864.1229 | 128.4629 | 169.8566 | 233.97 | 284.2837 | 345.3003 | 11.36%
-87.5 | 11 | 1831.0141 | 166.9794 | 226.2451 | 318.13 | 381.4924 | 472.1116 | 17.73%
-87 | 11 | 1797.9206 | 175.1944 | 235.391 | 325.4624 | 386.7431 | 473.5168 | 23.68%
-86.5 | 11 | 1764.8433 | 137.5395 | 170.8 | 219.9746 | 256.5713 | 304.6817 | 31.44%
-86 | 11 | 1731.7834 | 142.3731 | 179.0671 | 234.0768 | 275.5 | 324.3857 | 29.28%
-85.5 | 11 | 1698.742 | 134.6897 | 171.5297 | 227.515 | 270.1609 | 323.2316 | 19.78%
-85 | 11 | 1665.7204 | 124.4708 | 165.391 | 227.1375 | 275.4794 | 338.5434 | 10.34%
-84.5 | 11 | 1632.7198 | 121.2378 | 169.7571 | 247.501 | 310.3259 | 399.7214 | 5.842%
-84 | 11 | 1599.7419 | 100.0988 | 141.1874 | 200.1739 | 247.5269 | 315.6407 | 4.568%
-83.5 | 11 | 1566.788 | 91.5011 | 129.5492 | 182.4194 | 224.3818 | 286.0851 | 3.923%
-83 | 11 | 1533.86 | 81.6763 | 111.0894 | 152.1847 | 180.0965 | 219.4424 | 4.243%
-82.5 | 11 | 1500.9596 | 69.3089 | 91.1889 | 125.644 | 147.2062 | 175.1926 | 3.171%
-82 | 11 | 1468.089 | 55.2245 | 72.2513 | 97.0759 | 116.1788 | 140.7357 | 1.792%
-81.5 | 11 | 1435.2502 | 41.0492 | 56.1892 | 74.8851 | 88.7379 | 108.294 | 0.8849%
-81 | 11 | 1402.4457 | 32.1302 | 42.3789 | 58.4786 | 68.4707 | 82.3931 | 0.4837%
-80.5 | 11 | 1369.678 | 30.2313 | 39.8493 | 55.0257 | 65.2049 | 78.6135 | 0.4145%
-80 | 11 | 1336.95 | 34.3719 | 46.6653 | 64.8351 | 77.0333 | 94.3037 | 0.5616%
-79.5 | 11 | 1304.2649 | 38.5523 | 52.9169 | 71.7546 | 85.1898 | 104.1958 | 0.7473%
-79 | 11 | 1271.6261 | 41.9278 | 58.0372 | 76.9861 | 91.395 | 111.777 | 0.9309%
-78.5 | 11 | 1239.0374 | 43.5618 | 59.8865 | 79.4244 | 94.3059 | 115.3602 | 1.02%
-78 | 11 | 1206.5029 | 42.4126 | 58.4866 | 77.3385 | 91.6639 | 111.8917 | 0.9646%
-77.5 | 11 | 1174.0274 | 39.565 | 54.0212 | 72.3275 | 85.4228 | 103.8425 | 0.8128%
-77 | 11 | 1141.6161 | 38.161 | 52.031 | 70.5028 | 83.4909 | 101.8135 | 0.7331%
-76.5 | 11 | 1109.2746 | 39.5802 | 54.6234 | 74.1215 | 88.4789 | 108.9102 | 0.7848%
-76 | 11 | 1077.0094 | 41.3812 | 57.5129 | 77.3645 | 92.5103 | 114.1042 | 0.8732%
-75.5 | 11 | 1044.8277 | 45.7365 | 62.8415 | 84.6823 | 101.5282 | 125.6154 | 1.088%
-75 | 11 | 1012.7377 | 53.821 | 71.4908 | 96.9653 | 116.7148 | 141.9026 | 1.611%
-74.5 | 11 | 980.7485 | 62.8956 | 82.3693 | 112.8804 | 135.3714 | 160.8023 | 2.406%
-74 | 11 | 948.8703 | 69.266 | 91.4107 | 126.3988 | 147.9137 | 176.0185 | 3.133%
-73.5 | 11 | 917.1149 | 71.6098 | 94.6932 | 131.1915 | 152.1335 | 181.0073 | 3.457%
-73 | 11 | 885.4957 | 69.7456 | 91.9457 | 126.9805 | 148.2838 | 176.2463 | 3.227%
-72.5 | 11 | 854.0279 | 65.1089 | 85.0634 | 116.2461 | 138.2507 | 163.8992 | 2.711%
-72 | 11 | 822.7291 | 63.1413 | 81.6631 | 110.2891 | 132.083 | 155.6118 | 2.599%
-71.5 | 11 | 791.6194 | 72.5814 | 96.3835 | 133.385 | 154.6478 | 183.9579 | 3.57%
-71 | 11 | 760.7221 | 93.2999 | 129.4924 | 171.0397 | 202.1714 | 245.9999 | 6.391%
-70.5 | 11 | 730.0643 | 136.4847 | 175.3765 | 235.0595 | 280.8982 | 329.4377 | 19.47%
-70 | 11 | 699.6777 | 149.9728 | 191.4252 | 254.5756 | 300.3195 | 344.3901 | 31.2%
-69.5 | 11 | 669.5993 | 176.4684 | 236.0865 | 318.7368 | 365.1174 | 428.2164 | 39.76%
-69 | 11 | 639.8727 | 151.0194 | 194.3494 | 260.9543 | 306.5289 | 352.9824 | 29.29%
-68.5 | 11 | 610.5495 | 133.2148 | 170.1934 | 226.5853 | 269.6673 | 318.9087 | 19.2%
-68 | 11 | 581.6907 | 125.1609 | 168.7797 | 234.8638 | 287.1407 | 339.9014 | 10.25%
-67.5 | 11 | 553.3692 | 87.6021 | 125.2303 | 168.7019 | 200.4413 | 245.3782 | 4.762%
-67 | 11 | 525.6719 | 69.9856 | 97.8201 | 140.6296 | 166.7046 | 203.5293 | 2.54%
-66.5 | 11 | 498.7029 | 68.7202 | 98.3319 | 144.5167 | 174.6936 | 218.2311 | 2.136%
-66 | 11 | 472.5871 | 81.3547 | 116.6541 | 161.5231 | 192.5599 | 236.664 | 3.661%
-65.5 | 11 | 447.474 | 96.7443 | 137.4675 | 183.4799 | 218.7025 | 268.7465 | 6.091%
-65 | 11 | 423.5421 | 100.0092 | 140.9856 | 191.4233 | 230.5581 | 286.7963 | 5.912%
-64.5 | 11 | 401.0031 | 115.5038 | 153.5526 | 203.2201 | 240.9874 | 294.3459 | 11.41%
-64 | 11 | 380.1049 | 142.9138 | 181.4233 | 239.7421 | 284.0348 | 329.4088 | 27.19%
-63.5 | 11 | 361.1325 | 187.765 | 252.2344 | 333.5038 | 382.1986 | 448.477 | 52.82%
-63 | 11 | 344.4045 | 176.0252 | 226.832 | 301.533 | 338.5539 | 387.8299 | 65.26%
-62.5 | 11 | 330.2621 | 100.3623 | 131.8032 | 164.0691 | 187.4434 | 219.1509 | 15.5%
-62 | 11 | 319.0495 | 94.1367 | 123.5048 | 158.1911 | 182.1136 | 214.8361 | 10.32%
-61.5 | 11 | 311.0835 | 99.2808 | 132.2502 | 168.4428 | 195.142 | 231.915 | 11.16%
-61 | 11 | 306.6175 | 112.2878 | 146.5466 | 188.6917 | 220.0506 | 263.5543 | 14.74%
-60.5 | 11 | 305.8048 | 113.4833 | 148.0295 | 191.146 | 223.3003 | 267.9918 | 14.72%
-60 | 11 | 308.6743 | 97.1469 | 131.3484 | 168.8694 | 196.7546 | 235.4007 | 9.245%
-59.5 | 11 | 315.1254 | 68.9775 | 90.3403 | 123.8137 | 145.4736 | 173.1461 | 3.174%
-59 | 11 | 324.9448 | 35.5074 | 47.2412 | 64.0475 | 74.848 | 89.8656 | 0.6282%
-90 | 11.5 | 1989.7517 | 48.1023 | 64.5422 | 87.7243 | 105.7262 | 131.6051 | 1.192%
-89.5 | 11.5 | 1956.5413 | 68.2792 | 90.5029 | 125.7837 | 151.1484 | 186.575 | 2.597%
-89 | 11.5 | 1923.3397 | 103.3103 | 143.3906 | 200.8655 | 246.5706 | 311.2376 | 5.367%
-88.5 | 11.5 | 1890.1477 | 135.055 | 178.7122 | 247.8923 | 301.2877 | 366.1591 | 12.3%
-88 | 11.5 | 1856.9659 | 148.5453 | 193.5629 | 263.7097 | 313.7569 | 375.068 | 20.3%
-87.5 | 11.5 | 1823.7949 | 140.0733 | 174.9426 | 226.818 | 265.6288 | 314.5121 | 30.56%
-87 | 11.5 | 1790.6356 | 138.3428 | 171.0771 | 219.2527 | 254.9669 | 302.439 | 34.5%
-86.5 | 11.5 | 1757.4888 | 137.3267 | 170.3607 | 219.1461 | 255.4186 | 303.4934 | 31.75%
-86 | 11.5 | 1724.3553 | 140.2325 | 178.3263 | 236.1242 | 280.091 | 332.7235 | 23.03%
-85.5 | 11.5 | 1691.2361 | 152.7737 | 210.4036 | 304.506 | 371.8097 | 469.9839 | 11.03%
-85 | 11.5 | 1658.1322 | 116.3966 | 160.7984 | 228.3905 | 282.7289 | 354.2358 | 6.549%
-84.5 | 11.5 | 1625.0447 | 85.4709 | 119.3511 | 169.5194 | 208.2821 | 265.2108 | 3.408%
-84 | 11.5 | 1591.9748 | 64.1826 | 85.5588 | 119.706 | 144.7361 | 178.4467 | 2.188%
-83.5 | 11.5 | 1558.9236 | 58.2997 | 76.8872 | 106.2336 | 129.3191 | 158.5352 | 1.808%
-83 | 11.5 | 1525.8927 | 56.5275 | 73.9963 | 100.3349 | 120.7496 | 146.0607 | 1.839%
-82.5 | 11.5 | 1492.8835 | 53.4484 | 70.5857 | 94.7848 | 113.3981 | 138.112 | 1.637%
-82 | 11.5 | 1459.8976 | 49.8785 | 67.0167 | 89.7631 | 107.2238 | 131.8885 | 1.369%
-81.5 | 11.5 | 1426.9368 | 44.4936 | 61.4757 | 82.446 | 98.5596 | 121.5265 | 1.036%
-81 | 11.5 | 1394.003 | 34.9606 | 47.5947 | 65.8142 | 77.9756 | 95.1408 | 0.5886%
-80.5 | 11.5 | 1361.0984 | 26.6332 | 34.7382 | 47.3809 | 57.2256 | 68.5453 | 0.3022%
-80 | 11.5 | 1328.2252 | 22.9671 | 30.5105 | 40.8283 | 48.7428 | 59.6514 | 0.2142%
-79.5 | 11.5 | 1295.386 | 23.4508 | 31.0635 | 41.7388 | 49.9539 | 60.9579 | 0.2251%
-79 | 11.5 | 1262.5835 | 25.2417 | 32.9083 | 44.5054 | 53.4757 | 64.4967 | 0.2645%
-78.5 | 11.5 | 1229.821 | 26.3462 | 34.1919 | 46.3635 | 55.7976 | 66.7439 | 0.2926%
-78 | 11.5 | 1197.1018 | 26.7243 | 34.7336 | 47.1787 | 56.8379 | 67.8777 | 0.3036%
-77.5 | 11.5 | 1164.4297 | 27.5642 | 36.1771 | 49.7038 | 59.8899 | 72.0217 | 0.3302%
-77 | 11.5 | 1131.8089 | 29.5821 | 39.6188 | 55.7338 | 66.6482 | 81.5034 | 0.394%
-76.5 | 11.5 | 1099.2442 | 30.9667 | 41.7823 | 59.0819 | 70.3586 | 86.3642 | 0.4384%
-76 | 11.5 | 1066.7408 | 31.8811 | 42.9407 | 60.2867 | 71.5251 | 87.4112 | 0.4703%
-75.5 | 11.5 | 1034.3046 | 34.7742 | 47.1155 | 65.1208 | 77.1304 | 94.0757 | 0.5808%
-75 | 11.5 | 1001.9424 | 42.0077 | 58.3033 | 77.7896 | 92.702 | 113.8843 | 0.9197%
-74.5 | 11.5 | 969.6617 | 54.3508 | 72.0644 | 97.8605 | 117.8782 | 143.0737 | 1.648%
-74 | 11.5 | 937.471 | 64.7032 | 85.1575 | 117.3789 | 139.8327 | 166.5453 | 2.559%
-73.5 | 11.5 | 905.3801 | 68.625 | 90.6182 | 125.3894 | 147.1049 | 175.1821 | 3.029%
-73 | 11.5 | 873.4002 | 67.4659 | 88.826 | 122.4878 | 144.3383 | 171.6421 | 2.917%
-72.5 | 11.5 | 841.544 | 64.5185 | 84.4514 | 115.6645 | 137.9098 | 163.8775 | 2.602%
-72 | 11.5 | 809.8262 | 62.5284 | 80.8538 | 109.1699 | 131.0426 | 154.4661 | 2.52%
-71.5 | 11.5 | 778.264 | 67.2105 | 87.356 | 118.6597 | 139.5594 | 163.4794 | 3.169%
-71 | 11.5 | 746.8772 | 76.4351 | 101.3646 | 138.2987 | 160.3856 | 190.8401 | 4.251%
-70.5 | 11.5 | 715.6891 | 95.3551 | 131.2402 | 169.3611 | 197.7758 | 237.2535 | 8.158%
-70 | 11.5 | 684.7268 | 115.9611 | 152.0935 | 198.0675 | 232.5837 | 280.8291 | 14.01%
-69.5 | 11.5 | 654.0226 | 132.4089 | 170.2783 | 228.4442 | 273.1514 | 323.7538 | 17.22%
-69 | 11.5 | 623.6149 | 121.4425 | 158.1153 | 208.0947 | 245.9322 | 297.9753 | 14.59%
-68.5 | 11.5 | 593.5492 | 112.0952 | 150.4289 | 198.403 | 234.7838 | 286.0661 | 10.7%
-68 | 11.5 | 563.8805 | 102.0318 | 143.9046 | 195.1716 | 234.9154 | 291.987 | 6.22%
-67.5 | 11.5 | 534.6749 | 75.1594 | 104.9247 | 147.2644 | 173.7196 | 210.8829 | 3.218%
-67 | 11.5 | 506.0129 | 53.9714 | 73.473 | 102.4554 | 125.4204 | 151.4349 | 1.49%
-66.5 | 11.5 | 477.9922 | 50.9447 | 70.646 | 98.7995 | 121.1586 | 148.3315 | 1.277%
-66 | 11.5 | 450.7327 | 63.6932 | 87.3625 | 126.3704 | 149.968 | 181.1382 | 2.104%
-65.5 | 11.5 | 424.3813 | 70.6409 | 97.2953 | 138.2342 | 162.1337 | 195.4968 | 2.825%
-65 | 11.5 | 399.1178 | 73.3894 | 101.4935 | 143.523 | 170.1331 | 207.7134 | 2.961%
-64.5 | 11.5 | 375.1623 | 74.4477 | 98.6204 | 135.1963 | 155.6649 | 183.6677 | 4.081%
-64 | 11.5 | 352.7814 | 94.6 | 129.852 | 166.3075 | 192.9565 | 229.7202 | 8.711%
-63.5 | 11.5 | 332.2937 | 126.2246 | 163.4869 | 217.643 | 259.0149 | 310.9437 | 15.32%
-63 | 11.5 | 314.0698 | 128.78 | 163.9552 | 215.6932 | 254.8494 | 305.1844 | 18.9%
-62.5 | 11.5 | 298.5247 | 84.9221 | 111.3545 | 146.4554 | 168.3386 | 198.2205 | 6.961%
-62 | 11.5 | 286.0956 | 80.2396 | 105.051 | 140.8309 | 163.1707 | 193.9428 | 5.263%
-61.5 | 11.5 | 277.2018 | 87.563 | 116.5646 | 153.8749 | 178.8446 | 213.3574 | 6.651%
-61 | 11.5 | 272.1903 | 97.6419 | 131.7982 | 169.3605 | 197.2652 | 235.925 | 9.454%
-60.5 | 11.5 | 271.2763 | 98.7857 | 133.1813 | 171.3878 | 199.8036 | 239.2099 | 9.646%
-60 | 11.5 | 274.5007 | 87.9577 | 117.7651 | 155.4697 | 180.8861 | 216.0564 | 6.6%
-59.5 | 11.5 | 281.7215 | 66.1449 | 86.4142 | 118.0879 | 140.0715 | 166.5288 | 2.824%
-59 | 11.5 | 292.6429 | 35.7564 | 47.7882 | 64.8757 | 75.9973 | 91.5017 | 0.6366%
-90 | 12 | 1983.3387 | 82.5407 | 111.5672 | 154.1508 | 184.9108 | 228.9178 | 3.97%
-89.5 | 12 | 1950.0892 | 98.1233 | 133.2067 | 177.9264 | 212.1798 | 260.871 | 6.806%
-89 | 12 | 1916.8459 | 125.2827 | 164.9677 | 224.6157 | 270.9994 | 330.4379 | 11.6%
-88.5 | 12 | 1883.6094 | 137.8158 | 176.5115 | 235.6828 | 280.9923 | 336.4192 | 19.41%
-88 | 12 | 1850.3801 | 138.7608 | 174.6619 | 228.5293 | 269.1219 | 320.6569 | 25.67%
-87.5 | 12 | 1817.1587 | 135.0895 | 166.4701 | 212.4772 | 246.4736 | 293.3629 | 33.6%
-87 | 12 | 1783.9457 | 145.6759 | 186.2179 | 248.0819 | 295.3635 | 354.294 | 22.79%
-86.5 | 12 | 1750.7417 | 149.3019 | 195.8927 | 269.0391 | 321.9976 | 391.8242 | 17.72%
-86 | 12 | 1717.5474 | 151.088 | 206.4762 | 297.154 | 361.6714 | 455.4522 | 11.42%
-85.5 | 12 | 1684.3637 | 114.5409 | 156.89 | 219.9039 | 270.0365 | 337.6445 | 6.916%
-85 | 12 | 1651.1912 | 82.9485 | 113.9944 | 160.1498 | 194.6879 | 244.826 | 3.517%
-84.5 | 12 | 1618.0309 | 58.378 | 77.0796 | 106.6435 | 129.9248 | 160.3424 | 1.787%
-84 | 12 | 1584.8836 | 42.9063 | 58.7046 | 77.6721 | 92.092 | 112.4611 | 0.9908%
-83.5 | 12 | 1551.7504 | 39.8667 | 54.5071 | 72.8333 | 86.0216 | 104.5726 | 0.8295%
-83 | 12 | 1518.6323 | 44.4083 | 61.6912 | 83.3205 | 100.033 | 123.9656 | 1.01%
-82.5 | 12 | 1485.5305 | 57.1228 | 76.3445 | 106.4237 | 130.2513 | 155.2519 | 1.733%
-82 | 12 | 1452.4462 | 65.4229 | 87.9011 | 124.1188 | 146.1651 | 173.751 | 2.5%
-81.5 | 12 | 1419.3809 | 64.7431 | 87.5089 | 124.4304 | 146.9908 | 175.5868 | 2.353%
-81 | 12 | 1386.3361 | 49.4847 | 68.8556 | 95.357 | 116.2425 | 142.2213 | 1.228%
-80.5 | 12 | 1353.3134 | 30.9375 | 43.161 | 62.3114 | 74.5995 | 92.1421 | 0.4421%
-80 | 12 | 1320.3146 | 18.5045 | 25.807 | 34.161 | 40.5143 | 49.4916 | 0.1362%
-79.5 | 12 | 1287.3418 | 15.3738 | 20.477 | 27.8451 | 32.3424 | 38.5542 | 0.0797%
-79 | 12 | 1254.3971 | 15.2013 | 20.2183 | 27.5926 | 32.1317 | 38.4186 | 0.07829%
-78.5 | 12 | 1221.4829 | 15.951 | 21.5007 | 29.2532 | 34.3314 | 41.4251 | 0.09172%
-78 | 12 | 1188.602 | 17.9194 | 24.9196 | 33.742 | 40.3725 | 49.8322 | 0.1308%
-77.5 | 12 | 1155.7574 | 21.1062 | 29.3418 | 40.7149 | 49.6919 | 62.0236 | 0.1944%
-77 | 12 | 1122.9523 | 24.5206 | 33.4885 | 47.4359 | 58.541 | 71.9083 | 0.265%
-76.5 | 12 | 1090.1906 | 25.4704 | 34.3288 | 48.4453 | 59.4403 | 72.6476 | 0.2834%
-76 | 12 | 1057.4763 | 25.7649 | 34.2252 | 47.6664 | 58.2737 | 70.416 | 0.2859%
-75.5 | 12 | 1024.8142 | 27.787 | 36.7883 | 51.0599 | 61.3765 | 73.6458 | 0.3399%
-75 | 12 | 992.2096 | 34.0008 | 46.0765 | 63.87 | 75.3796 | 91.5561 | 0.5535%
-74.5 | 12 | 959.6685 | 44.8848 | 61.9405 | 83.2319 | 99.6174 | 123.0022 | 1.051%
-74 | 12 | 927.1977 | 57.576 | 75.4569 | 103.1238 | 124.7014 | 149.9286 | 1.884%
-73.5 | 12 | 894.8051 | 63.6428 | 83.7649 | 115.4642 | 138.1162 | 164.6046 | 2.432%
-73 | 12 | 862.4996 | 63.5238 | 83.4589 | 114.8025 | 137.3748 | 163.5302 | 2.44%
-72.5 | 12 | 830.2915 | 61.9335 | 81.0004 | 110.8303 | 133.4238 | 158.763 | 2.301%
-72 | 12 | 798.1927 | 61.9318 | 80.2379 | 108.584 | 130.5207 | 154.3338 | 2.419%
-71.5 | 12 | 766.2173 | 67.5813 | 88.1965 | 120.373 | 141.2324 | 165.651 | 3.166%
-71 | 12 | 734.3813 | 75.2799 | 99.7159 | 136.3128 | 157.2216 | 185.8805 | 4.198%
-70.5 | 12 | 702.7039 | 87.5463 | 119.3253 | 157.5798 | 183.3307 | 218.9615 | 6.282%
-70 | 12 | 671.2077 | 94.8662 | 131.1853 | 168.9031 | 196.9667 | 235.8972 | 8.116%
-69.5 | 12 | 639.9197 | 96.9317 | 134.8321 | 176.8712 | 208.6149 | 253.2003 | 7.254%
-69 | 12 | 608.872 | 86.0859 | 118.9563 | 159.021 | 186.284 | 224.2914 | 5.379%
-68.5 | 12 | 578.1035 | 78.7079 | 108.2162 | 148.3735 | 173.3614 | 208.0986 | 4.087%
-68 | 12 | 547.6614 | 71.321 | 99.1155 | 141.1489 | 166.4915 | 202.0885 | 2.776%
-67.5 | 12 | 517.6036 | 56.9594 | 77.5946 | 110.4835 | 135.3138 | 162.4496 | 1.623%
-67 | 12 | 488.001 | 38.3204 | 54.0575 | 73.5855 | 87.657 | 107.6359 | 0.7328%
-66.5 | 12 | 458.942 | 35.3488 | 48.9153 | 67.1206 | 78.7956 | 95.1097 | 0.6194%
-66 | 12 | 430.5367 | 41.3909 | 60.0123 | 82.8747 | 100.8521 | 126.9789 | 0.8208%
-65.5 | 12 | 402.9237 | 44.0767 | 63.1845 | 87.7345 | 107.1223 | 134.2836 | 0.9297%
-65 | 12 | 376.2774 | 42.4785 | 60.1881 | 82.0839 | 99.1324 | 123.7041 | 0.8915%
-64.5 | 12 | 350.8184 | 42.0022 | 57.828 | 73.8484 | 85.5924 | 101.7753 | 1.05%
-64 | 12 | 326.8244 | 51.2964 | 67.2846 | 87.444 | 102.5547 | 123.6471 | 1.684%
-63.5 | 12 | 304.6418 | 61.8594 | 79.9511 | 107.8916 | 129.4665 | 152.072 | 2.475%
-63 | 12 | 284.6944 | 62.8287 | 81.1467 | 109.4149 | 131.1751 | 152.9741 | 2.62%
-62.5 | 12 | 267.483 | 57.3749 | 73.5491 | 97.7938 | 116.2975 | 139.8748 | 2.101%
-62 | 12 | 253.5652 | 57.2684 | 73.4425 | 97.6504 | 116.1257 | 140.0372 | 2.081%
-61.5 | 12 | 243.5067 | 67.0714 | 87.385 | 119.0327 | 140.7831 | 167.2358 | 2.987%
-61 | 12 | 237.7977 | 76.0791 | 100.2664 | 136.5898 | 158.4439 | 188.5861 | 4.258%
-60.5 | 12 | 236.753 | 80.818 | 107.3323 | 144.5902 | 168.0609 | 200.5034 | 5.034%
-60 | 12 | 240.4335 | 76.5246 | 101.2297 | 138.0034 | 160.2979 | 191.0922 | 4.253%
-59.5 | 12 | 248.6294 | 63.8374 | 83.5878 | 114.5266 | 136.9679 | 163.1551 | 2.502%
-59 | 12 | 260.9155 | 37.5385 | 51.0535 | 69.4049 | 82.1658 | 100.1618 | 0.7035%
-90 | 12.5 | 1977.4588 | 121.1671 | 163.12 | 226.6343 | 276.8167 | 342.6661 | 8.656%
-89.5 | 12.5 | 1944.1808 | 126.8657 | 166.4123 | 226.4615 | 273.1375 | 333.1171 | 12.09%
-89 | 12.5 | 1910.9068 | 121.2972 | 153.2365 | 195.717 | 227.124 | 270.461 | 22.31%
-88.5 | 12.5 | 1877.637 | 129.765 | 160.2236 | 204.1715 | 236.6045 | 281.289 | 30.35%
-88 | 12.5 | 1844.3718 | 137.1741 | 171.6031 | 222.9153 | 261.363 | 311.7412 | 27.2%
-87.5 | 12.5 | 1811.1118 | 144.9112 | 185.1071 | 246.3947 | 293.2101 | 348.1811 | 23.58%
-87 | 12.5 | 1777.8574 | 172.326 | 238.47 | 342.2469 | 420.3045 | 534.8837 | 13.86%
-86.5 | 12.5 | 1744.609 | 147.291 | 201.4111 | 290.3055 | 354.5753 | 447.3733 | 10.57%
-86 | 12.5 | 1711.3672 | 112.7381 | 155.5153 | 219.9958 | 271.6686 | 345.3213 | 6.082%
-85.5 | 12.5 | 1678.1326 | 79.8155 | 108.044 | 150.9193 | 182.3171 | 227.5846 | 3.442%
-85 | 12.5 | 1644.9057 | 56.0351 | 73.4406 | 99.5592 | 119.7999 | 146.6082 | 1.769%
-84.5 | 12.5 | 1611.6871 | 39.4748 | 53.195 | 70.8512 | 83.2641 | 100.6294 | 0.8215%
-84 | 12.5 | 1578.4776 | 32.7604 | 43.3669 | 59.6874 | 69.4615 | 82.99 | 0.5128%
-83.5 | 12.5 | 1545.278 | 31.9085 | 42.9203 | 60.0976 | 70.7213 | 85.6055 | 0.4758%
-83 | 12.5 | 1512.0889 | 39.7745 | 57.519 | 80.5406 | 98.6964 | 125.2841 | 0.738%
-82.5 | 12.5 | 1478.9114 | 64.2021 | 90.9078 | 134.8884 | 160.8358 | 197.715 | 1.928%
-82 | 12.5 | 1445.7464 | 78.2342 | 110.57 | 153.1633 | 180.4019 | 218.6016 | 3.617%
-81.5 | 12.5 | 1412.5948 | 84.1696 | 123.8271 | 171.8984 | 207.6141 | 259.0941 | 3.568%
-81 | 12.5 | 1379.4579 | 61.67 | 84.8592 | 123.21 | 147.2233 | 177.6052 | 1.92%
-80.5 | 12.5 | 1346.3369 | 34.1761 | 50.2831 | 73.0272 | 89.5943 | 113.8867 | 0.5381%
-80 | 12.5 | 1313.2332 | 16.9607 | 24.0451 | 32.9166 | 39.3737 | 48.5831 | 0.1213%
-79.5 | 12.5 | 1280.1482 | 11.9981 | 15.6431 | 21.3263 | 25.7501 | 30.2728 | 0.04367%
-79 | 12.5 | 1247.0836 | 10.4254 | 13.7161 | 18.2309 | 21.6756 | 26.37 | 0.02971%
-78.5 | 12.5 | 1214.0412 | 10.9752 | 14.5138 | 19.8233 | 23.9621 | 29.105 | 0.03858%
-78 | 12.5 | 1181.0231 | 13.2113 | 18.2919 | 26.5942 | 32.2759 | 40.5088 | 0.07687%
-77.5 | 12.5 | 1148.0315 | 16.8834 | 24.8084 | 35.8112 | 44.5558 | 57.5762 | 0.1407%
-77 | 12.5 | 1115.069 | 20.5775 | 30.0025 | 43.743 | 55.0182 | 68.3893 | 0.2037%
-76.5 | 12.5 | 1082.1382 | 22.7255 | 32.5627 | 47.6964 | 59.6526 | 73.2059 | 0.242%
-76 | 12.5 | 1049.2425 | 25.8036 | 37.4643 | 57.9161 | 71.5049 | 91.481 | 0.3132%
-75.5 | 12.5 | 1016.3853 | 28.7811 | 42.468 | 65.4868 | 82.7776 | 108.9724 | 0.3794%
-75 | 12.5 | 983.5708 | 32.5581 | 46.9803 | 69.051 | 85.0308 | 108.5572 | 0.4824%
-74.5 | 12.5 | 950.8033 | 40.6555 | 59.3054 | 83.5729 | 102.9615 | 131.4036 | 0.7612%
-74 | 12.5 | 918.0882 | 47.6256 | 65.7325 | 89.4262 | 107.8391 | 133.5177 | 1.165%
-73.5 | 12.5 | 885.4314 | 53.8313 | 71.9911 | 98.303 | 118.81 | 143.985 | 1.581%
-73 | 12.5 | 852.8397 | 54.6903 | 72.6204 | 98.9078 | 119.3543 | 144.3419 | 1.664%
-72.5 | 12.5 | 820.3211 | 53.8882 | 71.4193 | 96.537 | 115.9572 | 140.8092 | 1.638%
-72 | 12.5 | 787.8849 | 57.9465 | 74.5686 | 99.9789 | 119.5001 | 143.2701 | 2.09%
-71.5 | 12.5 | 755.5416 | 66.7374 | 87.2942 | 119.4593 | 140.5922 | 165.0377 | 3.004%
-71 | 12.5 | 723.3041 | 84.1041 | 117.0261 | 160.2576 | 190.5603 | 233.5005 | 4.288%
-70.5 | 12.5 | 691.1871 | 93.051 | 130.3647 | 170.6831 | 200.8803 | 243.1931 | 6.614%
-70 | 12.5 | 659.2086 | 95.9113 | 134.2461 | 175.922 | 207.3662 | 251.5007 | 7.035%
-69.5 | 12.5 | 627.3898 | 87.0951 | 125.3335 | 172.5346 | 207.9907 | 258.9916 | 4.064%
-69 | 12.5 | 595.7565 | 64.4288 | 86.7759 | 122.8781 | 146.2377 | 175.9545 | 2.293%
-68.5 | 12.5 | 564.34 | 52.2026 | 71.1721 | 98.3344 | 119.7013 | 145.7514 | 1.406%
-68 | 12.5 | 533.1788 | 45.1804 | 64.6789 | 91.6236 | 113.2398 | 142.4039 | 0.941%
-67.5 | 12.5 | 502.3206 | 34.5412 | 48.0054 | 66.6911 | 78.7552 | 95.722 | 0.5785%
-67 | 12.5 | 471.8249 | 28.2619 | 37.8683 | 53.3003 | 63.3771 | 75.4125 | 0.3592%
-66.5 | 12.5 | 441.767 | 26.2683 | 35.0921 | 49.2206 | 59.8148 | 71.2291 | 0.3017%
-66 | 12.5 | 412.2429 | 25.9879 | 34.8706 | 49.1621 | 59.9052 | 71.5728 | 0.2959%
-65.5 | 12.5 | 383.376 | 24.8633 | 33.3144 | 46.2261 | 56.4173 | 67.4458 | 0.2664%
-65 | 12.5 | 355.3267 | 23.7919 | 31.4579 | 42.1382 | 50.3371 | 60.8666 | 0.232%
-64.5 | 12.5 | 328.3047 | 25.5203 | 32.5062 | 42.9077 | 50.8007 | 60.6777 | 0.2617%
-64 | 12.5 | 302.5855 | 28.2842 | 36.3266 | 48.6621 | 58.132 | 66.8877 | 0.349%
-63.5 | 12.5 | 278.5304 | 30.9714 | 40.3756 | 55.0365 | 63.624 | 73.8603 | 0.4513%
-63 | 12.5 | 256.608 | 32.5257 | 42.7316 | 58.5885 | 67.1463 | 78.7951 | 0.513%
-62.5 | 12.5 | 237.4098 | 33.2982 | 43.7818 | 59.7225 | 69.0075 | 81.7591 | 0.5402%
-62 | 12.5 | 221.645 | 36.2658 | 48.3475 | 65.3577 | 76.5315 | 92.102 | 0.6612%
-61.5 | 12.5 | 210.088 | 43.1311 | 58.8718 | 77.5955 | 91.787 | 111.7826 | 1.015%
-61 | 12.5 | 203.4572 | 54.2759 | 71.2584 | 95.5978 | 114.305 | 138.9085 | 1.715%
-60.5 | 12.5 | 202.2378 | 64.3712 | 84.1886 | 115.1927 | 137.52 | 163.7797 | 2.578%
-60 | 12.5 | 206.5255 | 67.0636 | 88.1755 | 121.3965 | 143.5459 | 171.21 | 2.85%
-59.5 | 12.5 | 215.9928 | 62.3255 | 82.0162 | 113.0297 | 135.9509 | 162.4927 | 2.273%
-59 | 12.5 | 230.0007 | 38.7081 | 53.3144 | 72.5802 | 86.5132 | 106.309 | 0.7458%
-90 | 13 | 1972.1168 | 119.8728 | 152.4898 | 195.6595 | 227.6923 | 272.0277 | 19.88%
-89.5 | 13 | 1938.8211 | 119.7291 | 151.9142 | 194.3632 | 225.7899 | 269.2039 | 20.72%
-89 | 13 | 1905.5274 | 127.7582 | 160.2481 | 206.9126 | 241.7114 | 290.0769 | 22.92%
-88.5 | 13 | 1872.2358 | 147.1232 | 193.6538 | 266.9619 | 323.1742 | 402.2856 | 14.74%
-88 | 13 | 1838.9467 | 153.7301 | 206.0783 | 290.2137 | 350.3178 | 435.9617 | 14.38%
-87.5 | 13 | 1805.6603 | 155.7415 | 213.9544 | 308.6429 | 378.6663 | 481.3427 | 11.3%
-87 | 13 | 1772.3771 | 131.9003 | 178.0857 | 252.8994 | 311.1353 | 389.3128 | 9.024%
-86.5 | 13 | 1739.0974 | 101.0423 | 139.202 | 193.1131 | 235.6579 | 297.4558 | 5.429%
-86 | 13 | 1705.8216 | 79.5841 | 108.6466 | 153.6819 | 187.7109 | 237.3658 | 3.117%
-85.5 | 13 | 1672.5499 | 57.7913 | 75.2578 | 102.2521 | 123.2084 | 150.441 | 1.901%
-85 | 13 | 1639.283 | 43.6428 | 60.1045 | 80.84 | 96.8094 | 119.6145 | 0.9829%
-84.5 | 13 | 1606.0212 | 35.5373 | 49.3215 | 69.852 | 84.9499 | 106.8766 | 0.5822%
-84 | 13 | 1572.7651 | 29.7348 | 40.7386 | 58.7418 | 70.9934 | 88.6654 | 0.399%
-83.5 | 13 | 1539.5152 | 26.4653 | 34.6806 | 47.5608 | 57.6336 | 68.354 | 0.2999%
-83 | 13 | 1506.272 | 30.9903 | 43.1641 | 62.4954 | 75.6154 | 94.5634 | 0.4386%
-82.5 | 13 | 1473.0362 | 47.074 | 67.9024 | 96.8912 | 120.2804 | 148.465 | 1.024%
-82 | 13 | 1439.8085 | 62.0874 | 84.3184 | 120.56 | 143.8359 | 171.736 | 2.064%
-81.5 | 13 | 1406.5896 | 66.0391 | 92.0858 | 134.4066 | 159.035 | 193.7469 | 2.19%
-81 | 13 | 1373.3803 | 50.6837 | 71.55 | 101.4245 | 125.4037 | 151.9175 | 1.231%
-80.5 | 13 | 1340.1815 | 30.2496 | 44.0051 | 65.542 | 80.0768 | 101.2923 | 0.423%
-80 | 13 | 1306.9942 | 14.8821 | 21.0316 | 29.7662 | 35.4942 | 43.636 | 0.09486%
-79.5 | 13 | 1273.8195 | 9.2944 | 12.8405 | 17.401 | 20.9342 | 25.9473 | 0.02976%
-79 | 13 | 1240.6585 | 7.251 | 9.8939 | 13.3699 | 15.6558 | 18.8412 | 0.01395%
-78.5 | 13 | 1207.5124 | 7.2693 | 10.0035 | 13.819 | 16.5336 | 20.4063 | 0.01769%
-78 | 13 | 1174.3829 | 8.8238 | 12.7166 | 18.4563 | 23.1495 | 29.4454 | 0.04013%
-77.5 | 13 | 1141.2713 | 12.1276 | 17.8104 | 27.4659 | 34.1586 | 44.1191 | 0.08321%
-77 | 13 | 1108.1796 | 15.1534 | 22.9102 | 34.0337 | 42.5547 | 55.3111 | 0.1242%
-76.5 | 13 | 1075.1097 | 19.5613 | 30.3696 | 47.2986 | 61.0338 | 77.8504 | 0.2073%
-76 | 13 | 1042.0639 | 26.1146 | 39.7155 | 62.937 | 78.2132 | 100.9296 | 0.3305%
-75.5 | 13 | 1009.0447 | 33.2607 | 54.5529 | 85.2355 | 110.7092 | 144.5203 | 0.5003%
-75 | 13 | 976.055 | 33.4139 | 52.01 | 78.3723 | 98.79 | 129.6279 | 0.5061%
-74.5 | 13 | 943.0979 | 32.472 | 47.3999 | 69.5201 | 85.0958 | 107.8771 | 0.4859%
-74 | 13 | 910.1773 | 35.6683 | 51.5949 | 73.705 | 89.9813 | 113.7192 | 0.5895%
-73.5 | 13 | 877.2974 | 39.5616 | 57.5021 | 79.6202 | 96.8779 | 121.9549 | 0.7465%
-73 | 13 | 844.4632 | 40.295 | 57.805 | 79.0773 | 95.5923 | 119.42 | 0.7924%
-72.5 | 13 | 811.6802 | 40.3191 | 56.3676 | 75.2036 | 89.1356 | 108.8084 | 0.8469%
-72 | 13 | 778.9552 | 48.4486 | 66.2038 | 89.1977 | 106.9306 | 131.985 | 1.248%
-71.5 | 13 | 746.296 | 62.5325 | 81.7432 | 111.7819 | 134.0212 | 157.2823 | 2.439%
-71 | 13 | 713.7117 | 80.6386 | 111.3832 | 152.8586 | 180.2001 | 218.5808 | 4.091%
-70.5 | 13 | 681.2133 | 93.1058 | 131.2146 | 171.3308 | 201.5122 | 243.7729 | 6.634%
-70 | 13 | 648.8138 | 93.2892 | 131.8889 | 172.1645 | 202.4591 | 244.8708 | 6.635%
-69.5 | 13 | 616.529 | 76.2919 | 107.6239 | 151.6666 | 180.5385 | 221.4992 | 3.125%
-69 | 13 | 584.378 | 52.3654 | 72.4644 | 102.0676 | 125.7101 | 152.4854 | 1.344%
-68.5 | 13 | 552.3845 | 35.1991 | 48.5169 | 66.7065 | 78.405 | 94.7736 | 0.6105%
-68 | 13 | 520.5775 | 30.6462 | 42.0446 | 60.0775 | 70.6808 | 85.5325 | 0.4369%
-67.5 | 13 | 488.9936 | 25.7434 | 34.6555 | 49.0053 | 59.8393 | 71.5596 | 0.2908%
-67 | 13 | 457.6793 | 19.9251 | 28.2773 | 38.9028 | 47.2331 | 59.0018 | 0.1753%
-66.5 | 13 | 426.6939 | 16.9035 | 24.2168 | 33.3402 | 40.061 | 49.6942 | 0.1242%
-66 | 13 | 396.1149 | 15.572 | 22.0336 | 30.9879 | 37.1906 | 46.0696 | 0.1048%
-65.5 | 13 | 366.0443 | 14.4835 | 19.9793 | 28.2104 | 33.4372 | 40.8178 | 0.08402%
-65 | 13 | 336.6186 | 13.9649 | 18.6748 | 26.0962 | 30.1571 | 35.7349 | 0.0666%
-64.5 | 13 | 308.0227 | 14.5521 | 19.2935 | 26.4661 | 30.1856 | 35.222 | 0.06677%
-64 | 13 | 280.5106 | 15.917 | 21.2882 | 28.4049 | 32.5038 | 38.0738 | 0.08159%
-63.5 | 13 | 254.4345 | 17.5354 | 23.7003 | 30.7906 | 35.4799 | 41.9007 | 0.104%
-63 | 13 | 230.2827 | 19.2164 | 26.0679 | 33.2887 | 38.6266 | 45.9912 | 0.1315%
-62.5 | 13 | 208.7244 | 21.7301 | 28.7504 | 37.4667 | 44.0142 | 53.1703 | 0.1801%
-62 | 13 | 190.6416 | 26.7488 | 34.7126 | 47.0665 | 56.6415 | 67.9799 | 0.3034%
-61.5 | 13 | 177.1022 | 33.4479 | 44.9066 | 62.3043 | 73.7447 | 89.8749 | 0.5281%
-61 | 13 | 169.2006 | 42.7854 | 58.8927 | 78.3073 | 93.1248 | 114.1245 | 0.9697%
-60.5 | 13 | 167.7354 | 54.3353 | 71.9469 | 97.5594 | 117.4118 | 142.7885 | 1.651%
-60 | 13 | 172.8703 | 59.705 | 77.8885 | 106.2581 | 128.3528 | 153.4238 | 2.093%
-59.5 | 13 | 184.0538 | 58.0589 | 76.0876 | 104.3017 | 126.3588 | 151.9676 | 1.9%
-59 | 13 | 200.275 | 36.9014 | 50.5133 | 69.31 | 82.4272 | 101.0178 | 0.6665%
-90 | 13.5 | 1967.3171 | 141.107 | 181.9624 | 244.9028 | 293.4021 | 354.2246 | 18.33%
-89.5 | 13.5 | 1934.0147 | 143.8179 | 190.1106 | 263.3838 | 318.4731 | 392.6829 | 14.02%
-89 | 13.5 | 1900.7125 | 141.5018 | 187.5756 | 260.7265 | 316.6849 | 393.373 | 12.71%
-88.5 | 13.5 | 1867.4108 | 136.4355 | 180.9645 | 251.7077 | 306.5242 | 379.8105 | 11.62%
-88 | 13.5 | 1834.1098 | 124.2797 | 165.8712 | 229.6898 | 279.9807 | 347.0197 | 9.462%
-87.5 | 13.5 | 1800.8096 | 111.5904 | 152.4097 | 213.3139 | 261.7129 | 329.6855 | 6.512%
-87 | 13.5 | 1767.5105 | 91.4242 | 125.3814 | 174.5593 | 212.807 | 268.5023 | 4.381%
-86.5 | 13.5 | 1734.2128 | 72.1867 | 96.7702 | 135.8446 | 164.4621 | 205.8189 | 2.724%
-86 | 13.5 | 1700.9166 | 56.0883 | 73.8034 | 100.6033 | 121.4623 | 149.7315 | 1.718%
-85.5 | 13.5 | 1667.6223 | 47.3629 | 64.9527 | 88.6301 | 107.0736 | 133.0921 | 1.139%
-85 | 13.5 | 1634.3302 | 41.7797 | 59.5295 | 81.612 | 98.8769 | 123.8474 | 0.8499%
-84.5 | 13.5 | 1601.0405 | 38.396 | 57.1074 | 81.7494 | 101.4201 | 130.6171 | 0.6683%
-84 | 13.5 | 1567.7537 | 31.5991 | 45.715 | 67.362 | 82.4619 | 104.5496 | 0.4585%
-83.5 | 13.5 | 1534.47 | 26.1263 | 35.902 | 52.0456 | 63.7503 | 78.8085 | 0.3059%
-83 | 13.5 | 1501.1899 | 25.2357 | 33.5389 | 46.3534 | 56.4362 | 67.3351 | 0.2728%
-82.5 | 13.5 | 1467.9138 | 32.0053 | 45.0641 | 64.8458 | 77.871 | 96.5281 | 0.4759%
-82 | 13.5 | 1434.6421 | 41.828 | 61.2153 | 84.93 | 103.6459 | 130.9303 | 0.8308%
-81.5 | 13.5 | 1401.3753 | 43.4274 | 63.353 | 88.7778 | 109.0017 | 136.6756 | 0.8874%
-81 | 13.5 | 1368.1139 | 34.4858 | 50.3492 | 72.0923 | 87.5207 | 109.8844 | 0.5566%
-80.5 | 13.5 | 1334.8586 | 21.1573 | 30.5111 | 43.6711 | 54.3147 | 67.2505 | 0.2094%
-80 | 13.5 | 1301.61 | 12.1402 | 16.7251 | 24.3178 | 29.0535 | 35.074 | 0.06066%
-79.5 | 13.5 | 1268.3688 | 7.2923 | 10.3897 | 14.3099 | 17.0863 | 21.0384 | 0.01963%
-79 | 13.5 | 1235.1356 | 5.5652 | 7.4069 | 10.3438 | 12.3181 | 14.6259 | 0.00808%
-78.5 | 13.5 | 1201.9115 | 5.243 | 6.9719 | 9.7262 | 11.8278 | 14.3941 | 0.008022%
-78 | 13.5 | 1168.6973 | 5.8556 | 8.2248 | 12.1229 | 14.9369 | 19.0825 | 0.01725%
-77.5 | 13.5 | 1135.494 | 7.3346 | 11.0162 | 16.404 | 20.8132 | 27.1235 | 0.03483%
-77 | 13.5 | 1102.3029 | 9.5945 | 14.3327 | 21.864 | 27.6273 | 34.6291 | 0.05574%
-76.5 | 13.5 | 1069.1252 | 13.61 | 21.3597 | 33.6778 | 43.3619 | 58.2902 | 0.1191%
-76 | 13.5 | 1035.9624 | 21.0212 | 33.928 | 55.7241 | 69.9938 | 90.1745 | 0.2447%
-75.5 | 13.5 | 1002.8162 | 29.123 | 47.6989 | 75.743 | 96.7712 | 129.0029 | 0.4056%
-75 | 13.5 | 969.6884 | 28.3331 | 44.3514 | 69.5552 | 87.1739 | 113.6175 | 0.3838%
-74.5 | 13.5 | 936.581 | 23.7018 | 35.3189 | 55.0037 | 68.4795 | 87.213 | 0.2755%
-74 | 13.5 | 903.4967 | 21.1779 | 29.9111 | 41.9461 | 51.5247 | 63.523 | 0.2014%
-73.5 | 13.5 | 870.4381 | 22.4567 | 30.9609 | 42.9674 | 52.4452 | 63.9625 | 0.2196%
-73 | 13.5 | 837.4085 | 24.1605 | 32.4434 | 44.6965 | 54.3134 | 65.4297 | 0.2493%
-72.5 | 13.5 | 804.4116 | 26.9834 | 35.3313 | 48.4081 | 58.4885 | 68.6775 | 0.3146%
-72 | 13.5 | 771.4517 | 34.3926 | 47.1699 | 65.2798 | 76.8 | 92.9355 | 0.5745%
-71.5 | 13.5 | 738.5341 | 48.5046 | 66.4617 | 89.3556 | 106.982 | 131.8466 | 1.259%
-71 | 13.5 | 705.6648 | 66.4052 | 89.4597 | 126.7149 | 148.9149 | 177.9833 | 2.552%
-70.5 | 13.5 | 672.851 | 75.0322 | 102.568 | 142.2599 | 165.58 | 197.8629 | 3.623%
-70 | 13.5 | 640.1015 | 74.4516 | 102.625 | 143.1281 | 166.9906 | 200.1108 | 3.423%
-69.5 | 13.5 | 607.4267 | 59.7719 | 81.7915 | 117.9872 | 142.6196 | 172.08 | 1.785%
-69 | 13.5 | 574.8398 | 35.7314 | 50.5245 | 70.4281 | 84.196 | 103.8205 | 0.6143%
-68.5 | 13.5 | 542.3565 | 25.657 | 34.0339 | 47.2391 | 57.6644 | 68.491 | 0.2832%
-68 | 13.5 | 509.997 | 21.4448 | 30.304 | 42.64 | 52.4842 | 64.5893 | 0.2074%
-67.5 | 13.5 | 477.7864 | 17.678 | 26.0895 | 36.7252 | 45.2154 | 57.7125 | 0.1496%
-67 | 13.5 | 445.7574 | 13.7319 | 19.5149 | 28.5251 | 34.524 | 43.1904 | 0.08759%
-66.5 | 13.5 | 413.9522 | 10.9592 | 15.0482 | 21.4578 | 26.4142 | 31.9109 | 0.04881%
-66 | 13.5 | 382.4269 | 9.3091 | 13.0929 | 18.1845 | 22.2062 | 27.4946 | 0.0348%
-65.5 | 13.5 | 351.2568 | 8.5447 | 12.0373 | 16.2714 | 19.5451 | 24.2358 | 0.02589%
-65 | 13.5 | 320.546 | 8.4689 | 11.7495 | 15.3656 | 18.0896 | 21.9076 | 0.01955%
-64.5 | 13.5 | 290.4403 | 9.1369 | 12.2889 | 15.7661 | 18.3461 | 21.9166 | 0.01825%
-64 | 13.5 | 261.1491 | 10.6585 | 13.6063 | 17.5023 | 20.399 | 24.415 | 0.02291%
-63.5 | 13.5 | 232.9801 | 12.5333 | 15.814 | 20.7495 | 24.477 | 28.3646 | 0.03631%
-63 | 13.5 | 206.3934 | 14.9749 | 19.48 | 26.2688 | 29.8625 | 34.7109 | 0.06496%
-62.5 | 13.5 | 182.0837 | 19.1787 | 26.0694 | 33.7415 | 39.4736 | 47.4531 | 0.1354%
-62 | 13.5 | 161.0852 | 27.7705 | 37.8005 | 54.1926 | 66.3935 | 83.509 | 0.3423%
-61.5 | 13.5 | 144.8455 | 37.9753 | 53.6113 | 75.7869 | 92.7383 | 117.5234 | 0.6656%
-61 | 13.5 | 135.0917 | 46.0896 | 62.8225 | 83.9846 | 100.2048 | 123.2749 | 1.138%
-60.5 | 13.5 | 133.256 | 56.2379 | 73.6164 | 99.6297 | 119.762 | 144.806 | 1.83%
-60 | 13.5 | 139.6508 | 60.4919 | 78.801 | 107.3211 | 129.5036 | 154.2741 | 2.188%
-59.5 | 13.5 | 153.2493 | 58.4613 | 76.4368 | 104.5502 | 126.4907 | 151.8853 | 1.954%
-59 | 13.5 | 172.3548 | 37.5143 | 51.3722 | 70.1861 | 83.4189 | 102.1608 | 0.6953%
-90 | 14 | 1963.0636 | 164.6307 | 223.4778 | 317.3451 | 387.4322 | 489.651 | 14.29%
-89.5 | 14 | 1929.7657 | 143.3957 | 191.8291 | 269.4972 | 328.1503 | 409.6684 | 11.99%
-89 | 14 | 1896.4666 | 139.4274 | 190.4671 | 274.2101 | 339.3064 | 433.4378 | 8.802%
-88.5 | 14 | 1863.1667 | 120.844 | 165.6987 | 236.3065 | 293.2504 | 371.8948 | 6.813%
-88 | 14 | 1829.8659 | 100.153 | 137.4753 | 192.8193 | 236.873 | 301.1582 | 4.996%
-87.5 | 14 | 1796.5645 | 86.7281 | 118.7136 | 169.2805 | 209.4982 | 269.0329 | 3.423%
-87 | 14 | 1763.2626 | 71.5007 | 94.6399 | 131.3056 | 158.8598 | 198.6506 | 2.781%
-86.5 | 14 | 1729.9604 | 59.0473 | 75.2624 | 99.9274 | 118.7303 | 142.8781 | 2.282%
-86 | 14 | 1696.6579 | 46.3306 | 61.9057 | 80.1699 | 93.8218 | 112.8334 | 1.299%
-85.5 | 14 | 1663.3555 | 41.8337 | 58.2278 | 78.8387 | 94.7955 | 117.6837 | 0.8773%
-85 | 14 | 1630.0533 | 40.9447 | 59.4864 | 83.9442 | 103.5062 | 132.0176 | 0.7704%
-84.5 | 14 | 1596.7514 | 41.4957 | 63.5266 | 96.7371 | 124.9334 | 158.2067 | 0.7254%
-84 | 14 | 1563.4501 | 34.2676 | 51.4515 | 76.0461 | 94.7492 | 122.6403 | 0.5317%
-83.5 | 14 | 1530.1497 | 27.7847 | 39.4066 | 59.013 | 71.4637 | 89.4622 | 0.3554%
-83 | 14 | 1496.8502 | 25.0948 | 34.0625 | 48.1731 | 59.1004 | 70.6079 | 0.2773%
-82.5 | 14 | 1463.5521 | 29.243 | 41.3052 | 61.0102 | 73.9212 | 92.5957 | 0.392%
-82 | 14 | 1430.2555 | 34.5465 | 50.4028 | 72.2424 | 87.8214 | 110.4369 | 0.5572%
-81.5 | 14 | 1396.9608 | 34.88 | 51.4814 | 74.8548 | 92.3282 | 118.0996 | 0.5562%
-81 | 14 | 1363.6683 | 27.6268 | 39.6498 | 59.947 | 73.2052 | 92.547 | 0.353%
-80.5 | 14 | 1330.3782 | 16.0754 | 23.5574 | 33.0467 | 39.9255 | 49.8438 | 0.1196%
-80 | 14 | 1297.0911 | 9.6748 | 13.762 | 19.5279 | 24.1596 | 29.3711 | 0.04122%
-79.5 | 14 | 1263.8073 | 6.0585 | 8.4574 | 12.1795 | 14.4208 | 17.582 | 0.01386%
-79 | 14 | 1230.5273 | 4.4056 | 6.0207 | 8.2137 | 9.9216 | 12.1098 | 0.005347%
-78.5 | 14 | 1197.2514 | 3.824 | 5.354 | 7.2034 | 8.6281 | 10.663 | 0.004025%
-78 | 14 | 1163.9804 | 4.0576 | 5.7488 | 8.1296 | 10.037 | 12.6095 | 0.007188%
-77.5 | 14 | 1130.7148 | 4.9623 | 7.055 | 10.5758 | 13.0831 | 16.4831 | 0.01363%
-77 | 14 | 1097.4552 | 6.2648 | 9.3119 | 13.9659 | 17.3729 | 22.4448 | 0.02492%
-76.5 | 14 | 1064.2024 | 8.6749 | 13.4221 | 20.7168 | 26.6807 | 33.694 | 0.05277%
-76 | 14 | 1030.9572 | 13.2 | 22.1337 | 37.3897 | 50.5943 | 68.7128 | 0.1339%
-75.5 | 14 | 997.7206 | 17.3541 | 29.595 | 50.4048 | 67.1263 | 90.7531 | 0.1982%
-75 | 14 | 964.4937 | 17.5823 | 29.3596 | 48.8701 | 64.5245 | 85.2123 | 0.1955%
-74.5 | 14 | 931.2776 | 14.483 | 22.3054 | 35.0765 | 45.6092 | 61.4509 | 0.1289%
-74 | 14 | 898.0737 | 12.8085 | 17.7441 | 25.9243 | 30.8201 | 37.756 | 0.06971%
-73.5 | 14 | 864.8837 | 13.1198 | 17.76 | 25.298 | 29.7504 | 35.7601 | 0.06432%
-73 | 14 | 831.7093 | 14.3046 | 19.3621 | 27.0572 | 31.5522 | 37.7878 | 0.07421%
-72.5 | 14 | 798.5527 | 16.8793 | 23.4368 | 31.4605 | 36.9559 | 44.6402 | 0.1093%
-72 | 14 | 765.4163 | 23.2662 | 31.4664 | 42.9843 | 51.964 | 63.004 | 0.2296%
-71.5 | 14 | 732.3031 | 32.3698 | 44.6069 | 62.8587 | 73.923 | 89.4136 | 0.4973%
-71 | 14 | 699.2166 | 43.8322 | 63.1066 | 88.5432 | 108.7963 | 137.0886 | 0.8987%
-70.5 | 14 | 666.1609 | 51.008 | 71.782 | 102.1384 | 126.5768 | 154.3324 | 1.229%
-70 | 14 | 633.1411 | 47.8419 | 68.8092 | 98.4288 | 122.3736 | 150.6137 | 1.055%
-69.5 | 14 | 600.1631 | 36.2979 | 54.6736 | 82.6741 | 105.6987 | 138.9547 | 0.5704%
-69 | 14 | 567.2345 | 22.3387 | 30.853 | 42.6073 | 51.8501 | 63.3479 | 0.2168%
-68.5 | 14 | 534.3646 | 16.2737 | 23.0673 | 31.9637 | 38.2548 | 47.2327 | 0.1127%
-68 | 14 | 501.5652 | 13.8368 | 19.7129 | 28.8935 | 35.1944 | 44.3611 | 0.09067%
-67.5 | 14 | 468.8511 | 11.4376 | 16.1399 | 24.1277 | 29.7586 | 37.4815 | 0.06453%
-67 | 14 | 436.2418 | 8.5154 | 12.432 | 17.865 | 22.2728 | 28.2289 | 0.03724%
-66.5 | 14 | 403.7628 | 6.7566 | 9.5681 | 13.6237 | 16.4654 | 20.5645 | 0.01932%
-66 | 14 | 371.4486 | 5.926 | 8.0834 | 11.5759 | 13.6831 | 16.6499 | 0.01178%
-65.5 | 14 | 339.3463 | 5.6943 | 7.5172 | 10.3982 | 12.3582 | 14.7241 | 0.007853%
-65 | 14 | 307.5225 | 5.9793 | 7.7247 | 10.4188 | 12.1831 | 14.1754 | 0.006128%
-64.5 | 14 | 276.0737 | 6.894 | 9.0017 | 11.9831 | 13.5329 | 15.6088 | 0.007292%
-64 | 14 | 245.1446 | 8.8948 | 11.911 | 15.0316 | 17.317 | 20.4455 | 0.01453%
-63.5 | 14 | 214.9596 | 12.5096 | 16.0504 | 21.4753 | 25.6361 | 29.5998 | 0.0417%
-63 | 14 | 185.8819 | 17.5741 | 23.9936 | 31.4721 | 36.6027 | 43.6991 | 0.1106%
-62.5 | 14 | 158.5221 | 26.7344 | 34.7734 | 47.2751 | 56.9851 | 67.0014 | 0.3051%
-62 | 14 | 133.9373 | 38.5656 | 54.0444 | 75.1172 | 90.9501 | 113.8334 | 0.7076%
-61.5 | 14 | 113.9385 | 49.8501 | 67.1895 | 90.3992 | 108.2789 | 133.214 | 1.349%
-61 | 14 | 101.2798 | 61.3767 | 79.6551 | 108.0114 | 129.9906 | 154.5945 | 2.32%
-60.5 | 14 | 98.8235 | 71.3786 | 94.3822 | 130.8048 | 152.394 | 182.224 | 3.35%
-60 | 14 | 107.2726 | 71.0993 | 93.7814 | 129.5983 | 151.0042 | 180.1195 | 3.373%
-59.5 | 14 | 124.425 | 64.743 | 85.1277 | 117.2059 | 139.7348 | 166.7608 | 2.559%
-59 | 14 | 147.2705 | 41.0514 | 56.7733 | 76.0625 | 90.5528 | 111.1129 | 0.8701%
-90 | 14.5 | 1959.36 | 182.9599 | 240.5844 | 319.3965 | 364.7318 | 426.1986 | 54.79%
-89.5 | 14.5 | 1926.0778 | 154.1275 | 201.2659 | 274.889 | 323.701 | 384.8884 | 23.41%
-89 | 14.5 | 1892.7935 | 131.912 | 177.6489 | 251.5302 | 310.1996 | 393.9984 | 8.75%
-88.5 | 14.5 | 1859.5073 | 111.3818 | 152.5697 | 213.5382 | 261.9883 | 331.1023 | 6.411%
-88 | 14.5 | 1826.2192 | 88.7759 | 119.7003 | 165.5727 | 200.6313 | 251.3458 | 4.418%
-87.5 | 14.5 | 1792.9294 | 82.0263 | 109.1075 | 150.6703 | 181.9252 | 226.9618 | 3.855%
-87 | 14.5 | 1759.638 | 89.748 | 123.3651 | 165.2746 | 195.6165 | 238.395 | 5.595%
-86.5 | 14.5 | 1726.345 | 80.617 | 108.63 | 146.9462 | 170.887 | 203.998 | 4.796%
-86 | 14.5 | 1693.0505 | 61.2568 | 79.9927 | 109.2557 | 131.8862 | 158.4531 | 2.203%
-85.5 | 14.5 | 1659.7547 | 44.815 | 61.032 | 80.3913 | 95.0572 | 115.7124 | 1.117%
-85 | 14.5 | 1626.4577 | 38.196 | 52.9203 | 72.8617 | 87.4318 | 108.2848 | 0.7083%
-84.5 | 14.5 | 1593.1595 | 35.6799 | 51.3783 | 74.5222 | 92.1876 | 118.3256 | 0.574%
-84 | 14.5 | 1559.8603 | 32.194 | 46.5429 | 68.282 | 83.5943 | 105.9946 | 0.4756%
-83.5 | 14.5 | 1526.5602 | 28.2323 | 39.9359 | 59.4494 | 71.566 | 88.9681 | 0.3672%
-83 | 14.5 | 1493.2594 | 26.5517 | 36.6024 | 53.2578 | 64.2682 | 77.7956 | 0.3191%
-82.5 | 14.5 | 1459.9579 | 32.1728 | 47.5354 | 70.1303 | 86.0195 | 109.3117 | 0.4783%
-82 | 14.5 | 1426.656 | 39.4704 | 60.2968 | 86.0025 | 106.736 | 135.6155 | 0.7145%
-81.5 | 14.5 | 1393.3537 | 39.6824 | 61.8479 | 91.8981 | 116.9261 | 148.2622 | 0.6917%
-81 | 14.5 | 1360.0513 | 28.3044 | 42.2499 | 64.8881 | 80.0623 | 102.4507 | 0.3764%
-80.5 | 14.5 | 1326.7489 | 15.7984 | 24.2829 | 36.6648 | 46.755 | 61.4354 | 0.1407%
-80 | 14.5 | 1293.4467 | 8.7344 | 12.728 | 18.1471 | 22.5167 | 28.2061 | 0.03742%
-79.5 | 14.5 | 1260.1448 | 5.69 | 7.7923 | 11.2508 | 13.348 | 16.2285 | 0.01144%
-79 | 14.5 | 1226.8436 | 4.1868 | 5.7766 | 7.7803 | 9.3252 | 11.5086 | 0.004632%
-78.5 | 14.5 | 1193.5433 | 3.6158 | 5.1468 | 6.8063 | 8.0674 | 9.8482 | 0.003213%
-78 | 14.5 | 1160.244 | 3.6706 | 5.282 | 7.2064 | 8.7051 | 10.8659 | 0.004783%
-77.5 | 14.5 | 1126.9462 | 4.2208 | 6.0593 | 8.6956 | 10.8323 | 13.3202 | 0.008574%
-77 | 14.5 | 1093.65 | 5.2436 | 7.491 | 11.3636 | 13.7763 | 17.2315 | 0.01498%
-76.5 | 14.5 | 1060.3559 | 6.4553 | 9.7177 | 14.5124 | 18.076 | 23.3883 | 0.02696%
-76 | 14.5 | 1027.0643 | 8.0537 | 12.5069 | 18.8953 | 24.2858 | 30.7636 | 0.04507%
-75.5 | 14.5 | 993.7754 | 9.5615 | 15.0903 | 24.6652 | 31.604 | 41.8285 | 0.07135%
-75 | 14.5 | 960.49 | 9.5605 | 14.9666 | 24.3325 | 31.2898 | 41.4963 | 0.07026%
-74.5 | 14.5 | 927.2084 | 8.3736 | 12.4297 | 18.182 | 22.9144 | 29.1604 | 0.03996%
-74 | 14.5 | 893.9313 | 7.8098 | 11.1805 | 15.3795 | 18.6035 | 23.2583 | 0.02433%
-73.5 | 14.5 | 860.6595 | 8.1053 | 11.4236 | 15.1936 | 18.0649 | 22.1333 | 0.02083%
-73 | 14.5 | 827.3936 | 9.174 | 12.5772 | 16.7277 | 19.8961 | 24.3872 | 0.02536%
-72.5 | 14.5 | 794.1347 | 11.516 | 15.0942 | 20.7055 | 25.0946 | 29.8064 | 0.04172%
-72 | 14.5 | 760.8839 | 14.6895 | 20.3259 | 28.6234 | 33.9305 | 41.4254 | 0.08683%
-71.5 | 14.5 | 727.6424 | 19.4354 | 27.7318 | 38.0722 | 46.1656 | 57.8821 | 0.1672%
-71 | 14.5 | 694.4118 | 23.9899 | 32.7411 | 45.766 | 56.1061 | 67.2289 | 0.2518%
-70.5 | 14.5 | 661.1939 | 26.4379 | 36.0367 | 51.7481 | 62.7581 | 75.925 | 0.3124%
-70 | 14.5 | 627.9909 | 24.0471 | 33.3998 | 47.7928 | 59.1173 | 71.7715 | 0.2601%
-69.5 | 14.5 | 594.8054 | 17.8954 | 25.8565 | 35.0567 | 42.1871 | 52.4242 | 0.1401%
-69 | 14.5 | 561.6408 | 13.454 | 18.2971 | 26.0893 | 30.5189 | 36.6847 | 0.06841%
-68.5 | 14.5 | 528.5012 | 10.69 | 14.4389 | 19.9955 | 24.3745 | 29.4278 | 0.04044%
-68 | 14.5 | 495.3919 | 8.6621 | 12.2869 | 17.0264 | 20.7633 | 26.1307 | 0.03095%
-67.5 | 14.5 | 462.3193 | 7.1869 | 10.1502 | 14.3634 | 17.4853 | 22.0241 | 0.02201%
-67 | 14.5 | 429.2924 | 6.0183 | 8.2525 | 11.8402 | 14.2038 | 17.5855 | 0.01353%
-66.5 | 14.5 | 396.3226 | 5.244 | 7.0047 | 9.8237 | 11.9288 | 14.4037 | 0.008183%
-66 | 14.5 | 363.4257 | 4.8162 | 6.3843 | 8.71 | 10.5213 | 12.704 | 0.005558%
-65.5 | 14.5 | 330.6237 | 4.9425 | 6.3615 | 8.4506 | 10.0437 | 12.0887 | 0.004025%
-65 | 14.5 | 297.9481 | 5.5941 | 7.1042 | 9.3921 | 11.1303 | 12.9263 | 0.004416%
-64.5 | 14.5 | 265.4458 | 7.0608 | 9.3033 | 12.3736 | 14.131 | 16.5141 | 0.008813%
-64 | 14.5 | 233.1894 | 10.4289 | 13.6316 | 17.967 | 21.253 | 25.8557 | 0.02788%
-63.5 | 14.5 | 201.2974 | 15.9253 | 21.5924 | 29.0802 | 33.6442 | 39.921 | 0.08817%
-63 | 14.5 | 169.9753 | 27.0459 | 35.2678 | 48.0892 | 58.0709 | 67.3681 | 0.3155%
-62.5 | 14.5 | 139.6073 | 45.8511 | 63.1887 | 83.711 | 99.3286 | 121.408 | 1.155%
-62 | 14.5 | 110.9797 | 82.3738 | 119.3609 | 166.1978 | 199.8257 | 248.058 | 3.519%
-61.5 | 14.5 | 85.8519 | 79.2529 | 106.7451 | 145.1742 | 168.9638 | 201.895 | 4.497%
-61 | 14.5 | 68.2082 | 78.6122 | 103.6975 | 140.1814 | 162.5831 | 193.4749 | 4.75%
-60.5 | 14.5 | 64.5132 | 85.16 | 113.8276 | 151.6627 | 176.5735 | 211.069 | 5.857%
-60 | 14.5 | 76.807 | 82.1119 | 109.4134 | 146.9889 | 170.977 | 204.1619 | 5.238%
-59.5 | 14.5 | 99.32 | 71.793 | 94.8982 | 131.3653 | 152.7809 | 182.4021 | 3.439%
-59 | 14.5 | 126.7176 | 45.0698 | 61.7066 | 82.3826 | 98.2134 | 120.7096 | 1.083%
-90 | 15 | 1956.2095 | 172.6554 | 220.7961 | 294.288 | 330.0232 | 376.9813 | 64.01%
-89.5 | 15 | 1922.9542 | 159.8313 | 202.9874 | 268.3741 | 309.9406 | 352.9148 | 46.79%
-89 | 15 | 1889.6964 | 160.1887 | 206.5121 | 277.8549 | 319.4074 | 367.0116 | 38.62%
-88.5 | 15 | 1856.4361 | 146.5833 | 186.7979 | 247.9552 | 294.5686 | 337.517 | 28.69%
-88 | 15 | 1823.1732 | 125.8721 | 161.9718 | 214.0349 | 253.5761 | 307.2304 | 15.95%
-87.5 | 15 | 1789.908 | 129.7869 | 165.1903 | 218.0863 | 258.2307 | 311.747 | 18.15%
-87 | 15 | 1756.6404 | 134.7106 | 168.1027 | 217.7347 | 254.8381 | 302.7387 | 27.35%
-86.5 | 15 | 1723.3705 | 115.2716 | 149.5557 | 191.1161 | 221.8556 | 264.2865 | 17.6%
-86 | 15 | 1690.0985 | 84.6007 | 113.2976 | 150.1687 | 173.5115 | 205.5688 | 6.153%
-85.5 | 15 | 1656.8242 | 62.3694 | 79.9442 | 106.8418 | 127.4532 | 150.0602 | 2.648%
-85 | 15 | 1623.5479 | 43.6125 | 59.2074 | 75.989 | 88.4439 | 105.6853 | 1.141%
-84.5 | 15 | 1590.2695 | 34.9829 | 46.9462 | 64.3425 | 75.7514 | 91.7436 | 0.5956%
-84 | 15 | 1556.9892 | 29.9788 | 40.3571 | 57.1144 | 68.0041 | 83.1264 | 0.4079%
-83.5 | 15 | 1523.7069 | 26.1367 | 34.7213 | 48.3831 | 58.9405 | 70.4716 | 0.296%
-83 | 15 | 1490.4229 | 25.4727 | 34.6146 | 49.3083 | 60.3568 | 72.7876 | 0.2871%
-82.5 | 15 | 1457.137 | 30.8119 | 45.1757 | 67.1364 | 82.0712 | 103.884 | 0.4398%
-82 | 15 | 1423.8495 | 37.5738 | 58.028 | 82.3929 | 101.9372 | 130.8591 | 0.6523%
-81.5 | 15 | 1390.5604 | 37.4614 | 58.9311 | 85.85 | 107.9251 | 138.1534 | 0.6357%
-81 | 15 | 1357.2697 | 27.1197 | 40.5582 | 62.9807 | 77.5232 | 98.9237 | 0.3498%
-80.5 | 15 | 1323.9776 | 15.4005 | 23.6543 | 36.3964 | 46.8806 | 62.0582 | 0.1379%
-80 | 15 | 1290.684 | 8.927 | 12.7657 | 17.9258 | 22.037 | 27.6117 | 0.03527%
-79.5 | 15 | 1257.3892 | 6.3177 | 8.6622 | 12.2104 | 14.3424 | 17.3235 | 0.01253%
-79 | 15 | 1224.0931 | 5.2852 | 7.0287 | 9.8066 | 11.8377 | 13.9829 | 0.007419%
-78.5 | 15 | 1190.7959 | 4.8322 | 6.5342 | 9.111 | 11.1526 | 13.2578 | 0.00695%
-78 | 15 | 1157.4977 | 4.9109 | 6.7034 | 9.5131 | 11.6711 | 13.8867 | 0.008211%
-77.5 | 15 | 1124.1985 | 5.4071 | 7.5369 | 11.1094 | 13.3123 | 16.3065 | 0.01242%
-77 | 15 | 1090.8984 | 6.278 | 9.2158 | 13.6548 | 16.8061 | 21.4431 | 0.02255%
-76.5 | 15 | 1057.5977 | 7.3459 | 11.3338 | 16.6805 | 21.0695 | 27.249 | 0.03561%
-76 | 15 | 1024.2963 | 7.9432 | 12.2503 | 18.2778 | 23.3141 | 29.5938 | 0.04192%
-75.5 | 15 | 990.9944 | 7.6648 | 11.8303 | 17.5558 | 22.3197 | 28.5615 | 0.0391%
-75 | 15 | 957.6922 | 6.7648 | 10.0873 | 14.9254 | 18.6233 | 24.1465 | 0.02816%
-74.5 | 15 | 924.3898 | 5.9863 | 8.428 | 12.3167 | 14.9006 | 18.6317 | 0.01625%
-74 | 15 | 891.0873 | 5.7634 | 7.7672 | 11.0066 | 13.0135 | 15.6527 | 0.009883%
-73.5 | 15 | 857.7851 | 6.0796 | 8.0923 | 11.3023 | 13.0707 | 15.4315 | 0.008786%
-73 | 15 | 824.4832 | 6.8811 | 9.3119 | 12.6638 | 14.68 | 17.4587 | 0.01151%
-72.5 | 15 | 791.1819 | 8.2512 | 11.5467 | 15.162 | 17.8941 | 21.734 | 0.01949%
-72 | 15 | 757.8814 | 10.355 | 13.9525 | 19.0241 | 22.9723 | 27.9489 | 0.03539%
-71.5 | 15 | 724.5822 | 12.4838 | 16.7656 | 23.6612 | 28.3048 | 34.0651 | 0.05691%
-71 | 15 | 691.2845 | 13.7998 | 18.8279 | 26.7251 | 31.4369 | 38.0354 | 0.07324%
-70.5 | 15 | 657.9888 | 14.1386 | 19.3278 | 27.2789 | 32.0791 | 38.7992 | 0.07677%
-70 | 15 | 624.6956 | 13.3221 | 17.9365 | 25.3883 | 29.7465 | 35.6413 | 0.06433%
-69.5 | 15 | 591.4055 | 11.9011 | 15.6182 | 21.4552 | 25.9632 | 30.5953 | 0.04487%
-69 | 15 | 558.1192 | 10.1115 | 13.5181 | 18.0707 | 21.56 | 26.3183 | 0.03002%
-68.5 | 15 | 524.8377 | 8.6521 | 11.9409 | 15.7462 | 18.6316 | 22.6982 | 0.02137%
-68 | 15 | 491.5621 | 7.5599 | 10.3818 | 14.0034 | 16.54 | 20.1083 | 0.01643%
-67.5 | 15 | 458.2939 | 6.679 | 9.0111 | 12.4629 | 14.6779 | 17.7839 | 0.01253%
-67 | 15 | 425.0351 | 6.0412 | 8.0583 | 11.2827 | 13.2664 | 15.9819 | 0.009834%
-66.5 | 15 | 391.7882 | 5.7009 | 7.5842 | 10.5861 | 12.625 | 15.2215 | 0.008855%
-66 | 15 | 358.5568 | 5.6534 | 7.5152 | 10.4802 | 12.5608 | 15.2387 | 0.008909%
-65.5 | 15 | 325.3457 | 5.9111 | 7.7988 | 10.7805 | 12.8127 | 15.4964 | 0.008835%
-65 | 15 | 292.1622 | 6.6978 | 8.8401 | 12.0287 | 13.9554 | 16.6132 | 0.009731%
-64.5 | 15 | 259.017 | 8.7256 | 11.8172 | 15.2253 | 17.7625 | 21.2837 | 0.01719%
-64 | 15 | 225.9272 | 13.1665 | 17.2078 | 23.5257 | 27.5794 | 32.1083 | 0.05185%
-63.5 | 15 | 192.9216 | 21.655 | 29.1109 | 38.3854 | 45.4173 | 55.3278 | 0.186%
-63 | 15 | 160.0525 | 40.2351 | 56.1629 | 73.563 | 86.0724 | 103.489 | 0.8865%
-62.5 | 15 | 127.4257 | 91.7175 | 129.5645 | 167.7056 | 195.7038 | 234.5726 | 6.911%
-62 | 15 | 95.2907 | 133.2729 | 171.3496 | 229.819 | 274.7497 | 322.5135 | 18.13%
-61.5 | 15 | 64.3885 | 95.4327 | 128.292 | 164.4248 | 190.4734 | 226.3474 | 9.501%
-61 | 15 | 37.8685 | 99.1785 | 133.3521 | 171.3246 | 199.5297 | 238.6008 | 9.969%
-60.5 | 15 | 30.7369 | 98.2917 | 132.6096 | 170.6603 | 198.9615 | 238.2099 | 9.498%
-60 | 15 | 51.7502 | 89.6192 | 120.2588 | 158.0647 | 184.0212 | 219.9633 | 6.986%
-59.5 | 15 | 81.4493 | 74.9249 | 99.1601 | 135.9549 | 158.0825 | 188.6809 | 3.935%
-59 | 15 | 113.1921 | 47.0287 | 63.8534 | 85.3777 | 101.8778 | 125.3487 | 1.193%
-90 | 15.5 | 1953.6146 | 166.5924 | 216.2337 | 293.2563 | 332.9325 | 385.3446 | 41.43%
-89.5 | 15.5 | 1920.3979 | 156.7152 | 200.4769 | 267.3074 | 310.5209 | 356.0471 | 37.77%
-89 | 15.5 | 1887.1783 | 180.2125 | 241.6155 | 324.0558 | 371.4149 | 435.8837 | 43.26%
-88.5 | 15.5 | 1853.956 | 172.6408 | 226.3392 | 305.2958 | 346.6195 | 402.2951 | 45%
-88 | 15.5 | 1820.731 | 166.292 | 213.7443 | 286.5891 | 325.5702 | 373.587 | 48.19%
-87.5 | 15.5 | 1787.5034 | 191.0628 | 256.4904 | 336.9399 | 385.9727 | 452.6804 | 58.43%
-87 | 15.5 | 1754.2732 | 178.0754 | 233.0729 | 310.8219 | 352.5229 | 408.6423 | 54.28%
-86.5 | 15.5 | 1721.0405 | 155.8847 | 198.9621 | 264.5849 | 308.2369 | 353.5641 | 37.52%
-86 | 15.5 | 1687.8052 | 140.1577 | 182.2775 | 247.7696 | 297.6729 | 347.9097 | 18.3%
-85.5 | 15.5 | 1654.5676 | 94.3957 | 128.7009 | 165.8716 | 192.8841 | 230.2408 | 8.433%
-85 | 15.5 | 1621.3276 | 65.1324 | 82.8123 | 109.6327 | 130.0321 | 150.3519 | 3.251%
-84.5 | 15.5 | 1588.0853 | 45.4383 | 60.8346 | 77.0387 | 88.9381 | 105.2648 | 1.349%
-84 | 15.5 | 1554.8407 | 34.226 | 44.9531 | 60.6164 | 69.1588 | 80.7297 | 0.5961%
-83.5 | 15.5 | 1521.5939 | 28.3403 | 36.5606 | 49.23 | 58.7568 | 68.4776 | 0.3512%
-83 | 15.5 | 1488.3449 | 25.7312 | 33.2662 | 44.8576 | 53.8028 | 64.287 | 0.2745%
-82.5 | 15.5 | 1455.0939 | 27.1613 | 37.3673 | 54.2426 | 66.5882 | 83.7593 | 0.3301%
-82 | 15.5 | 1421.8408 | 30.3589 | 43.7744 | 65.1011 | 79.8803 | 101.554 | 0.4224%
-81.5 | 15.5 | 1388.5857 | 29.3509 | 43.0338 | 65.6758 | 82.3868 | 107.4932 | 0.3933%
-81 | 15.5 | 1355.3286 | 22.4806 | 33.0659 | 50.1706 | 63.6278 | 81.9276 | 0.2465%
-80.5 | 15.5 | 1322.0697 | 14.7119 | 20.6294 | 29.4043 | 35.3238 | 43.8062 | 0.09343%
-80 | 15.5 | 1288.8089 | 10.7196 | 14.3339 | 19.5907 | 23.6906 | 28.5307 | 0.03739%
-79.5 | 15.5 | 1255.5463 | 8.4699 | 11.9456 | 15.9153 | 18.9498 | 23.256 | 0.02339%
-79 | 15.5 | 1222.282 | 7.6733 | 10.9885 | 14.965 | 17.927 | 22.1584 | 0.02179%
-78.5 | 15.5 | 1189.016 | 7.4279 | 10.724 | 14.7867 | 17.7674 | 22.0397 | 0.022%
-78 | 15.5 | 1155.7484 | 7.4876 | 10.9176 | 14.9596 | 17.9525 | 22.2365 | 0.02251%
-77.5 | 15.5 | 1122.4791 | 8.1559 | 11.9954 | 16.6475 | 20.3199 | 25.6747 | 0.03054%
-77 | 15.5 | 1089.2084 | 10.0536 | 14.7431 | 22.0799 | 27.6935 | 34.7501 | 0.05601%
-76.5 | 15.5 | 1055.9361 | 12.2767 | 18.3615 | 28.4765 | 35.3757 | 45.6311 | 0.08808%
-76 | 15.5 | 1022.6624 | 12.6557 | 19.2459 | 29.8576 | 37.2525 | 48.2969 | 0.09587%
-75.5 | 15.5 | 989.3873 | 10.6953 | 16.2491 | 25.9088 | 32.1098 | 41.3036 | 0.07392%
-75 | 15.5 | 956.1109 | 7.6135 | 11.6716 | 17.3378 | 22.0559 | 28.438 | 0.03847%
-74.5 | 15.5 | 922.8332 | 6.0021 | 8.4301 | 12.3 | 14.8851 | 18.6193 | 0.01615%
-74 | 15.5 | 889.5542 | 5.6876 | 7.6389 | 10.7815 | 12.7862 | 15.335 | 0.009335%
-73.5 | 15.5 | 856.2741 | 6.205 | 8.3645 | 11.7456 | 13.7212 | 16.4671 | 0.01073%
-73 | 15.5 | 822.9929 | 7.3679 | 10.2396 | 14.0257 | 16.6915 | 20.4726 | 0.01781%
-72.5 | 15.5 | 789.7105 | 9.0355 | 12.6022 | 17.2515 | 20.8822 | 26.0457 | 0.03031%
-72 | 15.5 | 756.4272 | 10.9359 | 14.7481 | 20.5858 | 25.215 | 30.3763 | 0.04357%
-71.5 | 15.5 | 723.1429 | 12.1155 | 16.1573 | 22.6167 | 27.251 | 32.634 | 0.05168%
-71 | 15.5 | 689.8577 | 12.5161 | 16.5238 | 22.8585 | 27.2664 | 32.247 | 0.05109%
-70.5 | 15.5 | 656.5716 | 12.5741 | 16.4479 | 22.5094 | 26.8086 | 31.396 | 0.0483%
-70 | 15.5 | 623.2848 | 12.4668 | 16.2396 | 22.1163 | 26.4224 | 30.8698 | 0.04629%
-69.5 | 15.5 | 589.9972 | 12.2672 | 15.9953 | 21.8088 | 26.185 | 30.7299 | 0.04547%
-69 | 15.5 | 556.7089 | 11.9637 | 15.6689 | 21.4747 | 25.9598 | 30.7546 | 0.04508%
-68.5 | 15.5 | 523.4201 | 11.3516 | 14.924 | 20.483 | 24.8332 | 29.8736 | 0.04139%
-68 | 15.5 | 490.1308 | 10.1091 | 13.6298 | 18.551 | 22.3767 | 27.4498 | 0.03366%
-67.5 | 15.5 | 456.8411 | 8.9322 | 12.26 | 16.4527 | 19.676 | 24.2722 | 0.02526%
-67 | 15.5 | 423.5511 | 8.2707 | 11.4808 | 15.3698 | 18.3539 | 22.6022 | 0.02163%
-66.5 | 15.5 | 390.2609 | 8.2555 | 11.5395 | 15.7572 | 19.0445 | 23.7864 | 0.02483%
-66 | 15.5 | 356.9707 | 8.6251 | 12.0921 | 16.8656 | 20.6486 | 26.1008 | 0.03068%
-65.5 | 15.5 | 323.6807 | 8.9756 | 12.4738 | 17.3591 | 21.2238 | 26.6489 | 0.03198%
-65 | 15.5 | 290.3912 | 9.5422 | 12.9122 | 17.4466 | 20.9515 | 25.9372 | 0.02922%
-64.5 | 15.5 | 257.1026 | 11.7321 | 15.0322 | 20.0809 | 23.9483 | 28.425 | 0.03627%
-64 | 15.5 | 223.8154 | 16.2799 | 21.8218 | 29.1487 | 33.709 | 39.9779 | 0.08927%
-63.5 | 15.5 | 190.5307 | 27.8726 | 36.2209 | 49.1907 | 58.9107 | 68.5222 | 0.3391%
-63 | 15.5 | 157.2504 | 59.7652 | 79.8241 | 111.9348 | 135.7942 | 162.4103 | 1.924%
-62.5 | 15.5 | 123.9781 | 127.783 | 166.4679 | 224.0925 | 268.5024 | 318.6022 | 14.76%
-62 | 15.5 | 90.723 | 117.3098 | 151.5919 | 195.0655 | 227.397 | 272.2311 | 17.23%
-61.5 | 15.5 | 57.5152 | 117.5452 | 151.8304 | 196.1766 | 229.2643 | 275.2723 | 16.54%
-61 | 15.5 | 24.548 | 111.6472 | 146.0273 | 188.1954 | 219.5943 | 263.1797 | 14.28% | 185.7288
-60.5 | 15.5 | 10.7005 | 100.9563 | 134.9104 | 173.1519 | 201.5341 | 240.8243 | 10.73%
-60 | 15.5 | 42.9382 | 86.2029 | 114.1887 | 150.9049 | 174.9398 | 208.0672 | 6.539%
-59.5 | 15.5 | 76.0931 | 72.7341 | 95.9079 | 132.1493 | 153.654 | 183.3904 | 3.618%
-59 | 15.5 | 109.3339 | 43.9059 | 60.1831 | 80.0766 | 95.2677 | 116.8062 | 1.029%
-90 | 16 | 1951.5777 | 138.1367 | 176.3476 | 234.5705 | 279.0203 | 326.6004 | 22.11%
-89.5 | 16 | 1918.4109 | 136.1317 | 171.9525 | 225.9049 | 266.693 | 314.4253 | 24.14%
-89 | 16 | 1885.2415 | 150.3382 | 194.1954 | 261.8857 | 308.0028 | 356.1936 | 27.18%
-88.5 | 16 | 1852.0696 | 160.1295 | 205.8741 | 276.1163 | 318.0367 | 365.6398 | 39.33%
-88 | 16 | 1818.8951 | 167.2593 | 213.6695 | 284.4378 | 322.6627 | 368.3727 | 54.94%
-87.5 | 16 | 1785.7182 | 186.3568 | 244.4833 | 320.9819 | 363.8427 | 421.4878 | 69.29%
-87 | 16 | 1752.5389 | 185.9903 | 241.6972 | 316.0816 | 356.2615 | 409.9679 | 80.23%
-86.5 | 16 | 1719.3573 | 179.302 | 230.2857 | 303.6949 | 340.3716 | 389.0944 | 76.65%
-86 | 16 | 1686.1736 | 183.235 | 240.8311 | 318.4388 | 361.5266 | 419.5764 | 60.79%
-85.5 | 16 | 1652.9876 | 158.8322 | 204.5532 | 274.8894 | 317.4304 | 365.4675 | 36.89%
-85 | 16 | 1619.7997 | 125.466 | 161.1586 | 211.7965 | 250.0891 | 301.2397 | 17.01%
-84.5 | 16 | 1586.6097 | 83.1997 | 113.8199 | 154.7919 | 182.507 | 221.4185 | 4.587%
-84 | 16 | 1553.4179 | 55.0735 | 71.0386 | 93.4284 | 110.3695 | 133.3306 | 1.952%
-83.5 | 16 | 1520.2242 | 40.8273 | 56.0339 | 73.1584 | 85.4438 | 102.5149 | 0.9286%
-83 | 16 | 1487.0288 | 34.1082 | 45.5346 | 62.1366 | 71.9388 | 85.4296 | 0.5759%
-82.5 | 16 | 1453.8318 | 31.4128 | 41.416 | 57.2042 | 65.9187 | 77.4021 | 0.4674%
-82 | 16 | 1420.6332 | 31.3748 | 41.8876 | 58.5472 | 67.8101 | 80.5645 | 0.4637%
-81.5 | 16 | 1387.4331 | 29.4959 | 39.3142 | 54.9959 | 64.7682 | 77.0826 | 0.3965%
-81 | 16 | 1354.2317 | 24.338 | 32.183 | 43.5284 | 52.3047 | 62.9219 | 0.2466%
-80.5 | 16 | 1321.029 | 17.9795 | 25.1468 | 32.8538 | 38.4507 | 46.2455 | 0.1233%
-80 | 16 | 1287.8252 | 14.5847 | 19.6985 | 27.2673 | 31.5327 | 37.3961 | 0.07434%
-79.5 | 16 | 1254.6203 | 13.4208 | 18.2568 | 26.0551 | 30.503 | 36.6996 | 0.06832%
-79 | 16 | 1221.4145 | 13.4525 | 18.7676 | 27.1557 | 32.2302 | 39.4063 | 0.07677%
-78.5 | 16 | 1188.2079 | 13.3962 | 18.7795 | 27.2444 | 32.287 | 39.4062 | 0.07696%
-78 | 16 | 1155.0007 | 13.0003 | 17.9794 | 26.1134 | 30.5765 | 36.7954 | 0.06848%
-77.5 | 16 | 1121.7929 | 13.2667 | 18.4109 | 26.6141 | 31.2156 | 37.6393 | 0.07172%
-77 | 16 | 1088.5848 | 15.5092 | 22.8033 | 32.6526 | 39.7784 | 50.1466 | 0.1159%
-76.5 | 16 | 1055.3764 | 18.5696 | 27.9965 | 40.404 | 50.5043 | 63.4177 | 0.1732%
-76 | 16 | 1022.1681 | 19.0463 | 28.9456 | 42.448 | 53.5786 | 66.548 | 0.1856%
-75.5 | 16 | 988.9599 | 15.3189 | 23.6767 | 35.0825 | 43.9307 | 57.1981 | 0.1303%
-75 | 16 | 955.7521 | 10.5503 | 15.5594 | 23.9273 | 29.7994 | 37.7874 | 0.0646%
-74.5 | 16 | 922.545 | 7.5651 | 10.9432 | 15.431 | 18.9007 | 23.9791 | 0.02654%
-74 | 16 | 889.3388 | 7.2384 | 10.1026 | 13.9504 | 16.6534 | 20.5001 | 0.01816%
-73.5 | 16 | 856.1338 | 8.5388 | 12.0498 | 16.5339 | 20.042 | 25.1188 | 0.02823%
-73 | 16 | 822.9304 | 11.4297 | 15.6038 | 22.4368 | 27.4061 | 33.2321 | 0.05309%
-72.5 | 16 | 789.729 | 14.6291 | 20.8914 | 30.0704 | 36.3254 | 45.3432 | 0.09776%
-72 | 16 | 756.5301 | 18.0976 | 26.8805 | 39.3973 | 49.7108 | 64.2354 | 0.1656%
-71.5 | 16 | 723.3341 | 19.6039 | 28.7951 | 42.486 | 53.8262 | 68.977 | 0.1899%
-71 | 16 | 690.1418 | 18.3988 | 26.164 | 35.5953 | 42.9247 | 53.4713 | 0.1459%
-70.5 | 16 | 656.9538 | 17.6873 | 24.5709 | 32.8024 | 38.7773 | 47.19 | 0.1224%
-70 | 16 | 623.7711 | 17.8312 | 24.7158 | 32.8873 | 38.8397 | 47.212 | 0.1235%
-69.5 | 16 | 590.5947 | 18.3031 | 25.574 | 33.9958 | 40.3623 | 49.369 | 0.1341%
-69 | 16 | 557.4261 | 18.5169 | 25.9962 | 34.8248 | 41.6027 | 51.2562 | 0.1411%
-68.5 | 16 | 524.2668 | 17.6675 | 24.7504 | 33.5869 | 40.1847 | 49.5973 | 0.1287%
-68 | 16 | 491.119 | 15.7736 | 21.6599 | 29.999 | 35.6919 | 43.764 | 0.09817%
-67.5 | 16 | 457.9854 | 13.9246 | 18.6859 | 26.2282 | 30.9024 | 37.4597 | 0.07069%
-67 | 16 | 424.8695 | 13.1759 | 17.624 | 24.7561 | 29.414 | 35.6492 | 0.06273%
-66.5 | 16 | 391.7759 | 14.0367 | 19.3987 | 27.8103 | 33.4927 | 41.6578 | 0.08349%
-66 | 16 | 358.7112 | 15.9061 | 22.9554 | 33.15 | 40.8802 | 52.2791 | 0.1213%
-65.5 | 16 | 325.6842 | 16.5238 | 23.9144 | 34.3555 | 42.4401 | 54.384 | 0.1306%
-65 | 16 | 292.7081 | 15.3225 | 21.1652 | 29.8589 | 35.9983 | 44.8303 | 0.09807%
-64.5 | 16 | 259.8023 | 15.4989 | 20.6471 | 28.1116 | 32.851 | 39.4406 | 0.08269%
-64 | 16 | 226.9977 | 20.5461 | 27.6524 | 36.1944 | 42.6333 | 51.6638 | 0.1618%
-63.5 | 16 | 194.3458 | 34.3867 | 46.2115 | 63.3169 | 73.9221 | 88.6524 | 0.5799%
-63 | 16 | 161.9391 | 72.4065 | 100.7651 | 143.1994 | 169.5478 | 206.71 | 2.836%
-62.5 | 16 | 129.9615 | 93.1806 | 126.2102 | 162.9488 | 188.9917 | 224.9051 | 8.384%
-62 | 16 | 98.8308 | 112.0436 | 146.4798 | 188.8329 | 220.3767 | 264.1717 | 14.39%
-61.5 | 16 | 69.6913 | 118.2465 | 151.8652 | 195.3233 | 227.631 | 272.4177 | 18.05%
-61 | 16 | 46.4553 | 109.7766 | 143.409 | 183.5541 | 213.2845 | 254.3659 | 14.77%
-60.5 | 16 | 40.8802 | 94.287 | 125.0693 | 161.0286 | 186.3366 | 221.1494 | 9.405%
-60 | 16 | 58.2765 | 79.0951 | 103.1416 | 138.2944 | 159.6731 | 189.0095 | 5.218%
-59.5 | 16 | 85.6329 | 63.7091 | 82.8464 | 112.5996 | 134.7096 | 160.1485 | 2.565%
-59 | 16 | 116.1106 | 36.2881 | 48.7176 | 66.2632 | 78.0414 | 94.5579 | 0.6531%
-90 | 16.5 | 1950.1004 | 78.1644 | 104.7 | 144.5703 | 172.1069 | 211.177 | 3.697%
-89.5 | 16.5 | 1916.9952 | 91.2919 | 126.4155 | 167.0321 | 196.6055 | 238.0494 | 6.25%
-89 | 16.5 | 1883.8878 | 111.202 | 149.1693 | 196.6338 | 232.6125 | 283.3095 | 10.56%
-88.5 | 16.5 | 1850.7785 | 130.6626 | 164.8713 | 216.0492 | 254.6617 | 304.5113 | 21.03%
-88 | 16.5 | 1817.6672 | 143.0165 | 179.7116 | 234.668 | 276.016 | 320.5612 | 31.85%
-87.5 | 16.5 | 1784.5541 | 163.8895 | 210.0824 | 280.7828 | 320.9744 | 368.072 | 46.19%
-87 | 16.5 | 1751.4394 | 174.5872 | 223.0806 | 296.4324 | 331.7389 | 378.5655 | 69.43%
-86.5 | 16.5 | 1718.3231 | 177.2696 | 223.4546 | 292.861 | 326.4542 | 369.5168 | 94.9%
-86 | 16.5 | 1685.2053 | 189.0716 | 241.822 | 312.3887 | 349.4563 | 398.5972 | 114.2%
-85.5 | 16.5 | 1652.0863 | 175.988 | 222.6809 | 293.1411 | 327.6575 | 372.2424 | 83.85%
-85 | 16.5 | 1618.9661 | 160.5836 | 203.498 | 268.3639 | 309.5877 | 351.9962 | 49.51%
-84.5 | 16.5 | 1585.8449 | 137.3793 | 174.6372 | 231.1454 | 274.1174 | 321.4886 | 22.99%
-84 | 16.5 | 1552.7227 | 101.1786 | 138.8264 | 181.0087 | 212.7083 | 257.0524 | 8.733%
-83.5 | 16.5 | 1519.5999 | 80.402 | 110.8 | 151.2224 | 177.0715 | 213.0906 | 4.296%
-83 | 16.5 | 1486.4765 | 66.9627 | 90.721 | 129.3507 | 151.9903 | 182.9094 | 2.52%
-82.5 | 16.5 | 1453.3527 | 59.3726 | 77.8459 | 106.8263 | 129.5017 | 153.4155 | 2.041%
-82 | 16.5 | 1420.2287 | 59.2415 | 77.6753 | 106.5944 | 129.2221 | 153.1035 | 2.03%
-81.5 | 16.5 | 1387.1047 | 53.2028 | 71.5654 | 97.7483 | 118.1592 | 143.0662 | 1.535%
-81 | 16.5 | 1353.981 | 38.4361 | 53.2022 | 71.093 | 83.3977 | 100.5779 | 0.7723%
-80.5 | 16.5 | 1320.8576 | 28.4754 | 37.2769 | 51.061 | 60.7058 | 71.0627 | 0.3603%
-80 | 16.5 | 1287.7349 | 23.7329 | 32.1504 | 44.44 | 54.1108 | 66.218 | 0.2422%
-79.5 | 16.5 | 1254.6132 | 24.3663 | 33.8977 | 48.8945 | 60.4065 | 73.8875 | 0.2682%
-79 | 16.5 | 1221.4927 | 28.3697 | 40.9441 | 61.5581 | 74.512 | 93.2284 | 0.3745%
-78.5 | 16.5 | 1188.3737 | 28.0429 | 39.9531 | 59.8051 | 71.9585 | 89.404 | 0.3642%
-78 | 16.5 | 1155.2566 | 24.3772 | 33.6159 | 47.8613 | 59.0062 | 70.8643 | 0.2653%
-77.5 | 16.5 | 1122.1417 | 21.5029 | 29.882 | 40.7159 | 49.1454 | 60.2749 | 0.1987%
-77 | 16.5 | 1089.0295 | 23.4779 | 32.3004 | 45.1194 | 55.2906 | 66.3485 | 0.2423%
-76.5 | 16.5 | 1055.9204 | 26.5732 | 36.4968 | 52.8751 | 63.6636 | 76.5167 | 0.319%
-76 | 16.5 | 1022.8149 | 25.7796 | 35.7395 | 52.3313 | 63.4868 | 76.693 | 0.3018%
-75.5 | 16.5 | 989.7137 | 19.1855 | 28.5124 | 40.9031 | 50.9424 | 63.564 | 0.1798%
-75 | 16.5 | 956.6173 | 13.3074 | 19.1736 | 28.4766 | 34.6892 | 43.728 | 0.08745%
-74.5 | 16.5 | 923.5264 | 10.2578 | 14.1699 | 19.965 | 24.5944 | 30.014 | 0.04235%
-74 | 16.5 | 890.442 | 10.6201 | 14.3988 | 20.049 | 24.5208 | 29.6718 | 0.04123%
-73.5 | 16.5 | 857.3649 | 13.4479 | 18.5301 | 26.6594 | 31.6479 | 38.704 | 0.07402%
-73 | 16.5 | 824.2962 | 19.2285 | 27.8715 | 39.3653 | 48.5646 | 61.1004 | 0.1726%
-72.5 | 16.5 | 791.2372 | 28.7523 | 41.8989 | 63.3251 | 77.6174 | 98.5526 | 0.3835%
-72 | 16.5 | 758.1895 | 34.7622 | 51.3839 | 73.9624 | 90.4011 | 114.4064 | 0.5617%
-71.5 | 16.5 | 725.1546 | 35.848 | 52.3262 | 74.232 | 90.2276 | 113.4443 | 0.6031%
-71 | 16.5 | 692.1347 | 33.5708 | 47.3893 | 67.6405 | 81.5468 | 101.5514 | 0.5253%
-70.5 | 16.5 | 659.1322 | 31.3824 | 42.4589 | 59.8138 | 69.9771 | 84.1256 | 0.4615%
-70 | 16.5 | 626.1502 | 31.3346 | 42.1441 | 59.1792 | 68.9185 | 82.4091 | 0.4609%
-69.5 | 16.5 | 593.1921 | 32.7019 | 44.7423 | 62.8143 | 74.0931 | 89.9358 | 0.506%
-69 | 16.5 | 560.2625 | 32.7447 | 45.0035 | 63.3536 | 74.9545 | 91.3032 | 0.5062%
-68.5 | 16.5 | 527.3668 | 30.1405 | 40.9208 | 58.4072 | 68.9366 | 83.7363 | 0.4171%
-68 | 16.5 | 494.5122 | 25.8327 | 34.0376 | 46.9789 | 57.1507 | 68.6111 | 0.2848%
-67.5 | 16.5 | 461.7075 | 22.0274 | 29.8398 | 40.4661 | 48.7033 | 60.0616 | 0.2019%
-67 | 16.5 | 428.9644 | 21.6286 | 29.7332 | 41.0393 | 49.9261 | 61.9709 | 0.2009%
-66.5 | 16.5 | 396.2983 | 26.7307 | 38.2653 | 58.1768 | 71.5144 | 91.1132 | 0.3304%
-66 | 16.5 | 363.7304 | 33.7246 | 51.1833 | 76.197 | 95.2082 | 123.6472 | 0.5159%
-65.5 | 16.5 | 331.2897 | 37.5773 | 58.3885 | 84.9398 | 106.6896 | 136.7739 | 0.638%
-65 | 16.5 | 299.0178 | 29.9435 | 43.5032 | 65.2937 | 80.5867 | 103.1577 | 0.411%
-64.5 | 16.5 | 266.9763 | 22.9492 | 30.6613 | 41.4826 | 49.8553 | 61.1093 | 0.2174%
-64 | 16.5 | 235.2594 | 27.0076 | 34.9089 | 47.1124 | 56.5363 | 67.279 | 0.3097%
-63.5 | 16.5 | 204.0188 | 47.2011 | 65.971 | 92.3788 | 113.3725 | 140.9916 | 1.065%
-63 | 16.5 | 173.5124 | 70.1958 | 92.1 | 126.4886 | 147.4158 | 174.5874 | 3.397%
-62.5 | 16.5 | 144.2068 | 92.2412 | 123.1639 | 159.9384 | 185.5366 | 220.8443 | 8.229%
-62 | 16.5 | 117.0082 | 114.8873 | 148.8988 | 191.6619 | 223.473 | 267.5949 | 16.07%
-61.5 | 16.5 | 93.7686 | 117.992 | 151.0388 | 193.3219 | 224.6359 | 267.9057 | 19.23%
-61 | 16.5 | 78.1057 | 107.8526 | 140.8856 | 179.3122 | 207.6434 | 246.6454 | 14.99%
-60.5 | 16.5 | 74.9321 | 89.943 | 118.0583 | 153.4 | 176.9232 | 209.1643 | 8.356%
-60 | 16.5 | 85.6474 | 73.9287 | 96.0765 | 130.487 | 150.9827 | 178.9776 | 4.155%
-59.5 | 16.5 | 106.1248 | 51.7122 | 68.5929 | 91.8763 | 109.7495 | 134.4126 | 1.509%
-59 | 16.5 | 131.8931 | 29.048 | 37.8284 | 51.5011 | 61.3546 | 73.3376 | 0.3739%
-90 | 17 | 1949.1841 | 48.9029 | 66.915 | 92.24 | 112.1254 | 140.968 | 1.178%
-89.5 | 17 | 1916.1519 | 48.4332 | 65.018 | 86.1873 | 102.305 | 125.1009 | 1.325%
-89 | 17 | 1883.1185 | 61.1266 | 79.1852 | 107.1447 | 128.7797 | 154.2939 | 2.291%
-88.5 | 17 | 1850.084 | 82.4762 | 113.9571 | 156.3626 | 185.4348 | 226.5117 | 4.176%
-88 | 17 | 1817.0486 | 101.5723 | 138.6088 | 180.7862 | 212.4906 | 256.8513 | 8.905%
-87.5 | 17 | 1784.0125 | 131.7055 | 169.64 | 228.0058 | 272.9314 | 324.9611 | 16.41%
-87 | 17 | 1750.9758 | 161.7568 | 210.1278 | 285.2462 | 327.203 | 379.3628 | 35.43%
-86.5 | 17 | 1717.9389 | 178.2646 | 228.6526 | 302.1361 | 339.1118 | 388.3087 | 73.26%
-86 | 17 | 1684.9017 | 222.5347 | 298.2211 | 369.8275 | 421.5461 | 491.5272 | 155.1%
-85.5 | 17 | 1651.8647 | 200.3615 | 260.9206 | 332.0941 | 374.1537 | 430.347 | 126.9%
-85 | 17 | 1618.8279 | 187.4529 | 242.8982 | 316.01 | 354.9491 | 406.8007 | 91.27%
-84.5 | 17 | 1585.7917 | 187.9586 | 254.4661 | 336.7315 | 386.4747 | 454.2906 | 50.05%
-84 | 17 | 1552.7563 | 146.1252 | 189.9801 | 258.1471 | 305.8122 | 354.248 | 22.57%
-83.5 | 17 | 1519.7219 | 122.4651 | 160.6046 | 213.9336 | 254.6928 | 306.867 | 13.54%
-83 | 17 | 1486.6889 | 113.8283 | 156.5642 | 215.2616 | 261.2578 | 317.6495 | 8.073%
-82.5 | 17 | 1453.6575 | 107.5602 | 147.3298 | 196.7267 | 234.5528 | 288.3111 | 8.325%
-82 | 17 | 1420.6282 | 110.4959 | 149.0501 | 196.8056 | 233.0528 | 284.185 | 10.1%
-81.5 | 17 | 1387.6011 | 109.8014 | 152.0402 | 208.0137 | 251.7055 | 308.9256 | 7.411%
-81 | 17 | 1354.5769 | 75.66 | 103.6497 | 144.1911 | 169.3034 | 204.4009 | 3.5%
-80.5 | 17 | 1321.5558 | 46.2029 | 63.6613 | 85.1136 | 101.5572 | 124.9466 | 1.141%
-80 | 17 | 1288.5383 | 36.7466 | 51.8489 | 73.2178 | 89.0776 | 112.1206 | 0.6285%
-79.5 | 17 | 1255.5249 | 43.6828 | 64.9401 | 95.0301 | 119.7931 | 150.0833 | 0.8399%
-79 | 17 | 1222.5162 | 52.6439 | 74.8911 | 108.8567 | 134.9622 | 162.786 | 1.28%
-78.5 | 17 | 1189.5128 | 55.4978 | 80.252 | 121.5922 | 149.4528 | 186.0771 | 1.31%
-78 | 17 | 1156.5153 | 46.6525 | 68.0004 | 98.0592 | 122.5133 | 151.4001 | 0.9844%
-77.5 | 17 | 1123.5245 | 38.2746 | 55.5292 | 76.6155 | 92.4312 | 115.2 | 0.7095%
-77 | 17 | 1090.5412 | 39.1063 | 57.3134 | 79.3728 | 96.5212 | 121.4239 | 0.7305%
-76.5 | 17 | 1057.5663 | 42.0644 | 62.5139 | 89.4222 | 111.1749 | 140.4487 | 0.8038%
-76 | 17 | 1024.6008 | 34.9888 | 51.4577 | 73.7594 | 89.9556 | 113.5501 | 0.5705%
-75.5 | 17 | 991.646 | 23.7362 | 33.0636 | 47.2307 | 58.5185 | 70.147 | 0.2539%
-75 | 17 | 958.703 | 15.8281 | 22.3934 | 31.368 | 37.6554 | 46.6577 | 0.1079%
-74.5 | 17 | 925.7734 | 13.8106 | 18.825 | 26.7501 | 31.7268 | 38.7592 | 0.07474%
-74 | 17 | 892.8589 | 15.7233 | 21.91 | 30.7387 | 36.9558 | 45.8725 | 0.104%
-73.5 | 17 | 859.9614 | 21.5959 | 30.1938 | 42.2695 | 51.8675 | 63.8666 | 0.2069%
-73 | 17 | 827.0831 | 34.416 | 50.4757 | 73.1993 | 89.8358 | 114.2388 | 0.5448%
-72.5 | 17 | 794.2267 | 48.5444 | 70.6316 | 103.5931 | 130.7673 | 160.6712 | 1.035%
-72 | 17 | 761.3952 | 60.5872 | 84.7312 | 125.3754 | 150.4644 | 183.6161 | 1.73%
-71.5 | 17 | 728.5921 | 64.6253 | 89.8495 | 131.7371 | 155.1492 | 187.9789 | 2.111%
-71 | 17 | 695.8218 | 59.222 | 81.5253 | 118.4283 | 144.5883 | 178.0617 | 1.651%
-70.5 | 17 | 663.0892 | 55.6925 | 75.1216 | 105.0357 | 128.7888 | 155.4397 | 1.59%
-70 | 17 | 630.4006 | 55.0314 | 73.8827 | 102.2875 | 124.6676 | 150.7175 | 1.596%
-69.5 | 17 | 597.7632 | 55.124 | 73.944 | 102.3283 | 124.6846 | 151.0551 | 1.6%
-69 | 17 | 565.1862 | 53.5526 | 72.2955 | 99.8007 | 121.4225 | 147.337 | 1.503%
-68.5 | 17 | 532.6808 | 47.3047 | 65.4994 | 89.9551 | 109.1021 | 135.503 | 1.118%
-68 | 17 | 500.2614 | 38.3365 | 52.5917 | 71.2593 | 84.454 | 103.0842 | 0.7407%
-67.5 | 17 | 467.9458 | 35.9054 | 49.0125 | 67.6295 | 80.436 | 98.588 | 0.623%
-67 | 17 | 435.7575 | 36.1787 | 49.7492 | 68.854 | 82.1868 | 101.159 | 0.6302%
-66.5 | 17 | 403.7271 | 41.372 | 58.6731 | 79.9159 | 96.4394 | 120.2343 | 0.8445%
-66 | 17 | 371.8956 | 48.2741 | 66.6462 | 91.3108 | 110.585 | 136.7287 | 1.182%
-65.5 | 17 | 340.3191 | 50.5624 | 69.0755 | 94.8109 | 114.9505 | 140.8664 | 1.321%
-65 | 17 | 309.076 | 46.1086 | 64.2218 | 88.0494 | 106.6795 | 133.0527 | 1.056%
-64.5 | 17 | 278.2787 | 35.2525 | 47.5866 | 65.5571 | 77.7371 | 94.9445 | 0.5985%
-64 | 17 | 248.0935 | 34.0594 | 44.9138 | 61.2061 | 71.4833 | 85.7636 | 0.5633%
-63.5 | 17 | 218.7743 | 53.7662 | 71.0559 | 95.8195 | 114.9303 | 139.8893 | 1.639%
-63 | 17 | 190.721 | 78.589 | 103.7572 | 140.3919 | 163.0092 | 194.2363 | 4.692%
-62.5 | 17 | 164.5824 | 105.104 | 139.485 | 179.4924 | 209.2469 | 250.5083 | 11.85%
-62 | 17 | 141.4243 | 126.9049 | 159.9371 | 206.7971 | 241.78 | 290.446 | 21.77%
-61.5 | 17 | 122.943 | 123.9278 | 156.2825 | 200.2559 | 232.8502 | 277.9224 | 22.86%
-61 | 17 | 111.4892 | 111.9635 | 145.118 | 185.2357 | 214.8817 | 255.7725 | 16.49%
-60.5 | 17 | 109.2949 | 93.098 | 123.8415 | 160.6379 | 186.4759 | 222.1411 | 8.507%
-60 | 17 | 116.883 | 64.064 | 82.3488 | 110.4193 | 131.7932 | 155.7482 | 2.778%
-59.5 | 17 | 132.5843 | 36.6172 | 48.4798 | 65.2167 | 76.2819 | 91.6822 | 0.68%
-59 | 17 | 153.9358 | 22.1094 | 29.2504 | 38.6313 | 45.753 | 55.8007 | 0.1915%
-90 | 17.5 | 1948.8296 | 29.8681 | 39.1962 | 53.8442 | 64.3292 | 78.3356 | 0.3986%
-89.5 | 17.5 | 1915.8819 | 29.3607 | 37.7507 | 50.6347 | 60.0113 | 70.7316 | 0.383%
-89 | 17.5 | 1882.9342 | 33.2445 | 43.4872 | 59.1362 | 67.9283 | 79.9256 | 0.5423%
-88.5 | 17.5 | 1849.9868 | 40.9794 | 55.4877 | 71.6335 | 82.912 | 98.4303 | 0.977%
-88 | 17.5 | 1817.0399 | 56.1559 | 71.9241 | 94.6119 | 111.7812 | 134.6921 | 2.071%
-87.5 | 17.5 | 1784.0938 | 71.9836 | 93.3796 | 126.5564 | 145.7981 | 170.1198 | 4.11%
-87 | 17.5 | 1751.1488 | 104.8542 | 141.077 | 182.8322 | 214.0611 | 257.5713 | 10.59%
-86.5 | 17.5 | 1718.2051 | 143.3537 | 180.6937 | 236.8049 | 279.1427 | 323.7282 | 30.66%
-86 | 17.5 | 1685.2631 | 173.9628 | 226.577 | 304.0105 | 344.3313 | 398.5134 | 50.45%
-85.5 | 17.5 | 1652.323 | 176.3481 | 227.2247 | 301.938 | 339.5451 | 389.6877 | 64.62%
-85 | 17.5 | 1619.3853 | 170.1008 | 218.212 | 291.9102 | 328.4537 | 375.3775 | 57.15%
-84.5 | 17.5 | 1586.4503 | 168.2725 | 220.541 | 299.9929 | 340.1268 | 394.1177 | 40.19%
-84 | 17.5 | 1553.5184 | 150.0204 | 193.6216 | 260.8546 | 306.6529 | 352.7563 | 27.86%
-83.5 | 17.5 | 1520.59 | 138.8708 | 177.5642 | 236.6239 | 281.7779 | 327.6605 | 22.44%
-83 | 17.5 | 1487.6656 | 138.2631 | 179.6776 | 244.0199 | 293.9532 | 341.2768 | 17.94%
-82.5 | 17.5 | 1454.7457 | 143.4434 | 184.2571 | 246.8667 | 294.9384 | 339.3266 | 23.72%
-82 | 17.5 | 1421.8307 | 151.4398 | 193.502 | 257.6554 | 302.7209 | 346.1606 | 32.8%
-81.5 | 17.5 | 1388.9214 | 155.5063 | 203.2654 | 277.9379 | 321.9742 | 373.6464 | 28.09%
-81 | 17.5 | 1356.0183 | 113.4249 | 151.0409 | 198.3729 | 234.1476 | 284.4347 | 11.68%
-80.5 | 17.5 | 1323.1221 | 71.3165 | 96.0967 | 134.7473 | 157.2734 | 188.5522 | 3.13%
-80 | 17.5 | 1290.2336 | 50.9163 | 69.7074 | 96.0343 | 116.6972 | 143.3444 | 1.324%
-79.5 | 17.5 | 1257.3535 | 62.2344 | 86.9651 | 128.5604 | 153.2471 | 187.13 | 1.853%
-79 | 17.5 | 1224.4828 | 71.9977 | 101.4898 | 144.6648 | 170.7556 | 207.431 | 2.779%
-78.5 | 17.5 | 1191.6225 | 77.0205 | 111.4503 | 157.8877 | 189.2944 | 234.2011 | 2.973%
-78 | 17.5 | 1158.7737 | 76.9164 | 111.2116 | 156.9805 | 187.4619 | 230.857 | 3.042%
-77.5 | 17.5 | 1125.9376 | 65.1227 | 89.5368 | 129.8774 | 152.4023 | 183.2784 | 2.254%
-77 | 17.5 | 1093.1155 | 67.68 | 95.2979 | 138.809 | 164.9093 | 201.8585 | 2.266%
-76.5 | 17.5 | 1060.309 | 66.1873 | 91.6377 | 133.0718 | 155.9512 | 187.862 | 2.317%
-76 | 17.5 | 1027.5199 | 50.9238 | 72.4991 | 104.3644 | 130.2527 | 157.0941 | 1.203%
-75.5 | 17.5 | 994.7499 | 32.2306 | 47.6736 | 72.3144 | 91.42 | 120.368 | 0.4632%
-75 | 17.5 | 962.0014 | 19.9248 | 27.6943 | 37.4324 | 44.9615 | 55.7485 | 0.1663%
-74.5 | 17.5 | 929.2768 | 19.1288 | 26.802 | 36.6452 | 44.3246 | 55.4115 | 0.1565%
-74 | 17.5 | 896.5789 | 24.797 | 33.9083 | 48.2905 | 59.5143 | 72.7057 | 0.2723%
-73.5 | 17.5 | 863.911 | 36.8838 | 54.7046 | 80.5316 | 101.1908 | 131.981 | 0.6002%
-73 | 17.5 | 831.2768 | 49.4728 | 68.1334 | 93.6077 | 113.5581 | 139.5018 | 1.25%
-72.5 | 17.5 | 798.6807 | 62.6878 | 83.5266 | 116.7982 | 139.897 | 166.8373 | 2.234%
-72 | 17.5 | 766.1278 | 66.726 | 88.5622 | 123.2785 | 145.0533 | 172.1346 | 2.765%
-71.5 | 17.5 | 733.6239 | 71.0041 | 94.522 | 131.7522 | 152.4596 | 180.9441 | 3.331%
-71 | 17.5 | 701.1763 | 71.2822 | 93.9297 | 129.6532 | 150.7124 | 179.2752 | 3.451%
-70.5 | 17.5 | 668.7932 | 71.2097 | 93.6404 | 128.942 | 150.2249 | 178.9245 | 3.447%
-70 | 17.5 | 636.4848 | 70.0543 | 91.9853 | 126.445 | 147.9166 | 176.0831 | 3.298%
-69.5 | 17.5 | 604.2632 | 68.293 | 89.4983 | 122.7469 | 144.4727 | 171.8574 | 3.076%
-69 | 17.5 | 572.1433 | 66.2478 | 86.6917 | 118.6958 | 140.7242 | 167.3825 | 2.817%
-68.5 | 17.5 | 540.1435 | 61.2259 | 79.5728 | 108.0797 | 130.2048 | 154.7319 | 2.291%
-68 | 17.5 | 508.2866 | 56.9905 | 74.3205 | 100.6174 | 120.9747 | 146.0223 | 1.896%
-67.5 | 17.5 | 476.6016 | 53.723 | 71.2134 | 96.364 | 115.8265 | 141.0806 | 1.613%
-67 | 17.5 | 445.1254 | 52.149 | 69.7218 | 94.4317 | 113.5669 | 138.9457 | 1.486%
-66.5 | 17.5 | 413.9058 | 56.336 | 74.489 | 102.0942 | 123.6725 | 149.5932 | 1.749%
-66 | 17.5 | 383.0058 | 59.9836 | 78.6173 | 107.8375 | 130.6924 | 156.1001 | 2.069%
-65.5 | 17.5 | 352.5096 | 63.4477 | 83.3976 | 114.7803 | 137.5216 | 164.3367 | 2.405%
-65 | 17.5 | 322.5321 | 60.2244 | 78.6278 | 107.3648 | 129.7619 | 155.1624 | 2.127%
-64.5 | 17.5 | 293.2325 | 51.1588 | 67.9422 | 91.0272 | 108.7516 | 133.4552 | 1.464%
-64 | 17.5 | 264.8362 | 45.0153 | 60.2922 | 78.9207 | 92.9633 | 112.6584 | 1.159%
-63.5 | 17.5 | 237.6675 | 59.1507 | 75.9847 | 101.8102 | 121.64 | 146.0269 | 2.204%
-63 | 17.5 | 212.1984 | 81.7525 | 107.957 | 144.6389 | 167.856 | 199.8936 | 5.395%
-62.5 | 17.5 | 189.1171 | 105.3973 | 139.3563 | 178.6782 | 207.8391 | 248.1801 | 12.52%
-62 | 17.5 | 169.4028 | 123.2406 | 156.1826 | 200.883 | 234.1152 | 280.1845 | 21.09%
-61.5 | 17.5 | 154.3509 | 124.8493 | 157.2863 | 201.9148 | 235.0432 | 280.9102 | 22.86%
-61 | 17.5 | 145.4169 | 108.671 | 142.2308 | 181.9845 | 211.4171 | 252.0779 | 14.34%
-60.5 | 17.5 | 143.7459 | 74.915 | 96.7838 | 130.542 | 150.3397 | 177.2511 | 4.576%
-60 | 17.5 | 149.5816 | 44.0165 | 58.9417 | 76.1723 | 89.0306 | 106.9121 | 1.145%
-59.5 | 17.5 | 162.1153 | 27.3481 | 34.8639 | 46.2982 | 55.0164 | 65.5183 | 0.3145%
-59 | 17.5 | 179.9529 | 16.6459 | 21.9479 | 29.2586 | 34.1035 | 40.821 | 0.09217%
-90 | 18 | 1949.0371 | 19.1898 | 26.2014 | 34.6935 | 41.1533 | 50.283 | 0.1432%
-89.5 | 18 | 1916.1853 | 18.6814 | 25.2617 | 32.4855 | 37.7079 | 44.9159 | 0.1226%
-89 | 18 | 1883.3352 | 21.2211 | 28.2233 | 36.4931 | 42.6669 | 51.2556 | 0.1688%
-88.5 | 18 | 1850.487 | 26.5557 | 33.7797 | 44.744 | 53.0869 | 63.5501 | 0.2901%
-88 | 18 | 1817.6412 | 31.8328 | 41.1629 | 55.5799 | 64.0735 | 74.5412 | 0.4846%
-87.5 | 18 | 1784.7981 | 40.3706 | 54.1939 | 69.6201 | 79.901 | 93.9164 | 0.9697%
-87 | 18 | 1751.9581 | 56.0713 | 70.8684 | 91.6235 | 107.1169 | 128.6691 | 2.258%
-86.5 | 18 | 1719.1216 | 76.9674 | 101.283 | 136.9551 | 156.9742 | 184.2264 | 4.844%
-86 | 18 | 1686.289 | 110.2949 | 148.1348 | 195.1464 | 230.764 | 280.9311 | 10.37%
-85.5 | 18 | 1653.4608 | 124.5163 | 160.6207 | 211.4142 | 249.8712 | 301.2594 | 16.21%
-85 | 18 | 1620.6376 | 130.3389 | 164.905 | 216.5168 | 255.517 | 305.2668 | 20.41%
-84.5 | 18 | 1587.8198 | 128.2636 | 165.2344 | 219.9868 | 261.8169 | 312.5785 | 16.48%
-84 | 18 | 1555.0081 | 117.5503 | 155.2573 | 204.8008 | 242.376 | 295.3384 | 12.49%
-83.5 | 18 | 1522.2029 | 111.3211 | 148.9736 | 195.0292 | 229.7507 | 278.4533 | 11.36%
-83 | 18 | 1489.4052 | 125.7086 | 162.8948 | 216.409 | 257.2242 | 308.5847 | 15.44%
-82.5 | 18 | 1456.6154 | 144.6367 | 183.928 | 243.5434 | 288.8932 | 332.3669 | 28.18%
-82 | 18 | 1423.8345 | 162.9352 | 207.7799 | 276.0298 | 315.8399 | 359.484 | 49.88%
-81.5 | 18 | 1391.0632 | 171.2079 | 221.8538 | 298.5014 | 335.944 | 385.9099 | 51.87%
-81 | 18 | 1358.3026 | 140.7668 | 178.2394 | 234.8294 | 277.7074 | 323.0927 | 26.83%
-80.5 | 18 | 1325.5536 | 93.1984 | 129.7636 | 168.2775 | 196.7031 | 236.2382 | 7.298%
-80 | 18 | 1292.8173 | 64.314 | 85.6452 | 119.6819 | 142.4264 | 169.8896 | 2.412%
-79.5 | 18 | 1260.095 | 65.0142 | 89.0973 | 128.7496 | 151.9899 | 183.5939 | 2.23%
-79 | 18 | 1227.3879 | 73.3154 | 101.9013 | 143.5844 | 168.6097 | 203.5901 | 3.09%
-78.5 | 18 | 1194.6977 | 81.3117 | 115.7201 | 159.4741 | 189.2198 | 231.2713 | 3.826%
-78 | 18 | 1162.0258 | 77.1702 | 107.066 | 148.3258 | 174.0197 | 209.8993 | 3.66%
-77.5 | 18 | 1129.3742 | 77.6858 | 107.8924 | 149.176 | 175.0209 | 211.112 | 3.733%
-77 | 18 | 1096.7449 | 84.2137 | 119.5421 | 162.1636 | 191.6609 | 233.1841 | 4.433%
-76.5 | 18 | 1064.1401 | 91.0467 | 131.9448 | 175.2137 | 208.2032 | 254.9162 | 5.302%
-76 | 18 | 1031.5623 | 51.5877 | 69.3161 | 93.4363 | 112.045 | 136.6366 | 1.473%
-75.5 | 18 | 999.0146 | 35.308 | 48.2978 | 66.5877 | 78.7125 | 95.7835 | 0.6066%
-75 | 18 | 966.5 | 26.4285 | 34.453 | 46.963 | 56.6996 | 68.0202 | 0.2964%
-74.5 | 18 | 934.0224 | 26.6729 | 35.267 | 48.8735 | 59.3389 | 71.847 | 0.3076%
-74 | 18 | 901.5859 | 34.1813 | 46.9083 | 65.6571 | 78.315 | 96.3126 | 0.5519%
-73.5 | 18 | 869.1953 | 47.1859 | 64.9228 | 88.1418 | 106.1563 | 131.8293 | 1.143%
-73 | 18 | 836.8562 | 59.8894 | 78.2867 | 107.0529 | 129.4982 | 154.5582 | 2.092%
-72.5 | 18 | 804.575 | 67.3124 | 88.6003 | 122.1385 | 144.3109 | 172.246 | 2.865%
-72 | 18 | 772.3592 | 70.1765 | 92.1929 | 126.8061 | 148.2961 | 176.6165 | 3.304%
-71.5 | 18 | 740.2176 | 75.2688 | 99.3053 | 135.7372 | 157.5953 | 187.7723 | 4.071%
-71 | 18 | 708.1604 | 82.1885 | 109.5313 | 147.2271 | 171.4227 | 204.9307 | 5.207%
-70.5 | 18 | 676.2 | 83.0386 | 110.605 | 148.1827 | 172.4147 | 205.9476 | 5.438%
-70 | 18 | 644.3509 | 80.1271 | 106.3027 | 143.5092 | 166.8791 | 199.1981 | 4.884%
-69.5 | 18 | 612.6308 | 77.1995 | 102.2116 | 139.185 | 161.9434 | 193.4364 | 4.317%
-69 | 18 | 581.0608 | 74.1015 | 97.6427 | 133.891 | 155.584 | 185.5606 | 3.863%
-68.5 | 18 | 549.6673 | 72.7059 | 95.4269 | 131.0943 | 152.086 | 181.042 | 3.715%
-68 | 18 | 518.4823 | 73.5709 | 96.7122 | 132.6343 | 154.0045 | 183.5103 | 3.822%
-67.5 | 18 | 487.5462 | 71.8221 | 94.1589 | 129.1963 | 150.3611 | 178.9774 | 3.59%
-67 | 18 | 456.9097 | 67.5337 | 88.1438 | 120.3158 | 142.0902 | 168.9427 | 3.022%
-66.5 | 18 | 426.6376 | 65.1915 | 85.2191 | 116.5352 | 138.7805 | 165.4053 | 2.678%
-66 | 18 | 396.8134 | 64.0143 | 83.1725 | 112.9308 | 134.9635 | 160.3984 | 2.613%
-65.5 | 18 | 367.5466 | 69.4719 | 90.3401 | 122.7845 | 144.2207 | 171.4025 | 3.355%
-65 | 18 | 338.9816 | 73.3925 | 95.2871 | 129.2683 | 150.108 | 178.2868 | 4.035%
-64.5 | 18 | 311.312 | 70.2299 | 90.2255 | 120.9043 | 141.699 | 167.5408 | 3.734%
-64 | 18 | 284.799 | 63.4932 | 80.4811 | 106.1656 | 125.6459 | 148.7795 | 2.954%
-63.5 | 18 | 259.7971 | 64.8731 | 82.6662 | 109.7238 | 130.3458 | 153.5904 | 3.045%
-63 | 18 | 236.7857 | 77.2107 | 100.1883 | 134.7163 | 155.3842 | 183.7136 | 4.918%
-62.5 | 18 | 216.401 | 93.649 | 124.2362 | 160.2501 | 185.4355 | 220.0797 | 9.152%
-62 | 18 | 199.4499 | 105.3035 | 138.7821 | 177.3608 | 205.8966 | 245.2873 | 13.06%
-61.5 | 18 | 186.8695 | 99.6387 | 132.727 | 169.1864 | 196.0997 | 233.1872 | 11.18%
-61 | 18 | 179.5807 | 80.1157 | 104.5464 | 139.8291 | 161.5418 | 191.3559 | 5.421%
-60.5 | 18 | 178.2339 | 48.5959 | 63.7697 | 82.3997 | 96.3005 | 115.6301 | 1.499%
-60 | 18 | 182.9605 | 30.5077 | 39.0214 | 52.0212 | 61.1491 | 71.9433 | 0.4239%
-59.5 | 18 | 193.3153 | 19.1922 | 25.6737 | 33.1013 | 38.6046 | 46.2397 | 0.1302%
-59 | 18 | 208.4614 | 12.7995 | 16.3307 | 21.708 | 25.8087 | 30.4046 | 0.04337%
-90 | 18.5 | 1949.8066 | 13.4714 | 17.6294 | 24.1387 | 28.6011 | 34.4331 | 0.05841%
-89.5 | 18.5 | 1917.062 | 13.8792 | 18.3895 | 25.5467 | 30.6351 | 37.8706 | 0.06964%
-89 | 18.5 | 1884.321 | 16.1059 | 22.2138 | 32.0584 | 39.9308 | 51.6668 | 0.1172%
-88.5 | 18.5 | 1851.5841 | 18.8127 | 26.3493 | 37.0804 | 45.6448 | 58.2597 | 0.1574%
-88 | 18.5 | 1818.8518 | 21.8623 | 29.6063 | 40.0302 | 48.0914 | 59.7052 | 0.1979%
-87.5 | 18.5 | 1786.1245 | 26.3393 | 33.3211 | 43.8544 | 51.8288 | 61.9265 | 0.2816%
-87 | 18.5 | 1753.4028 | 31.5485 | 40.7317 | 54.8975 | 63.2167 | 72.9795 | 0.4753%
-86.5 | 18.5 | 1720.6871 | 38.7276 | 51.798 | 67.313 | 77.0415 | 90.2643 | 0.8593%
-86 | 18.5 | 1687.9782 | 46.0428 | 61.561 | 78.1282 | 90.3153 | 107.0609 | 1.387%
-85.5 | 18.5 | 1655.2767 | 52.0007 | 67.3959 | 86.7696 | 101.1838 | 121.1791 | 1.845%
-85 | 18.5 | 1622.5831 | 59.2796 | 75.6393 | 100.5534 | 119.565 | 141.9153 | 2.352%
-84.5 | 18.5 | 1589.8984 | 59.9267 | 76.9618 | 103.0885 | 123.1448 | 145.3552 | 2.351%
-84 | 18.5 | 1557.2232 | 69.9618 | 97.4766 | 140.4254 | 167.7904 | 206.7737 | 2.457%
-83.5 | 18.5 | 1524.5584 | 75.765 | 105.3035 | 147.6739 | 174.7712 | 212.9721 | 3.252%
-83 | 18.5 | 1491.9049 | 92.3894 | 132.1169 | 178.9203 | 215.1615 | 267.1525 | 4.941%
-82.5 | 18.5 | 1459.2637 | 138.9276 | 181.0591 | 246.7204 | 297.0023 | 344.8204 | 17.75%
-82 | 18.5 | 1426.636 | 159.2949 | 205.6031 | 277.0147 | 318.8038 | 366.2519 | 37.25%
-81.5 | 18.5 | 1394.0228 | 187.868 | 254.3024 | 336.5502 | 386.2358 | 453.9673 | 50.03%
-81 | 18.5 | 1361.4255 | 155.0752 | 201.7709 | 274.4144 | 318.5118 | 368.593 | 29.29%
-80.5 | 18.5 | 1328.8454 | 116.0575 | 155.014 | 206.2875 | 245.4459 | 299.1866 | 11.04%
-80 | 18.5 | 1296.2842 | 79.2842 | 112.8067 | 159.1135 | 191.5544 | 238.1499 | 3.192%
-79.5 | 18.5 | 1263.7434 | 64.1795 | 87.1294 | 124.5289 | 148.2778 | 179.2108 | 2.196%
-79 | 18.5 | 1231.225 | 71.7733 | 99.2114 | 140.6663 | 165.5952 | 200.5358 | 2.886%
-78.5 | 18.5 | 1198.7309 | 87.9046 | 127.8404 | 175.4567 | 211.7835 | 264.1096 | 4.094%
-78 | 18.5 | 1166.2634 | 92.2481 | 132.5856 | 177.6487 | 212.2499 | 261.5375 | 5.227%
-77.5 | 18.5 | 1133.8252 | 89.5276 | 127.5365 | 170.1715 | 201.7229 | 246.2815 | 5.251%
-77 | 18.5 | 1101.4189 | 93.2827 | 135.4214 | 185.6789 | 224.9761 | 281.8166 | 4.576%
-76.5 | 18.5 | 1069.0477 | 72.6046 | 97.5281 | 135.7353 | 157.6178 | 187.8333 | 3.432%
-76 | 18.5 | 1036.7151 | 57.2279 | 74.1625 | 99.7658 | 119.487 | 143.9121 | 1.976%
-75.5 | 18.5 | 1004.4252 | 46.4546 | 63.4502 | 85.079 | 101.6961 | 125.378 | 1.147%
-75 | 18.5 | 972.1822 | 36.9094 | 50.0224 | 68.2039 | 80.7134 | 98.3477 | 0.6744%
-74.5 | 18.5 | 939.9914 | 34.8358 | 47.0829 | 64.9998 | 76.9911 | 93.9115 | 0.5829%
-74 | 18.5 | 907.8585 | 42.8024 | 59.7125 | 80.7376 | 96.9976 | 120.2991 | 0.9266%
-73.5 | 18.5 | 875.7901 | 58.2971 | 76.5522 | 105.2381 | 127.7143 | 153.4729 | 1.9%
-73 | 18.5 | 843.7937 | 68.7943 | 91.1415 | 126.5998 | 148.7288 | 177.9805 | 2.966%
-72.5 | 18.5 | 811.8781 | 76.3393 | 102.3002 | 140.7122 | 164.6252 | 197.9158 | 3.876%
-72 | 18.5 | 780.0535 | 74.9118 | 99.2068 | 136.097 | 158.3767 | 189.2129 | 3.905%
-71.5 | 18.5 | 748.3317 | 79.934 | 106.0452 | 143.2355 | 166.5381 | 198.7592 | 4.85%
-71 | 18.5 | 716.7265 | 90.0645 | 121.207 | 159.5615 | 186.2244 | 223.2447 | 6.868%
-70.5 | 18.5 | 685.2544 | 89.0264 | 118.8084 | 156.2131 | 181.6167 | 216.7407 | 7.006%
-70 | 18.5 | 653.9347 | 83.0288 | 109.5685 | 146.1252 | 169.4394 | 201.5818 | 5.753%
-69.5 | 18.5 | 622.7906 | 76.3531 | 99.9173 | 135.4584 | 156.9395 | 186.5276 | 4.449%
-69 | 18.5 | 591.8502 | 74.4077 | 96.9813 | 131.9091 | 152.5938 | 181.0374 | 4.18%
-68.5 | 18.5 | 561.1473 | 79.4002 | 104.1964 | 140.1634 | 162.4002 | 193.0311 | 5.035%
-68 | 18.5 | 530.7233 | 87.7757 | 117.0486 | 154.8203 | 180.3659 | 215.7651 | 6.511%
-67.5 | 18.5 | 500.6294 | 86.3737 | 114.607 | 151.793 | 176.4335 | 210.4932 | 6.375%
-67 | 18.5 | 470.929 | 80.6921 | 106.3844 | 142.9782 | 166.0506 | 197.9141 | 5.148%
-66.5 | 18.5 | 441.7017 | 73.9538 | 97.0691 | 132.866 | 154.5974 | 184.6705 | 3.86%
-66 | 18.5 | 413.0483 | 69.1461 | 88.703 | 118.6608 | 139.4575 | 164.6902 | 3.589%
-65.5 | 18.5 | 385.0969 | 76.4694 | 97.9145 | 130.6977 | 150.3498 | 177.0984 | 5.143%
-65 | 18.5 | 358.0123 | 89.909 | 117.2453 | 152.4974 | 176.0858 | 208.457 | 8.363%
-64.5 | 18.5 | 332.0069 | 88.9111 | 115.0404 | 149.3357 | 171.7963 | 202.4953 | 8.594%
-64 | 18.5 | 307.355 | 84.0464 | 108.7722 | 143.3728 | 165.4624 | 195.7594 | 6.696%
-63.5 | 18.5 | 284.4088 | 75.2703 | 96.8534 | 130.0249 | 150.3715 | 178.022 | 4.633%
-63 | 18.5 | 263.6143 | 72.8386 | 93.3783 | 124.819 | 145.0716 | 171.0572 | 4.305%
-62.5 | 18.5 | 245.5191 | 76.6129 | 99.0445 | 133.1026 | 153.412 | 181.2281 | 4.882%
-62 | 18.5 | 230.7591 | 78.1001 | 102.1319 | 137.7355 | 159.7138 | 190.015 | 4.785%
-61.5 | 18.5 | 220.0068 | 59.1576 | 74.4204 | 97.3069 | 114.5443 | 137.0978 | 2.51%
-61 | 18.5 | 213.8675 | 42.2347 | 56.1147 | 72.3547 | 83.9747 | 100.0107 | 1.056%
-60.5 | 18.5 | 212.741 | 30.2542 | 38.5863 | 51.269 | 60.3455 | 70.84 | 0.4141%
-60 | 18.5 | 216.7054 | 20.2471 | 26.8459 | 34.5428 | 40.2668 | 48.2039 | 0.147%
-59.5 | 18.5 | 225.4926 | 13.8534 | 17.7404 | 23.6831 | 27.7093 | 32.6271 | 0.05272%
-59 | 18.5 | 238.57 | 9.3328 | 12.3091 | 15.9155 | 18.6079 | 22.3534 | 0.01893%
-90 | 19 | 1951.1372 | 10.1578 | 13.7691 | 18.9455 | 23.0043 | 28.5235 | 0.03668%
-89.5 | 19 | 1918.5111 | 11.5904 | 16.3059 | 24.2958 | 31.0448 | 41.4322 | 0.07118%
-89 | 19 | 1885.8908 | 14.3299 | 21.3762 | 34.0933 | 45.2805 | 62.7879 | 0.126%
-88.5 | 19 | 1853.2771 | 17.1449 | 26.1728 | 42.2004 | 56.4292 | 77.533 | 0.1717%
-88 | 19 | 1820.6705 | 16.986 | 24.4281 | 36.56 | 46.6325 | 62.1252 | 0.146%
-87.5 | 19 | 1788.0717 | 17.2771 | 23.8798 | 33.1896 | 40.2386 | 50.4414 | 0.1254%
-87 | 19 | 1755.4813 | 18.8935 | 25.8857 | 32.9232 | 38.1089 | 45.2446 | 0.1271%
-86.5 | 19 | 1722.9001 | 22.6104 | 29.5606 | 38.0891 | 44.4384 | 53.2509 | 0.1932%
-86 | 19 | 1690.3288 | 26.3242 | 33.1932 | 43.5195 | 51.3136 | 60.8509 | 0.2801%
-85.5 | 19 | 1657.7683 | 28.1993 | 36.006 | 47.9035 | 56.9879 | 65.7367 | 0.3444%
-85 | 19 | 1625.2194 | 29.3454 | 37.8725 | 51.0205 | 60.1775 | 69.5426 | 0.3872%
-84.5 | 19 | 1592.6832 | 29.9828 | 38.9915 | 52.9983 | 62.0345 | 72.14 | 0.4117%
-84 | 19 | 1560.1606 | 31.7434 | 41.8556 | 57.8174 | 66.5471 | 78.3342 | 0.4795%
-83.5 | 19 | 1527.6528 | 35.6262 | 47.8238 | 64.3996 | 74.3667 | 88.0462 | 0.6528%
-83 | 19 | 1495.161 | 46.7792 | 63.3002 | 82.4758 | 96.8781 | 117.0159 | 1.294%
-82.5 | 19 | 1462.6864 | 71.4994 | 94.9762 | 131.9435 | 151.9455 | 179.3149 | 3.515%
-82 | 19 | 1430.2305 | 90.8504 | 124.1628 | 160.3671 | 185.2308 | 219.3641 | 7.893%
-81.5 | 19 | 1397.7949 | 109.8751 | 145.6095 | 186.8154 | 217.3888 | 259.7021 | 13.83%
-81 | 19 | 1365.3812 | 137.5073 | 176.8406 | 237.257 | 283.6953 | 330.3549 | 20.1%
-80.5 | 19 | 1332.9913 | 111.7393 | 151.3056 | 201.0503 | 238.9961 | 292.7497 | 9.73%
-80 | 19 | 1300.6271 | 79.679 | 113.2873 | 157.9016 | 188.2121 | 231.2768 | 3.479%
-79.5 | 19 | 1268.2909 | 65.6689 | 89.6249 | 128.8905 | 151.8698 | 183.1189 | 2.327%
-79 | 19 | 1235.9851 | 74.3382 | 102.0587 | 142.3931 | 166.3604 | 199.6759 | 3.403%
-78.5 | 19 | 1203.7124 | 98.7481 | 139.4096 | 186.6706 | 222.9408 | 274.5834 | 6.313%
-78 | 19 | 1171.4758 | 104.0251 | 143.3092 | 189.3009 | 224.2203 | 273.4925 | 8.301%
-77.5 | 19 | 1139.2786 | 99.0724 | 137.4721 | 179.5881 | 211.2861 | 255.6846 | 7.951%
-77 | 19 | 1107.1243 | 105.0209 | 146.557 | 198.0305 | 237.8174 | 294.8098 | 6.938%
-76.5 | 19 | 1075.0172 | 80.1935 | 108.5651 | 147.3454 | 171.5901 | 205.1726 | 4.608%
-76 | 19 | 1042.9618 | 70.4956 | 92.6161 | 127.3947 | 148.7624 | 177.0691 | 3.359%
-75.5 | 19 | 1010.9633 | 66.8089 | 87.9125 | 121.1501 | 143.4327 | 171.2765 | 2.799%
-75 | 19 | 979.0274 | 58.6117 | 76.4636 | 104.316 | 126.0084 | 151.2784 | 1.988%
-74.5 | 19 | 947.1607 | 49.1263 | 66.5219 | 89.8369 | 107.8507 | 133.119 | 1.283%
-74 | 19 | 915.3708 | 49.5512 | 67.0962 | 90.8017 | 109.1473 | 134.5514 | 1.304%
-73.5 | 19 | 883.666 | 60.5208 | 79.3926 | 109.015 | 131.9472 | 157.4513 | 2.117%
-73 | 19 | 852.0562 | 66.7038 | 87.8219 | 121.1021 | 143.3187 | 170.9356 | 2.791%
-72.5 | 19 | 820.5526 | 70.4426 | 93.0254 | 128.7316 | 150.3654 | 179.549 | 3.25%
-72 | 19 | 789.168 | 72.692 | 95.642 | 131.6053 | 152.6991 | 181.8004 | 3.679%
-71.5 | 19 | 757.9175 | 82.9581 | 110.2326 | 147.5089 | 171.4211 | 204.4671 | 5.515%
-71 | 19 | 726.8187 | 93.816 | 125.9998 | 163.4571 | 190.2375 | 227.3076 | 8.315%
-70.5 | 19 | 695.892 | 93.8134 | 125.3022 | 162.1844 | 188.3363 | 224.4483 | 8.656%
-70 | 19 | 665.1617 | 86.9535 | 114.8722 | 151.4454 | 175.5853 | 208.8612 | 6.788%
-69.5 | 19 | 634.6566 | 76.7171 | 99.8897 | 134.8601 | 156.0642 | 185.2335 | 4.641%
-69 | 19 | 604.4111 | 73.4871 | 95.2209 | 128.8794 | 149.4609 | 177.0977 | 4.132%
-68.5 | 19 | 574.4662 | 80.556 | 105.5219 | 141.3434 | 163.7203 | 194.5345 | 5.338%
-68 | 19 | 544.8718 | 93.9248 | 126.0046 | 163.8521 | 191.024 | 228.7065 | 8.171%
-67.5 | 19 | 515.6885 | 93.5938 | 125.1638 | 162.4918 | 189.0325 | 225.7534 | 8.349%
-67 | 19 | 486.9903 | 88.3153 | 117.4045 | 154.6904 | 179.8522 | 214.6433 | 6.857%
-66.5 | 19 | 458.8686 | 80.275 | 105.5987 | 142.0279 | 165.0439 | 196.85 | 5.067%
-66 | 19 | 431.4363 | 71.8764 | 91.0721 | 120.0823 | 139.7665 | 163.5837 | 4.509%
-65.5 | 19 | 404.8337 | 79.4256 | 100.0327 | 130.9719 | 149.0025 | 173.3275 | 6.965%
-65 | 19 | 379.2358 | 93.3049 | 119.5676 | 151.7739 | 172.9597 | 201.6193 | 12.4%
-64.5 | 19 | 354.86 | 93.835 | 119.9795 | 151.8258 | 172.7735 | 201.0673 | 13.11%
-64 | 19 | 331.9761 | 90.5317 | 116.4293 | 149.616 | 171.223 | 200.5877 | 10.1%
-63.5 | 19 | 310.9136 | 83.2802 | 109.0453 | 145.3066 | 168.9771 | 201.7135 | 5.789%
-63 | 19 | 292.0672 | 61.4648 | 77.668 | 102.0831 | 120.5474 | 143.6481 | 2.729%
-62.5 | 19 | 275.8914 | 49.1271 | 64.2882 | 83.3596 | 97.6291 | 117.5172 | 1.521%
-62 | 19 | 262.8798 | 39.7206 | 52.2675 | 68.4744 | 79.4737 | 94.6534 | 0.8774%
-61.5 | 19 | 253.5203 | 32.1225 | 41.1899 | 55.0731 | 64.0352 | 75.4058 | 0.4896%
-61 | 19 | 248.2263 | 25.4809 | 32.0978 | 41.8307 | 49.1422 | 59.1233 | 0.2548%
-60.5 | 19 | 247.259 | 18.4746 | 24.4697 | 31.6697 | 36.7456 | 43.7482 | 0.115%
-60 | 19 | 250.6688 | 13.6549 | 17.4306 | 23.1832 | 27.1934 | 31.9431 | 0.04986%
-59.5 | 19 | 258.2821 | 9.6756 | 12.6549 | 16.3537 | 19.1139 | 22.9522 | 0.02006%
-59 | 19 | 269.7433 | 6.8019 | 8.8013 | 11.7933 | 13.6031 | 16.084 | 0.008182%
-90 | 19.5 | 1953.028 | 8.1509 | 11.6312 | 16.3683 | 20.149 | 25.7129 | 0.03008%
-89.5 | 19.5 | 1920.5313 | 9.7201 | 14.698 | 23.4035 | 30.7519 | 42.1097 | 0.06908%
-89 | 19.5 | 1888.0431 | 12.7781 | 20.4079 | 34.1953 | 46.1544 | 64.6135 | 0.1214%
-88.5 | 19.5 | 1855.5643 | 15.4212 | 25.4395 | 42.5165 | 58.0445 | 79.5253 | 0.1632%
-88 | 19.5 | 1823.0955 | 13.8921 | 21.2429 | 34.3638 | 45.7692 | 63.4448 | 0.1255%
-87.5 | 19.5 | 1790.6376 | 12.3515 | 17.1916 | 25.2972 | 32.2477 | 42.9109 | 0.07655%
-87 | 19.5 | 1758.1914 | 12.1917 | 15.7114 | 21.1297 | 25.3024 | 29.9781 | 0.04185%
-86.5 | 19.5 | 1725.7579 | 13.3245 | 17.2527 | 23.3313 | 27.2735 | 31.5039 | 0.04977%
-86 | 19.5 | 1693.3379 | 14.6031 | 19.2025 | 26.2151 | 29.7568 | 34.5273 | 0.06428%
-85.5 | 19.5 | 1660.9326 | 15.6195 | 20.8169 | 27.9096 | 31.8685 | 37.2357 | 0.07737%
-85 | 19.5 | 1628.5431 | 16.299 | 21.9274 | 29.1073 | 33.4232 | 39.3103 | 0.08783%
-84.5 | 19.5 | 1596.1706 | 16.9257 | 22.9486 | 30.2178 | 34.8756 | 41.2643 | 0.09816%
-84 | 19.5 | 1563.8163 | 18.2408 | 25.1111 | 32.4043 | 37.6286 | 44.8424 | 0.1203%
-83.5 | 19.5 | 1531.4818 | 21.4055 | 28.7069 | 37.3445 | 43.824 | 52.8745 | 0.1768%
-83 | 19.5 | 1499.1684 | 27.4488 | 35.3484 | 47.5002 | 56.8522 | 66.1301 | 0.323%
-82.5 | 19.5 | 1466.878 | 34.1488 | 45.5337 | 61.7666 | 70.6814 | 82.796 | 0.5905%
-82 | 19.5 | 1434.6122 | 41.3974 | 57.0534 | 72.7165 | 83.9181 | 99.2813 | 1.026%
-81.5 | 19.5 | 1402.373 | 49.776 | 66.0565 | 85.7781 | 100.551 | 121.1609 | 1.552%
-81 | 19.5 | 1370.1626 | 56.2317 | 72.8084 | 97.0031 | 115.4978 | 138.2515 | 1.984%
-80.5 | 19.5 | 1337.9832 | 50.5597 | 67.8287 | 90.2008 | 107.2772 | 131.3407 | 1.455%
-80 | 19.5 | 1305.8373 | 54.333 | 76.4196 | 111.3437 | 137.7258 | 168.6249 | 1.349%
-79.5 | 19.5 | 1273.7279 | 51.5088 | 71.1581 | 99.3535 | 121.7171 | 148.2404 | 1.322%
-79 | 19.5 | 1241.6579 | 73.1541 | 100.8632 | 141.763 | 166.0576 | 199.9246 | 3.159%
-78.5 | 19.5 | 1209.6307 | 106.0191 | 146.0314 | 194.071 | 230.7205 | 282.6428 | 8.267%
-78 | 19.5 | 1177.65 | 118.7017 | 156.4854 | 206.5897 | 244.6148 | 297.2781 | 12.89%
-77.5 | 19.5 | 1145.72 | 110.5307 | 148.4534 | 194.3465 | 228.9453 | 277.4755 | 11.06%
-77 | 19.5 | 1113.8453 | 103.207 | 142.9843 | 190.1265 | 226.107 | 277.1003 | 7.635%
-76.5 | 19.5 | 1082.031 | 78.3448 | 103.572 | 140.0261 | 161.8401 | 191.8075 | 4.789%
-76 | 19.5 | 1050.2828 | 80.1115 | 106.3624 | 143.6221 | 166.9956 | 199.3166 | 4.874%
-75.5 | 19.5 | 1018.6072 | 81.4237 | 108.8382 | 146.9214 | 171.3485 | 205.2379 | 4.934%
-75 | 19.5 | 987.0113 | 72.016 | 95.069 | 131.3938 | 152.7655 | 182.3159 | 3.493%
-74.5 | 19.5 | 955.5033 | 62.0143 | 80.9044 | 110.3776 | 132.8335 | 158.0511 | 2.332%
-74 | 19.5 | 924.0925 | 56.0777 | 73.6258 | 99.8689 | 120.2153 | 145.4167 | 1.799%
-73.5 | 19.5 | 892.7893 | 59.1605 | 77.2915 | 105.6242 | 127.7201 | 152.9876 | 2.026%
-73 | 19.5 | 861.6056 | 63.4876 | 83.4169 | 114.7537 | 137.4153 | 163.9406 | 2.422%
-72.5 | 19.5 | 830.5553 | 65.7678 | 86.4811 | 119.0787 | 141.4565 | 168.7944 | 2.682%
-72 | 19.5 | 799.654 | 70.2495 | 92.3054 | 126.9876 | 148.4281 | 176.7178 | 3.317%
-71.5 | 19.5 | 768.9199 | 84.7327 | 113.0287 | 150.6244 | 175.1914 | 209.174 | 5.838%
-71 | 19.5 | 738.3742 | 100.6732 | 135.0067 | 173.6918 | 202.4578 | 242.3428 | 10.3%
-70.5 | 19.5 | 708.0415 | 101.901 | 135.8754 | 174.3483 | 202.8969 | 242.4109 | 11.09%
-70 | 19.5 | 677.9505 | 94.1797 | 126.1032 | 163.2736 | 189.8382 | 226.5703 | 8.598%
-69.5 | 19.5 | 648.1352 | 79.5545 | 104.4268 | 140.5033 | 162.9907 | 194.0077 | 5.016%
-69 | 19.5 | 618.6356 | 70.6225 | 91.4686 | 123.7369 | 144.8225 | 171.7576 | 3.623%
-68.5 | 19.5 | 589.4994 | 74.5758 | 97.1408 | 132.0105 | 152.8122 | 181.4372 | 4.205%
-68 | 19.5 | 560.7834 | 85.3666 | 113.2594 | 150.5761 | 175.18 | 209.2233 | 6.057%
-67.5 | 19.5 | 532.5559 | 87.3323 | 116.0424 | 153.2902 | 178.1819 | 212.5906 | 6.609%
-67 | 19.5 | 504.8989 | 83.2372 | 110.1973 | 147.2302 | 171.1054 | 204.1021 | 5.632%
-66.5 | 19.5 | 477.9118 | 77.9849 | 102.8283 | 139.4602 | 162.3194 | 193.964 | 4.508%
-66 | 19.5 | 451.7147 | 71.8409 | 91.8457 | 122.3756 | 142.6628 | 168.0855 | 4.18%
-65.5 | 19.5 | 426.4536 | 77.581 | 97.4646 | 127.2358 | 145.5946 | 169.3323 | 6.468%
-65 | 19.5 | 402.305 | 88.4433 | 112.122 | 143.6718 | 163.2869 | 189.744 | 10.61%
-64.5 | 19.5 | 379.4815 | 84.7205 | 106.6803 | 137.6317 | 156.178 | 181.151 | 9.285%
-64 | 19.5 | 358.2367 | 76.546 | 96.4744 | 126.4178 | 145.1573 | 169.2593 | 5.943%
-63.5 | 19.5 | 338.8676 | 53.5531 | 68.106 | 87.6088 | 102.1093 | 122.2127 | 2.037%
-63 | 19.5 | 321.7136 | 35.9048 | 46.0683 | 60.9514 | 70.3239 | 83.1751 | 0.6682%
-62.5 | 19.5 | 307.146 | 27.8402 | 35.0133 | 45.7661 | 53.8626 | 63.8973 | 0.3251%
-62 | 19.5 | 295.5476 | 22.597 | 29.2601 | 37.8197 | 44.208 | 53.0929 | 0.1906%
-61.5 | 19.5 | 287.2784 | 18.473 | 24.4098 | 31.604 | 36.672 | 43.6643 | 0.1145%
-61 | 19.5 | 282.6308 | 15.0502 | 19.3809 | 25.9889 | 29.9043 | 35.2571 | 0.06545%
-60.5 | 19.5 | 281.7841 | 12.1052 | 15.2636 | 20.0118 | 23.5956 | 28.0397 | 0.03413%
-60 | 19.5 | 284.7723 | 8.9713 | 11.8813 | 15.2575 | 17.7643 | 21.2358 | 0.01641%
-59.5 | 19.5 | 291.4773 | 6.6941 | 8.6344 | 11.5851 | 13.3391 | 15.7387 | 0.007676%
-59 | 19.5 | 301.6514 | 5.0305 | 6.3437 | 8.287 | 9.7496 | 11.7287 | 0.003185%
-90 | 20 | 1955.4771 | 6.5639 | 9.2885 | 13.4639 | 16.5037 | 20.9566 | 0.02045%
-89.5 | 20 | 1923.1207 | 7.2192 | 10.9194 | 17.0357 | 22.2711 | 30.1951 | 0.0412%
-89 | 20 | 1890.7759 | 9.1917 | 15.0555 | 26.346 | 36.061 | 52.1193 | 0.0848%
-88.5 | 20 | 1858.4435 | 10.4787 | 17.3506 | 30.363 | 41.5025 | 59.6375 | 0.1018%
-88 | 20 | 1826.1244 | 9.5765 | 15.2737 | 26.0427 | 35.0944 | 49.8027 | 0.08268%
-87.5 | 20 | 1793.8196 | 8.1111 | 11.9247 | 18.6057 | 24.3868 | 34.495 | 0.04896%
-87 | 20 | 1761.5302 | 7.4676 | 10.2475 | 13.8809 | 16.4098 | 19.9708 | 0.01626%
-86.5 | 20 | 1729.2573 | 7.9152 | 10.8817 | 14.1278 | 16.3839 | 19.4948 | 0.01421%
-86 | 20 | 1697.0021 | 8.6007 | 11.8008 | 15.0865 | 17.5176 | 20.8741 | 0.01646%
-85.5 | 20 | 1664.7658 | 9.2271 | 12.4379 | 16.0285 | 18.702 | 22.4131 | 0.01954%
-85 | 20 | 1632.5499 | 9.753 | 12.9611 | 16.8282 | 19.7246 | 23.765 | 0.02256%
-84.5 | 20 | 1600.3559 | 10.4126 | 13.5946 | 17.7865 | 20.9452 | 25.374 | 0.02641%
-84 | 20 | 1568.1852 | 11.628 | 14.8133 | 19.6557 | 23.3454 | 27.6654 | 0.03358%
-83.5 | 20 | 1536.0398 | 13.2146 | 17.2424 | 23.5277 | 27.5338 | 31.9581 | 0.05147%
-83 | 20 | 1503.9213 | 15.8604 | 21.4655 | 28.8141 | 33.1477 | 39.0708 | 0.08528%
-82.5 | 20 | 1471.8319 | 19.532 | 26.9197 | 34.6733 | 40.4441 | 48.4517 | 0.1441%
-82 | 20 | 1439.7738 | 23.6929 | 31.0081 | 40.8215 | 48.2527 | 58.5135 | 0.2235%
-81.5 | 20 | 1407.7492 | 26.7405 | 34.4547 | 46.3285 | 55.4711 | 64.7738 | 0.3021%
-81 | 20 | 1375.7609 | 27.5775 | 35.9299 | 48.9427 | 58.7588 | 68.1109 | 0.3312%
-80.5 | 20 | 1343.8116 | 26.9111 | 35.0686 | 47.7803 | 57.6705 | 67.2367 | 0.3112%
-80 | 20 | 1311.9045 | 27.1841 | 35.5637 | 48.6777 | 58.6884 | 68.7355 | 0.3202%
-79.5 | 20 | 1280.043 | 31.979 | 43.1502 | 60.2645 | 69.8286 | 83.0038 | 0.4882%
-79 | 20 | 1248.2307 | 49.8637 | 67.6069 | 90.4173 | 107.9064 | 132.2355 | 1.377%
-78.5 | 20 | 1216.4719 | 92.5465 | 134.9535 | 184.7346 | 223.609 | 279.7768 | 4.515%
-78 | 20 | 1184.771 | 105.4205 | 146.0196 | 195.1126 | 232.7267 | 286.2082 | 7.725%
-77.5 | 20 | 1153.133 | 98.6984 | 137.875 | 181.7899 | 215.0845 | 262.0069 | 7.215%
-77 | 20 | 1121.5636 | 100.2119 | 143.4093 | 198.3592 | 241.6223 | 301.7495 | 5.243%
-76.5 | 20 | 1090.0689 | 77.6819 | 102.7931 | 139.4151 | 161.3382 | 191.4973 | 4.591%
-76 | 20 | 1058.6559 | 81.4678 | 108.2392 | 145.5519 | 169.2147 | 201.9304 | 5.16%
-75.5 | 20 | 1027.3322 | 88.0482 | 118.8483 | 157.6722 | 184.2937 | 221.3166 | 6.193%
-75 | 20 | 996.1066 | 78.0686 | 103.5357 | 140.6211 | 163.4156 | 194.9167 | 4.499%
-74.5 | 20 | 964.9887 | 69.1333 | 91.0318 | 125.5462 | 146.8738 | 174.3343 | 3.168%
-74 | 20 | 933.9897 | 63.1553 | 83.5647 | 115.9032 | 138.6349 | 164.7501 | 2.352%
-73.5 | 20 | 903.122 | 54.6265 | 72.815 | 99.5887 | 120.4824 | 145.8814 | 1.631%
-73 | 20 | 872.3997 | 52.4164 | 70.4776 | 96.1748 | 116.1926 | 142.0676 | 1.469%
-72.5 | 20 | 841.839 | 53.8804 | 71.9437 | 98.279 | 118.8111 | 144.6905 | 1.572%
-72 | 20 | 811.4584 | 61.2753 | 80.1992 | 109.8294 | 132.5546 | 158.0554 | 2.215%
-71.5 | 20 | 781.2791 | 76.8731 | 102.37 | 140.0116 | 163.2684 | 195.5293 | 4.122%
-71 | 20 | 751.3257 | 97.502 | 132.9811 | 173.1559 | 203.315 | 245.4668 | 8.166%
-70.5 | 20 | 721.6265 | 97.3615 | 132.0748 | 170.9344 | 199.9666 | 240.3799 | 8.686%
-70 | 20 | 692.2144 | 86.8676 | 116.3311 | 154.588 | 180.3976 | 216.2285 | 6.105%
-69.5 | 20 | 663.1278 | 72.9032 | 96.3733 | 132.9736 | 155.2277 | 186.1341 | 3.537%
-69 | 20 | 634.4119 | 58.8514 | 75.8727 | 102.0882 | 122.2844 | 147.131 | 2.126%
-68.5 | 20 | 606.1193 | 59.7994 | 77.2915 | 104.3072 | 125.1687 | 150.1086 | 2.194%
-68 | 20 | 578.3127 | 67.2378 | 88.3679 | 121.6025 | 144.0403 | 172.5276 | 2.838%
-67.5 | 20 | 551.0655 | 68.5551 | 89.9849 | 123.644 | 145.7288 | 174.1645 | 3.045%
-67 | 20 | 524.4654 | 60.7488 | 78.9144 | 107.1248 | 129.0098 | 154.1354 | 2.233%
-66.5 | 20 | 498.6161 | 45.3154 | 60.5925 | 79.286 | 93.3737 | 113.1275 | 1.18%
-66 | 20 | 473.6407 | 43.8972 | 58.1532 | 74.8954 | 87.3552 | 104.6431 | 1.154%
-65.5 | 20 | 449.6851 | 48.1013 | 62.0112 | 78.4211 | 90.4585 | 106.9595 | 1.631%
-65 | 20 | 426.9211 | 53.1901 | 66.8005 | 84.2692 | 97.0584 | 114.5611 | 2.273%
-64.5 | 20 | 405.5495 | 46.3611 | 59.806 | 74.9114 | 85.9084 | 100.8875 | 1.536%
-64 | 20 | 385.8022 | 36.1587 | 45.5644 | 59.3826 | 67.7381 | 79.0533 | 0.7063%
-63.5 | 20 | 367.9407 | 28.7852 | 35.8203 | 46.245 | 54.0181 | 63.6851 | 0.354%
-63 | 20 | 352.2523 | 20.8962 | 27.1491 | 34.5747 | 40.0521 | 47.5954 | 0.1508%
-62.5 | 20 | 339.0389 | 16.2892 | 20.9104 | 27.5274 | 31.6926 | 37.3904 | 0.07704%
-62 | 20 | 328.5992 | 13.6353 | 17.282 | 22.7951 | 26.7456 | 31.374 | 0.04738%
-61.5 | 20 | 321.2039 | 11.6853 | 14.6592 | 19.105 | 22.4449 | 26.8632 | 0.02985%
-61 | 20 | 317.0662 | 9.4273 | 12.358 | 15.8986 | 18.5314 | 22.1817 | 0.01823%
-60.5 | 20 | 316.3139 | 7.5814 | 9.9126 | 13.021 | 15.0524 | 17.8437 | 0.01049%
-60 | 20 | 318.971 | 6.0628 | 7.7317 | 10.2719 | 12.0454 | 14.1387 | 0.005648%
-59.5 | 20 | 324.9539 | 4.6747 | 6.0019 | 7.7956 | 9.1393 | 11.0143 | 0.002748%
-59 | 20 | 334.0839 | 3.4172 | 4.4978 | 5.9071 | 6.8481 | 8.1453 | 0.001342%
-90 | 20.5 | 1958.4826 | 5.1878 | 7.2174 | 10.6145 | 13.0359 | 16.3234 | 0.01258%
-89.5 | 20.5 | 1926.2772 | 5.0979 | 7.2584 | 10.9677 | 13.7024 | 17.6709 | 0.01572%
-89 | 20.5 | 1894.0867 | 5.5276 | 8.4113 | 13.5223 | 17.7605 | 24.4562 | 0.02972%
-88.5 | 20.5 | 1861.9119 | 5.8175 | 9.0174 | 14.729 | 19.6271 | 27.3008 | 0.03544%
-88 | 20.5 | 1829.7541 | 5.5543 | 8.3588 | 13.4029 | 17.7493 | 24.6782 | 0.02981%
-87.5 | 20.5 | 1797.6144 | 5.0483 | 7.0121 | 10.2749 | 12.9411 | 16.9353 | 0.0136%
-87 | 20.5 | 1765.4941 | 4.8613 | 6.4653 | 8.8678 | 10.7469 | 13.2483 | 0.006343%
-86.5 | 20.5 | 1733.3945 | 5.105 | 6.5745 | 8.835 | 10.5748 | 12.6562 | 0.004787%
-86 | 20.5 | 1701.3171 | 5.363 | 6.9068 | 9.2817 | 11.1095 | 12.9637 | 0.005037%
-85.5 | 20.5 | 1669.2633 | 5.619 | 7.2694 | 9.8211 | 11.6763 | 13.4701 | 0.005616%
-85 | 20.5 | 1637.235 | 5.8802 | 7.6474 | 10.3951 | 12.1546 | 14.058 | 0.006248%
-84.5 | 20.5 | 1605.2337 | 6.25 | 8.203 | 11.2702 | 12.8752 | 14.9596 | 0.007413%
-84 | 20.5 | 1573.2615 | 6.909 | 9.2588 | 12.4565 | 14.2623 | 16.7177 | 0.009765%
-83.5 | 20.5 | 1541.3203 | 8.0909 | 11.2629 | 14.4708 | 16.7927 | 19.9965 | 0.01521%
-83 | 20.5 | 1509.4125 | 10.0243 | 13.352 | 17.5704 | 20.7637 | 25.2583 | 0.0267%
-82.5 | 20.5 | 1477.5405 | 12.2323 | 15.9137 | 21.6399 | 25.9869 | 29.9786 | 0.04365%
-82 | 20.5 | 1445.7068 | 13.9326 | 18.6061 | 25.9845 | 29.681 | 34.6944 | 0.06389%
-81.5 | 20.5 | 1413.9144 | 15.1963 | 20.6679 | 28.2109 | 32.5163 | 38.4132 | 0.08052%
-81 | 20.5 | 1382.1663 | 15.6567 | 21.4103 | 29.0236 | 33.5925 | 39.8789 | 0.08735%
-80.5 | 20.5 | 1350.4659 | 15.7209 | 21.4577 | 29.046 | 33.6205 | 39.9149 | 0.08763%
-80 | 20.5 | 1318.8169 | 17.0501 | 23.7062 | 31.5017 | 36.8081 | 44.1852 | 0.1096%
-79.5 | 20.5 | 1287.2233 | 23.8783 | 32.5437 | 45.3595 | 55.5107 | 67.2975 | 0.2484%
-79 | 20.5 | 1255.6895 | 39.2576 | 57.9292 | 80.0622 | 97.4137 | 122.6265 | 0.7372%
-78.5 | 20.5 | 1224.2206 | 62.2133 | 86.0863 | 125.8102 | 150.2822 | 182.682 | 1.907%
-78 | 20.5 | 1192.8217 | 69.056 | 94.474 | 134.6399 | 157.2079 | 188.5578 | 2.732%
-77.5 | 20.5 | 1161.4989 | 69.6513 | 94.7471 | 134.2612 | 156.137 | 186.3923 | 2.894%
-77 | 20.5 | 1130.2587 | 68.9538 | 93.8979 | 133.6038 | 156.0146 | 187.1496 | 2.746%
-76.5 | 20.5 | 1099.1084 | 73.8551 | 101.6193 | 142.6165 | 167.6878 | 202.7814 | 3.194%
-76 | 20.5 | 1068.0562 | 86.8731 | 122.0988 | 163.6445 | 192.878 | 233.9057 | 5.104%
-75.5 | 20.5 | 1037.111 | 99.6336 | 140.5429 | 189.1054 | 226.5176 | 279.9586 | 6.234%
-75 | 20.5 | 1006.283 | 96.7763 | 137.0133 | 182.052 | 216.407 | 265.0725 | 6.336%
-74.5 | 20.5 | 975.5836 | 83.8915 | 120.6699 | 164.4024 | 195.0997 | 238.5044 | 4.167%
-74 | 20.5 | 945.0255 | 53.9029 | 73.4748 | 102.4625 | 125.4325 | 149.8028 | 1.504%
-73.5 | 20.5 | 914.6231 | 36.4279 | 50.9886 | 70.5647 | 84.2193 | 103.647 | 0.6435%
-73 | 20.5 | 884.3927 | 30.3141 | 40.3274 | 56.2873 | 66.3769 | 79.8657 | 0.4204%
-72.5 | 20.5 | 854.3528 | 30.7859 | 40.8792 | 56.934 | 67.1056 | 80.9697 | 0.4352%
-72 | 20.5 | 824.5245 | 34.3732 | 46.0619 | 63.3011 | 74.4434 | 90.0433 | 0.5709%
-71.5 | 20.5 | 794.9318 | 40.2148 | 54.7557 | 72.9284 | 86.0398 | 104.4606 | 0.8521%
-71 | 20.5 | 765.6023 | 44.6586 | 60.4646 | 79.3262 | 93.57 | 113.5775 | 1.124%
-70.5 | 20.5 | 736.5676 | 44.3668 | 59.7805 | 77.798 | 91.3179 | 110.207 | 1.138%
-70 | 20.5 | 707.8642 | 40.1915 | 53.6783 | 70.651 | 82.5122 | 98.9931 | 0.8848%
-69.5 | 20.5 | 679.5345 | 34.6355 | 45.3117 | 61.175 | 71.1001 | 84.8179 | 0.5939%
-69 | 20.5 | 651.6272 | 30.6001 | 39.4726 | 53.146 | 62.5913 | 74.3295 | 0.4267%
-68.5 | 20.5 | 624.1993 | 29.972 | 38.6558 | 52.036 | 61.5441 | 73.148 | 0.4036%
-68 | 20.5 | 597.3171 | 30.9407 | 40.1132 | 54.3267 | 63.8898 | 76.1083 | 0.4396%
-67.5 | 20.5 | 571.0578 | 31.0293 | 40.317 | 54.7438 | 64.3599 | 76.7666 | 0.4429%
-67 | 20.5 | 545.5116 | 28.2442 | 36.3324 | 48.7594 | 58.2822 | 69.1915 | 0.3451%
-66.5 | 20.5 | 520.7837 | 24.1727 | 31.049 | 40.6894 | 47.9632 | 58.1676 | 0.2283%
-66 | 20.5 | 496.9963 | 23.1213 | 29.6119 | 38.1101 | 44.431 | 53.1972 | 0.1982%
-65.5 | 20.5 | 474.2913 | 24.6838 | 30.7892 | 39.1888 | 45.3818 | 53.9078 | 0.2259%
-65 | 20.5 | 452.8316 | 25.9524 | 31.8255 | 40.3904 | 46.6909 | 55.3481 | 0.2547%
-64.5 | 20.5 | 432.8027 | 23.6729 | 29.7089 | 37.5095 | 43.2242 | 51.0496 | 0.1999%
-64 | 20.5 | 414.4123 | 19.548 | 25.2734 | 31.8393 | 36.5279 | 42.9171 | 0.1194%
-63.5 | 20.5 | 397.8877 | 15.9969 | 20.2203 | 26.4331 | 30.239 | 35.4093 | 0.06768%
-63 | 20.5 | 383.4703 | 12.9402 | 16.1278 | 20.8592 | 24.3922 | 28.6969 | 0.03617%
-62.5 | 20.5 | 371.4058 | 10.3372 | 13.1692 | 16.8601 | 19.594 | 23.3724 | 0.02009%
-62 | 20.5 | 361.9296 | 8.44 | 11.0786 | 14.1936 | 16.4218 | 19.4863 | 0.01268%
-61.5 | 20.5 | 355.249 | 7.1573 | 9.2354 | 12.2141 | 14.0684 | 16.6064 | 0.008512%
-61 | 20.5 | 351.5234 | 6.0987 | 7.7583 | 10.2774 | 12.0377 | 14.1213 | 0.005521%
-60.5 | 20.5 | 350.847 | 5.1431 | 6.4553 | 8.418 | 9.8932 | 11.8556 | 0.003186%
-60 | 20.5 | 353.2374 | 4.0022 | 5.2955 | 6.803 | 7.9226 | 9.4735 | 0.001877%
-59.5 | 20.5 | 358.6332 | 3.1245 | 4.0624 | 5.4162 | 6.2541 | 7.404 | 0.001052%
-59 | 20.5 | 366.9017 | 2.4125 | 3.0669 | 4.0593 | 4.8141 | 5.7084 | 0.0005227%
-90 | 21 | 1962.0419 | 3.8249 | 5.5998 | 8.0737 | 10.086 | 12.7534 | 0.008234%
-89.5 | 21 | 1929.9979 | 3.497 | 5.2292 | 7.6135 | 9.5678 | 12.321 | 0.0082%
-89 | 21 | 1897.9723 | 3.3979 | 5.1476 | 7.6544 | 9.7435 | 12.7209 | 0.009326%
-88.5 | 21 | 1865.9663 | 3.3192 | 5.0302 | 7.5754 | 9.7084 | 12.808 | 0.009706%
-88 | 21 | 1833.9811 | 3.1568 | 4.6723 | 7.0251 | 8.9419 | 11.8325 | 0.008115%
-87.5 | 21 | 1802.0181 | 3.0075 | 4.2946 | 6.2857 | 7.8102 | 10.077 | 0.005184%
-87 | 21 | 1770.0789 | 2.9625 | 4.1146 | 5.8321 | 7.0264 | 8.7432 | 0.003084%
-86.5 | 21 | 1738.1649 | 3.0298 | 4.1607 | 5.7484 | 6.7663 | 8.1929 | 0.002166%
-86 | 21 | 1706.2779 | 3.1657 | 4.3454 | 5.8646 | 6.8218 | 8.1462 | 0.001837%
-85.5 | 21 | 1674.4197 | 3.3254 | 4.5813 | 6.0495 | 7.006 | 8.3228 | 0.001742%
-85 | 21 | 1642.5923 | 3.5397 | 4.913 | 6.3278 | 7.3256 | 8.6987 | 0.001783%
-84.5 | 21 | 1610.7977 | 3.8875 | 5.3345 | 6.8444 | 7.9648 | 9.5154 | 0.002162%
-84 | 21 | 1579.0381 | 4.5366 | 5.9962 | 7.8839 | 9.3118 | 11.3205 | 0.003497%
-83.5 | 21 | 1547.316 | 5.4752 | 7.1723 | 9.8321 | 11.7691 | 13.7703 | 0.006496%
-83 | 21 | 1515.634 | 6.6405 | 9.1224 | 12.6659 | 14.8421 | 17.8771 | 0.0131%
-82.5 | 21 | 1483.995 | 8.3594 | 11.9446 | 16.226 | 19.5493 | 24.3266 | 0.0265%
-82 | 21 | 1452.402 | 10.5748 | 14.6749 | 20.912 | 25.9133 | 31.8525 | 0.04773%
-81.5 | 21 | 1420.8583 | 12.0405 | 16.6643 | 24.3597 | 29.6635 | 36.8881 | 0.0641%
-81 | 21 | 1389.3676 | 12.1396 | 16.6554 | 24.0999 | 29.226 | 36.0564 | 0.06196%
-80.5 | 21 | 1357.9337 | 11.7142 | 15.5774 | 21.7322 | 26.4102 | 31.606 | 0.04785%
-80 | 21 | 1326.5611 | 12.1834 | 16.1014 | 22.3012 | 26.7549 | 31.4397 | 0.04842%
-79.5 | 21 | 1295.2543 | 14.8073 | 20.4622 | 28.5384 | 33.4478 | 40.2957 | 0.08475%
-79 | 21 | 1264.0186 | 20.8099 | 29.1745 | 39.7921 | 48.0599 | 59.4451 | 0.1873%
-78.5 | 21 | 1232.8596 | 28.2422 | 38.0179 | 53.8017 | 63.7575 | 75.6472 | 0.3605%
-78 | 21 | 1201.7836 | 32.1243 | 43.7437 | 61.1848 | 70.872 | 84.2119 | 0.4958%
-77.5 | 21 | 1170.7973 | 34.0471 | 46.5078 | 63.907 | 74.138 | 88.2503 | 0.5743%
-77 | 21 | 1139.9083 | 37.7839 | 53.3369 | 73.4875 | 88.0943 | 108.9768 | 0.6954%
-76.5 | 21 | 1109.1251 | 46.277 | 65.3415 | 90.5959 | 110.5168 | 137.4661 | 1.041%
-76 | 21 | 1078.4569 | 60.5385 | 81.2947 | 114.7184 | 138.2688 | 164.3269 | 1.992%
-75.5 | 21 | 1047.9142 | 74.0945 | 104.11 | 146.855 | 173.1358 | 210.0305 | 3.063%
-75 | 21 | 1017.5083 | 72.948 | 102.9109 | 145.9729 | 172.0824 | 208.7333 | 2.907%
-74.5 | 21 | 987.2522 | 42.514 | 60.0513 | 79.3701 | 94.0448 | 114.7594 | 0.9685%
-74 | 21 | 957.1605 | 28.8408 | 38.6347 | 54.3637 | 64.0485 | 75.7498 | 0.3781%
-73.5 | 21 | 927.2492 | 21.0777 | 28.8427 | 38.7574 | 46.3876 | 57.2772 | 0.1834%
-73 | 21 | 897.5367 | 17.9669 | 24.7302 | 32.9021 | 38.8759 | 47.2825 | 0.1242%
-72.5 | 21 | 868.0436 | 17.8642 | 24.3775 | 32.5153 | 38.4156 | 46.7181 | 0.121%
-72 | 21 | 838.7934 | 19.4999 | 26.6063 | 35.223 | 41.7767 | 51.0379 | 0.1486%
-71.5 | 21 | 809.8125 | 21.8849 | 29.2381 | 38.8971 | 46.2719 | 56.7274 | 0.1912%
-71 | 21 | 781.1312 | 23.5206 | 30.8323 | 40.9728 | 48.7086 | 59.3611 | 0.2216%
-70.5 | 21 | 752.784 | 23.2264 | 30.362 | 40.0364 | 47.3716 | 57.7099 | 0.2125%
-70 | 21 | 724.8103 | 21.2772 | 28.1825 | 36.7755 | 43.2373 | 52.2814 | 0.1713%
-69.5 | 21 | 697.2552 | 18.8349 | 25.1902 | 32.726 | 38.2358 | 45.8949 | 0.1256%
-69 | 21 | 670.1707 | 17.0167 | 22.3812 | 29.6229 | 34.4575 | 41.1458 | 0.09528%
-68.5 | 21 | 643.6163 | 16.3396 | 21.3944 | 28.5286 | 33.1743 | 39.599 | 0.08605%
-68 | 21 | 617.6606 | 16.3148 | 21.4088 | 28.6127 | 33.3325 | 39.8725 | 0.08691%
-67.5 | 21 | 592.3826 | 16.0339 | 21.028 | 28.2085 | 32.8791 | 39.3547 | 0.08375%
-67 | 21 | 567.8729 | 15.0001 | 19.4853 | 26.3229 | 30.5787 | 36.4576 | 0.06945%
-66.5 | 21 | 544.2356 | 13.7975 | 17.626 | 23.4637 | 27.5266 | 32.5381 | 0.05191%
-66 | 21 | 521.5895 | 13.3643 | 16.8078 | 21.9699 | 25.8468 | 30.284 | 0.04274%
-65.5 | 21 | 500.0694 | 13.6144 | 16.9737 | 21.9619 | 25.6878 | 29.95 | 0.04138%
-65 | 21 | 479.8271 | 13.7466 | 17.0745 | 21.9959 | 25.6593 | 29.8545 | 0.04096%
-64.5 | 21 | 461.031 | 13.0857 | 16.1755 | 20.721 | 24.0894 | 28.2512 | 0.03424%
-64 | 21 | 443.865 | 11.7101 | 14.383 | 18.2876 | 21.1642 | 25.1215 | 0.02346%
-63.5 | 21 | 428.5253 | 9.6154 | 12.3301 | 15.5746 | 17.9523 | 21.2091 | 0.01495%
-63 | 21 | 415.2143 | 7.8902 | 10.1213 | 13.0524 | 14.9892 | 17.6314 | 0.009191%
-62.5 | 21 | 404.1328 | 6.5756 | 8.3042 | 10.9071 | 12.5921 | 14.7454 | 0.005713%
-62 | 21 | 395.4683 | 5.5947 | 7.0028 | 9.1028 | 10.677 | 12.6038 | 0.003618%
-61.5 | 21 | 389.3822 | 4.7312 | 6.0141 | 7.7553 | 9.0524 | 10.8536 | 0.002419%
-61 | 21 | 385.9966 | 3.9199 | 5.1823 | 6.6272 | 7.6965 | 9.1732 | 0.001651%
-60.5 | 21 | 385.3826 | 3.259 | 4.2421 | 5.604 | 6.4721 | 7.6636 | 0.0011%
-60 | 21 | 387.5534 | 2.6771 | 3.4221 | 4.5587 | 5.3529 | 6.294 | 0.0006749%
-59.5 | 21 | 392.4628 | 2.115 | 2.7174 | 3.5583 | 4.1925 | 5.0816 | 0.0003836%
-59 | 21 | 400.01 | 1.5046 | 2.0027 | 2.66 | 3.1088 | 3.7328 | 0.0002161%
-90 | 21.5 | 1966.1519 | 2.7835 | 4.0883 | 6.0861 | 7.5301 | 9.667 | 0.005223%
-89.5 | 21.5 | 1934.2796 | 2.5151 | 3.6885 | 5.617 | 6.9639 | 8.9616 | 0.004814%
-89 | 21.5 | 1902.4294 | 2.3381 | 3.4381 | 5.3323 | 6.6529 | 8.6252 | 0.004785%
-88.5 | 21.5 | 1870.6027 | 2.1619 | 3.2082 | 5.0272 | 6.3192 | 8.2477 | 0.004678%
-88 | 21.5 | 1838.8012 | 2.0145 | 3.0002 | 4.6257 | 5.8753 | 7.6576 | 0.004058%
-87.5 | 21.5 | 1807.0262 | 1.8895 | 2.7884 | 4.1647 | 5.2886 | 6.8191 | 0.002974%
-87 | 21.5 | 1775.2797 | 1.8419 | 2.673 | 3.8559 | 4.8185 | 6.1132 | 0.001992%
-86.5 | 21.5 | 1743.5633 | 1.8678 | 2.6577 | 3.7326 | 4.5891 | 5.7212 | 0.0014%
-86 | 21.5 | 1711.879 | 1.9611 | 2.7143 | 3.7392 | 4.5435 | 5.57 | 0.001041%
-85.5 | 21.5 | 1680.229 | 2.0898 | 2.8063 | 3.8245 | 4.6169 | 5.5672 | 0.0008355%
-85 | 21.5 | 1648.6154 | 2.2776 | 2.9735 | 4.0601 | 4.9069 | 5.7779 | 0.0007972%
-84.5 | 21.5 | 1617.0407 | 2.5276 | 3.3521 | 4.6619 | 5.497 | 6.4634 | 0.001106%
-84 | 21.5 | 1585.5075 | 2.9572 | 4.0835 | 5.6906 | 6.7054 | 8.1293 | 0.002252%
-83.5 | 21.5 | 1554.0186 | 3.7921 | 5.4539 | 7.5977 | 9.2951 | 11.7261 | 0.006072%
-83 | 21.5 | 1522.5769 | 5.3828 | 7.6593 | 11.5465 | 14.2657 | 18.2837 | 0.01659%
-82.5 | 21.5 | 1491.1858 | 7.7514 | 12.0304 | 18.392 | 23.8098 | 30.6914 | 0.04425%
-82 | 21.5 | 1459.8487 | 11.4579 | 17.4515 | 27.8287 | 34.8512 | 45.3823 | 0.08465%
-81.5 | 21.5 | 1428.5695 | 13.4674 | 20.9375 | 32.3602 | 40.7957 | 53.5379 | 0.1108%
-81 | 21.5 | 1397.3524 | 12.9274 | 19.7631 | 30.6705 | 38.5037 | 50.282 | 0.101%
-80.5 | 21.5 | 1366.2018 | 10.6944 | 15.6867 | 24.0652 | 30.0552 | 38.3813 | 0.06579%
-80 | 21.5 | 1335.1227 | 9.1402 | 13.0308 | 18.2543 | 22.4081 | 27.9286 | 0.03617%
-79.5 | 21.5 | 1304.1204 | 9.8018 | 13.5244 | 18.4952 | 22.3739 | 27.2986 | 0.03402%
-79 | 21.5 | 1273.2009 | 12.1353 | 16.2991 | 23.0055 | 27.5146 | 32.5051 | 0.05245%
-78.5 | 21.5 | 1242.3704 | 14.511 | 20.0733 | 28.0842 | 32.7186 | 39.1408 | 0.08055%
-78 | 21.5 | 1211.6363 | 16.596 | 23.3484 | 31.3328 | 36.6834 | 44.1379 | 0.1072%
-77.5 | 21.5 | 1181.006 | 18.1991 | 25.7999 | 33.5876 | 39.4329 | 47.6014 | 0.1302%
-77 | 21.5 | 1150.4884 | 20.1512 | 27.8072 | 36.6164 | 43.2884 | 52.6832 | 0.1624%
-76.5 | 21.5 | 1120.0927 | 23.9014 | 31.8851 | 43.2878 | 52.1346 | 62.8678 | 0.2393%
-76 | 21.5 | 1089.8294 | 28.509 | 38.298 | 54.0676 | 64.0272 | 76.1268 | 0.3677%
-75.5 | 21.5 | 1059.7102 | 32.06 | 44.3957 | 62.8 | 73.7876 | 89.1558 | 0.4877%
-75 | 21.5 | 1029.748 | 29.4362 | 40.0362 | 57.345 | 66.9707 | 79.9431 | 0.3998%
-74.5 | 21.5 | 999.957 | 22.4291 | 30.57 | 41.5264 | 50.0308 | 60.8509 | 0.2123%
-74 | 21.5 | 970.3534 | 16.5659 | 23.1378 | 31.2402 | 36.7129 | 44.369 | 0.1068%
-73.5 | 21.5 | 940.9549 | 13.222 | 17.6399 | 24.7036 | 28.9024 | 34.2276 | 0.05957%
-73 | 21.5 | 911.7818 | 11.708 | 15.1926 | 20.5975 | 24.7863 | 29.4672 | 0.04019%
-72.5 | 21.5 | 882.8566 | 11.4583 | 14.7611 | 19.8438 | 23.7567 | 28.5762 | 0.03648%
-72 | 21.5 | 854.2048 | 11.992 | 15.5128 | 20.9554 | 25.1615 | 30.0497 | 0.04183%
-71.5 | 21.5 | 825.8549 | 12.7798 | 16.6078 | 22.555 | 26.8885 | 32.0141 | 0.04936%
-71 | 21.5 | 797.8395 | 13.2715 | 17.2426 | 23.4103 | 27.6827 | 32.9156 | 0.05317%
-70.5 | 21.5 | 770.1953 | 13.1512 | 16.9845 | 22.8995 | 27.1099 | 32.1029 | 0.05005%
-70 | 21.5 | 742.9638 | 12.4674 | 15.945 | 21.2544 | 25.3146 | 29.9295 | 0.04152%
-69.5 | 21.5 | 716.1926 | 11.5285 | 14.5896 | 19.2097 | 22.7087 | 27.2692 | 0.03152%
-69 | 21.5 | 689.9352 | 10.419 | 13.4557 | 17.5546 | 20.6364 | 24.9491 | 0.02494%
-68.5 | 21.5 | 664.2529 | 9.821 | 12.8392 | 16.7014 | 19.5985 | 23.645 | 0.02188%
-68 | 21.5 | 639.2153 | 9.5583 | 12.5752 | 16.3782 | 19.2337 | 23.2253 | 0.02107%
-67.5 | 21.5 | 614.9012 | 9.2554 | 12.2481 | 15.9513 | 18.7317 | 22.6181 | 0.01982%
-67 | 21.5 | 591.4002 | 8.7373 | 11.6294 | 15.0672 | 17.6379 | 21.2188 | 0.01678%
-66.5 | 21.5 | 568.8131 | 8.2027 | 10.7821 | 14.0075 | 16.2919 | 19.4518 | 0.01309%
-66 | 21.5 | 547.2534 | 7.938 | 10.2752 | 13.3207 | 15.3787 | 18.2023 | 0.01048%
-65.5 | 21.5 | 526.8474 | 7.923 | 10.1662 | 13.0985 | 15.0418 | 17.6927 | 0.009264%
-65 | 21.5 | 507.7344 | 7.8642 | 10.0368 | 12.9068 | 14.78 | 17.3275 | 0.008525%
-64.5 | 21.5 | 490.0658 | 7.5058 | 9.509 | 12.3037 | 14.0606 | 16.4447 | 0.007301%
-64 | 21.5 | 474.0033 | 6.8419 | 8.5845 | 11.1899 | 12.8128 | 14.9453 | 0.005551%
-63.5 | 21.5 | 459.7155 | 6.0261 | 7.4915 | 9.6606 | 11.2765 | 13.1473 | 0.003765%
-63 | 21.5 | 447.3724 | 5.198 | 6.4151 | 8.2024 | 9.525 | 11.3513 | 0.002312%
-62.5 | 21.5 | 437.1391 | 4.2456 | 5.4755 | 6.9553 | 8.0445 | 9.5421 | 0.001567%
-62 | 21.5 | 429.1665 | 3.5537 | 4.6089 | 5.9544 | 6.864 | 8.1101 | 0.001095%
-61.5 | 21.5 | 423.5823 | 3.025 | 3.8713 | 5.1465 | 5.9136 | 6.9608 | 0.0007895%
-61 | 21.5 | 420.4818 | 2.5741 | 3.2625 | 4.3032 | 5.0898 | 5.9666 | 0.0005435%
-60.5 | 21.5 | 419.9199 | 2.1395 | 2.7321 | 3.5669 | 4.195 | 5.0743 | 0.0003566%
-60 | 21.5 | 421.9069 | 1.658 | 2.2213 | 2.882 | 3.3693 | 4.047 | 0.0002316%
-59.5 | 21.5 | 426.4072 | 1.2262 | 1.5999 | 2.1831 | 2.5553 | 3.0506 | 0.0001428%
-59 | 21.5 | 433.3422 | 0.85131 | 1.0924 | 1.4619 | 1.7453 | 2.1486 | 5.879e-05%
-90 | 22 | 1970.8091 | 2.1005 | 3.0768 | 4.7103 | 5.8611 | 7.4287 | 0.003481%
-89.5 | 22 | 1939.1184 | 1.8743 | 2.8085 | 4.2872 | 5.4411 | 6.8943 | 0.003297%
-89 | 22 | 1907.4538 | 1.7263 | 2.6295 | 4.013 | 5.1665 | 6.5615 | 0.003222%
-88.5 | 22 | 1875.817 | 1.6015 | 2.4738 | 3.7759 | 4.8834 | 6.2663 | 0.003111%
-88 | 22 | 1844.2097 | 1.453 | 2.2786 | 3.4729 | 4.4877 | 5.8585 | 0.002878%
-87.5 | 22 | 1812.6337 | 1.3298 | 2.0594 | 3.1623 | 4.0611 | 5.3774 | 0.002473%
-87 | 22 | 1781.0911 | 1.2572 | 1.9101 | 2.9201 | 3.7054 | 4.9001 | 0.001949%
-86.5 | 22 | 1749.5837 | 1.2483 | 1.8561 | 2.7814 | 3.4664 | 4.4883 | 0.00139%
-86 | 22 | 1718.114 | 1.2397 | 1.8184 | 2.6828 | 3.289 | 4.1771 | 0.001029%
-85.5 | 22 | 1686.6842 | 1.255 | 1.8281 | 2.6528 | 3.2057 | 4.0031 | 0.0008057%
-85 | 22 | 1655.297 | 1.3366 | 1.9626 | 2.7834 | 3.3511 | 4.1664 | 0.0007931%
-84.5 | 22 | 1623.955 | 1.5428 | 2.317 | 3.2396 | 3.9722 | 5.0456 | 0.001285%
-84 | 22 | 1592.6612 | 2.0787 | 2.9912 | 4.4454 | 5.5614 | 7.0567 | 0.002827%
-83.5 | 22 | 1561.4188 | 2.9657 | 4.5089 | 6.9357 | 8.9094 | 11.852 | 0.008878%
-83 | 22 | 1530.2312 | 4.885 | 7.6521 | 12.5073 | 16.0245 | 21.4321 | 0.02518%
-82.5 | 22 | 1499.1021 | 8.6012 | 14.2722 | 23.6126 | 30.1689 | 39.0612 | 0.06578%
-82 | 22 | 1468.0355 | 13.8658 | 22.5255 | 34.7522 | 44.1003 | 58.2662 | 0.1237%
-81.5 | 22 | 1437.0357 | 17.0307 | 27.6551 | 41.5847 | 53.2951 | 66.7779 | 0.1683%
-81 | 22 | 1406.1074 | 15.6413 | 25.7362 | 38.3956 | 48.9501 | 62.7896 | 0.1478%
-80.5 | 22 | 1375.2557 | 11.6627 | 18.165 | 29.1194 | 36.5955 | 47.8501 | 0.09115%
-80 | 22 | 1344.4861 | 7.818 | 12.0099 | 18.0392 | 23.1035 | 29.7439 | 0.04177%
-79.5 | 22 | 1313.8046 | 6.7516 | 9.6495 | 13.6668 | 16.4038 | 20.322 | 0.01893%
-79 | 22 | 1283.2179 | 7.1822 | 10.2252 | 13.9476 | 16.4565 | 19.9818 | 0.01729%
-78.5 | 22 | 1252.7332 | 8.2602 | 11.8154 | 15.6829 | 18.6305 | 22.803 | 0.02264%
-78 | 22 | 1222.3583 | 9.5097 | 13.0894 | 17.566 | 21.0076 | 25.8755 | 0.02939%
-77.5 | 22 | 1192.1018 | 10.7846 | 14.2793 | 19.3076 | 23.1964 | 27.7266 | 0.0348%
-77 | 22 | 1161.9734 | 11.9711 | 15.6746 | 21.4759 | 25.9396 | 30.1515 | 0.04402%
-76.5 | 22 | 1131.9835 | 13.1915 | 17.6386 | 24.7662 | 28.8675 | 34.026 | 0.05931%
-76 | 22 | 1102.1436 | 14.5457 | 19.9346 | 27.8156 | 32.408 | 38.7724 | 0.07896%
-75.5 | 22 | 1072.4665 | 15.2723 | 21.2536 | 29.4144 | 34.5243 | 41.6631 | 0.09131%
-75 | 22 | 1042.9664 | 14.4855 | 20.0297 | 28.0922 | 32.8444 | 39.4553 | 0.08114%
-74.5 | 22 | 1013.659 | 12.5526 | 16.9186 | 23.9777 | 28.3178 | 33.4627 | 0.05647%
-74 | 22 | 984.5616 | 10.1777 | 13.7896 | 18.8104 | 22.7203 | 27.4803 | 0.03437%
-73.5 | 22 | 955.6939 | 8.2425 | 11.5353 | 15.1862 | 17.9509 | 21.8432 | 0.01979%
-73 | 22 | 927.0774 | 7.2729 | 9.8496 | 13.2509 | 15.466 | 18.5418 | 0.01312%
-72.5 | 22 | 898.7364 | 7.025 | 9.3684 | 12.6778 | 14.7841 | 17.706 | 0.01154%
-72 | 22 | 870.698 | 7.2214 | 9.6303 | 12.9823 | 15.1963 | 18.2802 | 0.01242%
-71.5 | 22 | 842.9926 | 7.5644 | 10.1314 | 13.5484 | 15.8928 | 19.166 | 0.01386%
-71 | 22 | 815.6546 | 7.7785 | 10.4253 | 13.8403 | 16.2238 | 19.5491 | 0.01437%
-70.5 | 22 | 788.7221 | 7.7052 | 10.268 | 13.6107 | 15.905 | 19.095 | 0.01336%
-70 | 22 | 762.2386 | 7.3556 | 9.6956 | 12.9141 | 15.0207 | 17.9348 | 0.01124%
-69.5 | 22 | 736.2526 | 6.873 | 8.9454 | 12.0075 | 13.8951 | 16.4919 | 0.008936%
-69 | 22 | 710.8189 | 6.4284 | 8.2806 | 11.1306 | 12.9053 | 15.246 | 0.007169%
-68.5 | 22 | 685.9993 | 6.118 | 7.8372 | 10.4666 | 12.2656 | 14.4662 | 0.006173%
-68 | 22 | 661.8628 | 5.9144 | 7.5622 | 10.0773 | 11.892 | 14.0336 | 0.005724%
-67.5 | 22 | 638.4874 | 5.7224 | 7.3016 | 9.7066 | 11.5242 | 13.6005 | 0.00528%
-67 | 22 | 615.9598 | 5.4883 | 6.9652 | 9.2009 | 10.8985 | 12.9446 | 0.004457%
-66.5 | 22 | 594.3765 | 5.262 | 6.6171 | 8.6483 | 10.1776 | 12.166 | 0.003477%
-66 | 22 | 573.8444 | 5.1272 | 6.3814 | 8.2403 | 9.6266 | 11.5358 | 0.002696%
-65.5 | 22 | 554.4805 | 5.0678 | 6.2617 | 8.01 | 9.3042 | 11.0917 | 0.002178%
-65 | 22 | 536.4113 | 4.9475 | 6.1311 | 7.796 | 9.0226 | 10.7102 | 0.001882%
-64.5 | 22 | 519.772 | 4.6609 | 5.8601 | 7.4182 | 8.5621 | 10.1311 | 0.001622%
-64 | 22 | 504.7044 | 4.2219 | 5.4181 | 6.829 | 7.8612 | 9.273 | 0.00131%
-63.5 | 22 | 491.353 | 3.7167 | 4.7913 | 6.096 | 6.9991 | 8.2309 | 0.000983%
-63 | 22 | 479.8614 | 3.2242 | 4.0917 | 5.3383 | 6.1128 | 7.1661 | 0.0007065%
-62.5 | 22 | 470.3658 | 2.7731 | 3.4821 | 4.5429 | 5.2927 | 6.1848 | 0.0004816%
-62 | 22 | 462.9892 | 2.3778 | 2.9655 | 3.8384 | 4.4907 | 5.3423 | 0.0003119%
-61.5 | 22 | 457.8342 | 1.9533 | 2.5244 | 3.2498 | 3.7894 | 4.5379 | 0.0002325%
-61 | 22 | 454.9762 | 1.5836 | 2.0856 | 2.7207 | 3.1639 | 3.7767 | 0.0001725%
-60.5 | 22 | 454.4587 | 1.2404 | 1.6062 | 2.1724 | 2.5374 | 3.0193 | 0.0001203%
-60 | 22 | 456.2895 | 0.91085 | 1.1673 | 1.5596 | 1.8602 | 2.2817 | 6.521e-05%
-59.5 | 22 | 460.4408 | 0.55759 | 0.7084 | 0.93698 | 1.1107 | 1.3561 | 1.368e-05%
-59 | 22 | 466.8504 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 22.5 | 1976.0097 | 1.7015 | 2.5646 | 3.8443 | 4.9175 | 6.1866 | 0.002657%
-89.5 | 22.5 | 1944.5102 | 1.5836 | 2.4151 | 3.6105 | 4.6108 | 5.8798 | 0.002487%
-89 | 22.5 | 1913.0411 | 1.5285 | 2.3437 | 3.4985 | 4.4636 | 5.7324 | 0.002404%
-88.5 | 22.5 | 1881.6042 | 1.4334 | 2.2153 | 3.3222 | 4.2415 | 5.5169 | 0.002346%
-88 | 22.5 | 1850.2015 | 1.3144 | 2.0247 | 3.0971 | 3.9587 | 5.2353 | 0.002288%
-87.5 | 22.5 | 1818.8351 | 1.2436 | 1.9085 | 2.948 | 3.7649 | 5.0166 | 0.002182%
-87 | 22.5 | 1787.5071 | 1.1505 | 1.7556 | 2.7455 | 3.5005 | 4.6551 | 0.001966%
-86.5 | 22.5 | 1756.2199 | 1.0676 | 1.6155 | 2.5477 | 3.2357 | 4.2832 | 0.001705%
-86 | 22.5 | 1724.976 | 0.99291 | 1.485 | 2.3523 | 2.9633 | 3.8856 | 0.001392%
-85.5 | 22.5 | 1693.7781 | 0.93493 | 1.3877 | 2.2013 | 2.7587 | 3.5741 | 0.001163%
-85 | 22.5 | 1662.6291 | 0.91438 | 1.3726 | 2.2062 | 2.7622 | 3.5744 | 0.001252%
-84.5 | 22.5 | 1631.5319 | 1.0304 | 1.6149 | 2.6094 | 3.3308 | 4.4354 | 0.00213%
-84 | 22.5 | 1600.49 | 1.4495 | 2.3856 | 3.81 | 5.0652 | 6.6083 | 0.004457%
-83.5 | 22.5 | 1569.5069 | 2.4164 | 3.9132 | 6.482 | 8.5446 | 11.7191 | 0.01072%
-83 | 22.5 | 1538.5864 | 4.348 | 7.2815 | 12.3815 | 15.9205 | 21.383 | 0.02674%
-82.5 | 22.5 | 1507.7326 | 8.3222 | 14.2015 | 23.6577 | 30.2405 | 39.1637 | 0.06607%
-82 | 22.5 | 1476.9501 | 13.867 | 22.6951 | 35.0122 | 44.4629 | 58.6284 | 0.1249%
-81.5 | 22.5 | 1446.2435 | 17.1111 | 27.8744 | 41.9679 | 53.8277 | 67.2566 | 0.1703%
-81 | 22.5 | 1415.6183 | 15.6142 | 25.9118 | 38.6843 | 49.3617 | 63.183 | 0.1489%
-80.5 | 22.5 | 1385.0799 | 11.2505 | 17.9205 | 29.1389 | 36.6684 | 48.0197 | 0.09058%
-80 | 22.5 | 1354.6346 | 6.6266 | 10.7459 | 16.9552 | 22.1897 | 29.1743 | 0.04099%
-79.5 | 22.5 | 1324.289 | 5.02 | 7.1396 | 10.7309 | 13.266 | 16.7644 | 0.01411%
-79 | 22.5 | 1294.0504 | 4.7417 | 6.5077 | 9.1593 | 11.2759 | 13.4613 | 0.007641%
-78.5 | 22.5 | 1263.9268 | 5.1648 | 6.8671 | 9.5787 | 11.6297 | 13.5817 | 0.007002%
-78 | 22.5 | 1233.9269 | 5.6503 | 7.5696 | 10.6521 | 12.4992 | 14.6366 | 0.008187%
-77.5 | 22.5 | 1204.0601 | 6.2065 | 8.4031 | 11.7842 | 13.5463 | 15.9528 | 0.009864%
-77 | 22.5 | 1174.3369 | 6.8245 | 9.3743 | 12.8018 | 14.8357 | 17.638 | 0.01222%
-76.5 | 22.5 | 1144.7688 | 7.4986 | 10.4987 | 14.0424 | 16.468 | 19.8536 | 0.01616%
-76 | 22.5 | 1115.3682 | 8.094 | 11.5164 | 15.257 | 18.1037 | 22.1283 | 0.02097%
-75.5 | 22.5 | 1086.1491 | 8.3202 | 11.8173 | 15.8184 | 18.8883 | 23.2583 | 0.02365%
-75 | 22.5 | 1057.1268 | 7.9472 | 11.389 | 15.2068 | 18.1124 | 22.2374 | 0.02155%
-74.5 | 22.5 | 1028.3182 | 7.0956 | 9.9527 | 13.6257 | 16.0541 | 19.4609 | 0.01605%
-74 | 22.5 | 999.742 | 6.1352 | 8.3441 | 11.7877 | 13.6777 | 16.2854 | 0.0107%
-73.5 | 22.5 | 971.419 | 5.3722 | 7.0727 | 9.7523 | 11.7288 | 13.743 | 0.00671%
-73 | 22.5 | 943.3722 | 4.8462 | 6.3231 | 8.4725 | 10.1229 | 12.1889 | 0.004453%
-72.5 | 22.5 | 915.6273 | 4.6105 | 6.0497 | 8.0159 | 9.5125 | 11.589 | 0.003794%
-72 | 22.5 | 888.2127 | 4.6645 | 6.0996 | 8.0936 | 9.613 | 11.7017 | 0.003877%
-71.5 | 22.5 | 861.1603 | 4.8303 | 6.2666 | 8.3428 | 9.929 | 12.0345 | 0.004131%
-71 | 22.5 | 834.5055 | 4.9396 | 6.3635 | 8.4689 | 10.0768 | 12.1734 | 0.004158%
-70.5 | 22.5 | 808.2879 | 4.8844 | 6.2887 | 8.3298 | 9.8829 | 11.9512 | 0.003866%
-70 | 22.5 | 782.5517 | 4.66 | 6.0427 | 7.9415 | 9.3774 | 11.3967 | 0.003356%
-69.5 | 22.5 | 757.3461 | 4.3477 | 5.7004 | 7.4255 | 8.721 | 10.532 | 0.002668%
-69 | 22.5 | 732.7262 | 4.0514 | 5.3662 | 6.9373 | 8.1101 | 9.7414 | 0.002131%
-68.5 | 22.5 | 708.7531 | 3.8209 | 5.1005 | 6.5662 | 7.6566 | 9.169 | 0.00181%
-68 | 22.5 | 685.495 | 3.6452 | 4.8381 | 6.2944 | 7.3347 | 8.7767 | 0.001655%
-67.5 | 22.5 | 663.0273 | 3.5023 | 4.6183 | 6.0602 | 7.0565 | 8.4364 | 0.001513%
-67 | 22.5 | 641.4332 | 3.3597 | 4.3929 | 5.7976 | 6.7357 | 8.0317 | 0.001308%
-66.5 | 22.5 | 620.8041 | 3.2304 | 4.1785 | 5.5248 | 6.3922 | 7.5851 | 0.001058%
-66 | 22.5 | 601.2396 | 3.1468 | 4.0254 | 5.3092 | 6.1103 | 7.2057 | 0.0008323%
-65.5 | 22.5 | 582.8469 | 3.089 | 3.9163 | 5.1503 | 5.9003 | 6.9208 | 0.0006755%
-65 | 22.5 | 565.7407 | 3.0141 | 3.7955 | 4.9686 | 5.6984 | 6.6599 | 0.000565%
-64.5 | 22.5 | 550.0409 | 2.8847 | 3.6107 | 4.6933 | 5.4257 | 6.3257 | 0.000466%
-64 | 22.5 | 535.8715 | 2.685 | 3.3406 | 4.3118 | 5.0358 | 5.8673 | 0.0003654%
-63.5 | 22.5 | 523.3568 | 2.4271 | 3.0024 | 3.8494 | 4.4776 | 5.3032 | 0.0002552%
-63 | 22.5 | 512.6182 | 2.0955 | 2.6383 | 3.363 | 3.898 | 4.6352 | 0.0001806%
-62.5 | 22.5 | 503.7693 | 1.7437 | 2.2751 | 2.887 | 3.337 | 3.9553 | 0.0001354%
-62 | 22.5 | 496.9112 | 1.4348 | 1.8408 | 2.4212 | 2.7935 | 3.304 | 9.982e-05%
-61.5 | 22.5 | 492.1272 | 1.1656 | 1.4793 | 1.9543 | 2.3048 | 2.7208 | 6.759e-05%
-61 | 22.5 | 489.4781 | 0.87837 | 1.1099 | 1.4588 | 1.7227 | 2.0938 | 3.575e-05%
-60.5 | 22.5 | 488.9986 | 0.57821 | 0.73029 | 0.95932 | 1.1324 | 1.3758 | 1.162e-05%
-60 | 22.5 | 490.6951 | 0.14259 | 0.18131 | 0.24005 | 0.28473 | 0.34787 | 4.273e-07%
-59.5 | 22.5 | 494.5452 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 22.5 | 500.4992 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 23 | 1981.7494 | 1.5431 | 2.3497 | 3.4754 | 4.4097 | 5.6402 | 0.002202%
-89.5 | 23 | 1950.4504 | 1.5014 | 2.298 | 3.4005 | 4.3157 | 5.5512 | 0.00218%
-89 | 23 | 1919.1862 | 1.4462 | 2.2255 | 3.3128 | 4.2128 | 5.462 | 0.002209%
-88.5 | 23 | 1887.959 | 1.3901 | 2.141 | 3.2271 | 4.1151 | 5.3802 | 0.002265%
-88 | 23 | 1856.7709 | 1.3664 | 2.1073 | 3.1962 | 4.0837 | 5.3595 | 0.002314%
-87.5 | 23 | 1825.6242 | 1.3142 | 2.0269 | 3.1052 | 3.9737 | 5.256 | 0.002325%
-87 | 23 | 1794.5213 | 1.2566 | 1.9339 | 2.9888 | 3.825 | 5.1024 | 0.002273%
-86.5 | 23 | 1763.4649 | 1.1833 | 1.811 | 2.8233 | 3.6061 | 4.8057 | 0.002077%
-86 | 23 | 1732.4576 | 1.0664 | 1.6188 | 2.5597 | 3.2573 | 4.3218 | 0.001769%
-85.5 | 23 | 1701.5026 | 0.95427 | 1.4399 | 2.3135 | 2.925 | 3.8518 | 0.001489%
-85 | 23 | 1670.6031 | 0.91706 | 1.3979 | 2.2799 | 2.8772 | 3.7803 | 0.001545%
-84.5 | 23 | 1639.7623 | 0.93958 | 1.4957 | 2.4963 | 3.217 | 4.3323 | 0.002375%
-84 | 23 | 1608.984 | 1.185 | 2.0358 | 3.398 | 4.576 | 6.0843 | 0.004721%
-83.5 | 23 | 1578.2722 | 1.8639 | 3.2286 | 5.6127 | 7.3383 | 10.0508 | 0.009845%
-83 | 23 | 1547.631 | 3.3197 | 5.8643 | 9.9734 | 13.1055 | 17.2867 | 0.02082%
-82.5 | 23 | 1517.0651 | 6.1709 | 10.868 | 17.5828 | 23.3409 | 30.4759 | 0.04525%
-82 | 23 | 1486.5793 | 10.2715 | 16.8719 | 27.8983 | 35.0573 | 45.8331 | 0.08373%
-81.5 | 23 | 1456.179 | 12.7748 | 20.7178 | 32.7212 | 41.4451 | 54.6909 | 0.1107%
-81 | 23 | 1425.8699 | 11.8892 | 19.0903 | 30.7227 | 38.7904 | 50.9975 | 0.09914%
-80.5 | 23 | 1395.6582 | 7.9418 | 13.6402 | 22.5506 | 29.1459 | 37.6358 | 0.06226%
-80 | 23 | 1365.5507 | 4.9245 | 7.9666 | 13.2382 | 17.1032 | 23.1003 | 0.0289%
-79.5 | 23 | 1335.5546 | 3.3737 | 5.2563 | 7.977 | 10.2807 | 13.3595 | 0.011%
-79 | 23 | 1305.678 | 2.9869 | 4.3455 | 6.2217 | 7.5363 | 9.4372 | 0.004224%
-78.5 | 23 | 1275.9295 | 3.0615 | 4.344 | 5.987 | 7.0397 | 8.5134 | 0.002584%
-78 | 23 | 1246.3186 | 3.3291 | 4.7309 | 6.2943 | 7.3699 | 8.8685 | 0.002455%
-77.5 | 23 | 1216.8554 | 3.6973 | 5.2284 | 6.8371 | 8.0488 | 9.7472 | 0.002884%
-77 | 23 | 1187.5514 | 4.1116 | 5.6571 | 7.5115 | 8.9253 | 10.9272 | 0.003799%
-76.5 | 23 | 1158.4188 | 4.518 | 6.0966 | 8.2469 | 9.9104 | 12.0154 | 0.004904%
-76 | 23 | 1129.4713 | 4.827 | 6.4517 | 8.8738 | 10.7724 | 12.8245 | 0.005966%
-75.5 | 23 | 1100.7235 | 4.9095 | 6.5715 | 9.1183 | 11.1286 | 13.1669 | 0.00658%
-75 | 23 | 1072.1919 | 4.6895 | 6.3529 | 8.79 | 10.7092 | 12.8016 | 0.006265%
-74.5 | 23 | 1043.8944 | 4.2433 | 5.8541 | 7.9788 | 9.6324 | 11.8266 | 0.00517%
-74 | 23 | 1015.8509 | 3.7354 | 5.2525 | 6.992 | 8.3208 | 10.2053 | 0.003489%
-73.5 | 23 | 988.0832 | 3.3045 | 4.5666 | 6.1287 | 7.1849 | 8.6586 | 0.002196%
-73 | 23 | 960.6155 | 3.0327 | 4.0782 | 5.556 | 6.4506 | 7.6855 | 0.001532%
-72.5 | 23 | 933.4745 | 2.9255 | 3.873 | 5.2976 | 6.1435 | 7.3098 | 0.001294%
-72 | 23 | 906.6898 | 2.924 | 3.8558 | 5.2692 | 6.1315 | 7.3249 | 0.001298%
-71.5 | 23 | 880.2941 | 2.9723 | 3.9225 | 5.3463 | 6.2353 | 7.4688 | 0.001364%
-71 | 23 | 854.3238 | 3.0073 | 3.9666 | 5.3904 | 6.2847 | 7.5249 | 0.001363%
-70.5 | 23 | 828.8191 | 2.9775 | 3.9121 | 5.3135 | 6.1812 | 7.3817 | 0.001261%
-70 | 23 | 803.8244 | 2.8837 | 3.7609 | 5.1183 | 5.9328 | 7.0552 | 0.001082%
-69.5 | 23 | 779.3892 | 2.7524 | 3.5578 | 4.802 | 5.6096 | 6.6379 | 0.0008728%
-69 | 23 | 755.5679 | 2.6061 | 3.3421 | 4.4692 | 5.2792 | 6.2209 | 0.0007045%
-68.5 | 23 | 732.4205 | 2.4746 | 3.1555 | 4.1916 | 4.9819 | 5.8794 | 0.0005877%
-68 | 23 | 710.0133 | 2.3702 | 3.0118 | 3.9845 | 4.7239 | 5.6276 | 0.0005055%
-67.5 | 23 | 688.4188 | 2.2718 | 2.8785 | 3.7955 | 4.4907 | 5.3955 | 0.0004404%
-67 | 23 | 667.7158 | 2.1584 | 2.7581 | 3.618 | 4.2673 | 5.1612 | 0.0003938%
-66.5 | 23 | 647.9901 | 2.0758 | 2.6623 | 3.4634 | 4.0644 | 4.9038 | 0.0003177%
-66 | 23 | 629.3338 | 2.005 | 2.5748 | 3.3187 | 3.8726 | 4.6416 | 0.0002425%
-65.5 | 23 | 611.8448 | 1.9493 | 2.5037 | 3.1996 | 3.7143 | 4.4247 | 0.0001871%
-65 | 23 | 595.6262 | 1.8831 | 2.4253 | 3.0793 | 3.5606 | 4.222 | 0.0001504%
-64.5 | 23 | 580.7845 | 1.7786 | 2.307 | 2.9153 | 3.3613 | 3.9723 | 0.0001228%
-64 | 23 | 567.4279 | 1.6397 | 2.115 | 2.701 | 3.1071 | 3.662 | 0.0001003%
-63.5 | 23 | 555.6636 | 1.4743 | 1.8768 | 2.4405 | 2.8016 | 3.294 | 7.852e-05%
-63 | 23 | 545.5947 | 1.2817 | 1.613 | 2.11 | 2.4445 | 2.8679 | 5.555e-05%
-62.5 | 23 | 537.3167 | 1.0633 | 1.3272 | 1.7194 | 2.0127 | 2.3962 | 3.336e-05%
-62 | 23 | 530.9134 | 0.84196 | 1.0457 | 1.3469 | 1.5712 | 1.8823 | 1.509e-05%
-61.5 | 23 | 526.4531 | 0.58048 | 0.7209 | 0.92853 | 1.0831 | 1.2975 | 5.221e-06%
-61 | 23 | 523.9857 | 0.14545 | 0.18491 | 0.24477 | 0.2903 | 0.35463 | 4.457e-07%
-60.5 | 23 | 523.5393 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 23 | 525.1191 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 23 | 528.7068 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 23 | 534.2621 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 23.5 | 1988.0235 | 1.524 | 2.3277 | 3.4475 | 4.3778 | 5.6166 | 0.00222%
-89.5 | 23.5 | 1956.934 | 1.5226 | 2.3344 | 3.4798 | 4.4363 | 5.6992 | 0.002366%
-89 | 23.5 | 1925.884 | 1.5401 | 2.3665 | 3.5529 | 4.5491 | 5.8396 | 0.002555%
-88.5 | 23.5 | 1894.8758 | 1.5423 | 2.3805 | 3.6009 | 4.6317 | 5.9543 | 0.002753%
-88 | 23.5 | 1863.9118 | 1.5385 | 2.3866 | 3.6346 | 4.6944 | 6.0494 | 0.002939%
-87.5 | 23.5 | 1832.9945 | 1.5165 | 2.3678 | 3.6259 | 4.6989 | 6.0826 | 0.003077%
-87 | 23.5 | 1802.1266 | 1.4665 | 2.3079 | 3.5447 | 4.6019 | 6.0002 | 0.003101%
-86.5 | 23.5 | 1771.311 | 1.362 | 2.1473 | 3.3289 | 4.3216 | 5.7092 | 0.002959%
-86 | 23.5 | 1740.5508 | 1.2529 | 1.9544 | 3.0611 | 3.9568 | 5.2957 | 0.002635%
-85.5 | 23.5 | 1709.8492 | 1.1115 | 1.7136 | 2.72 | 3.4912 | 4.6795 | 0.002161%
-85 | 23.5 | 1679.2098 | 1.0157 | 1.5616 | 2.5096 | 3.1975 | 4.2489 | 0.001869%
-84.5 | 23.5 | 1648.6363 | 1.0028 | 1.5735 | 2.5647 | 3.2858 | 4.3943 | 0.002178%
-84 | 23.5 | 1618.1328 | 1.1153 | 1.8482 | 3.0513 | 4.0279 | 5.4392 | 0.003626%
-83.5 | 23.5 | 1587.7035 | 1.4785 | 2.58 | 4.4059 | 5.8233 | 7.7425 | 0.006861%
-83 | 23.5 | 1557.3531 | 2.3381 | 4.0306 | 6.8622 | 9.1481 | 12.4288 | 0.01294%
-82.5 | 23.5 | 1527.0866 | 3.676 | 6.4817 | 11.2479 | 14.4246 | 19.206 | 0.02414%
-82 | 23.5 | 1496.9094 | 5.6112 | 9.7483 | 16.1419 | 21.3224 | 28.4562 | 0.04047%
-81.5 | 23.5 | 1466.8272 | 6.7306 | 12.0153 | 19.5469 | 26.1428 | 33.5358 | 0.05268%
-81 | 23.5 | 1436.8463 | 6.2781 | 11.2504 | 18.2375 | 24.3894 | 31.6669 | 0.04815%
-80.5 | 23.5 | 1406.9735 | 4.6477 | 7.9249 | 13.4774 | 17.4971 | 23.7676 | 0.03117%
-80 | 23.5 | 1377.2161 | 3.0203 | 5.2151 | 8.6137 | 11.6256 | 15.1679 | 0.01687%
-79.5 | 23.5 | 1347.5819 | 2.2325 | 3.4428 | 5.5806 | 7.1808 | 9.6527 | 0.007139%
-79 | 23.5 | 1318.0797 | 1.8881 | 2.7975 | 4.1571 | 5.248 | 6.5902 | 0.002705%
-78.5 | 23.5 | 1288.7186 | 1.8984 | 2.6894 | 3.7599 | 4.6099 | 5.622 | 0.001263%
-78 | 23.5 | 1259.5089 | 2.0814 | 2.8139 | 3.8621 | 4.6823 | 5.5806 | 0.0008956%
-77.5 | 23.5 | 1230.4616 | 2.3134 | 3.0468 | 4.2029 | 5.0999 | 5.9177 | 0.0009225%
-77 | 23.5 | 1201.5888 | 2.4919 | 3.3232 | 4.6516 | 5.4847 | 6.4241 | 0.001147%
-76.5 | 23.5 | 1172.9036 | 2.6617 | 3.5988 | 5.106 | 5.8953 | 6.9784 | 0.001475%
-76 | 23.5 | 1144.4203 | 2.7744 | 3.7953 | 5.3435 | 6.216 | 7.4231 | 0.001765%
-75.5 | 23.5 | 1116.1547 | 2.8007 | 3.852 | 5.4231 | 6.3318 | 7.594 | 0.00192%
-75 | 23.5 | 1088.124 | 2.7182 | 3.7285 | 5.2923 | 6.1707 | 7.3892 | 0.001844%
-74.5 | 23.5 | 1060.3471 | 2.5417 | 3.4481 | 4.9238 | 5.7636 | 6.8532 | 0.001548%
-74 | 23.5 | 1032.8448 | 2.3276 | 3.1002 | 4.3334 | 5.2368 | 6.1627 | 0.001136%
-73.5 | 23.5 | 1005.6397 | 2.104 | 2.8042 | 3.8207 | 4.6116 | 5.5368 | 0.0007935%
-73 | 23.5 | 978.757 | 1.9186 | 2.5868 | 3.4534 | 4.1169 | 5.0597 | 0.0005922%
-72.5 | 23.5 | 952.2242 | 1.8362 | 2.4825 | 3.2825 | 3.8904 | 4.7486 | 0.0004653%
-72 | 23.5 | 926.0715 | 1.8332 | 2.4709 | 3.2674 | 3.8727 | 4.7274 | 0.000454%
-71.5 | 23.5 | 900.3325 | 1.8643 | 2.5007 | 3.3143 | 3.9337 | 4.8095 | 0.0004743%
-71 | 23.5 | 875.0437 | 1.8774 | 2.5116 | 3.3286 | 3.9505 | 4.83 | 0.000473%
-70.5 | 23.5 | 850.2456 | 1.853 | 2.4787 | 3.2737 | 3.8772 | 4.7287 | 0.000432%
-70 | 23.5 | 825.9827 | 1.7849 | 2.396 | 3.1461 | 3.713 | 4.5096 | 0.0003654%
-69.5 | 23.5 | 802.3036 | 1.6872 | 2.2782 | 2.9709 | 3.4915 | 4.2198 | 0.0002937%
-69 | 23.5 | 779.2619 | 1.5868 | 2.1255 | 2.7935 | 3.2705 | 3.9351 | 0.0002404%
-68.5 | 23.5 | 756.9159 | 1.4842 | 1.9679 | 2.6183 | 3.0571 | 3.6666 | 0.0002028%
-68 | 23.5 | 735.3293 | 1.4013 | 1.8458 | 2.4808 | 2.8933 | 3.4656 | 0.0001813%
-67.5 | 23.5 | 714.5711 | 1.339 | 1.754 | 2.373 | 2.765 | 3.3083 | 0.0001631%
-67 | 23.5 | 694.7158 | 1.2922 | 1.6801 | 2.2774 | 2.6481 | 3.1606 | 0.0001383%
-66.5 | 23.5 | 675.843 | 1.2386 | 1.5963 | 2.147 | 2.5107 | 2.9859 | 0.0001088%
-66 | 23.5 | 658.0376 | 1.2121 | 1.5457 | 2.0533 | 2.4073 | 2.8474 | 7.99e-05%
-65.5 | 23.5 | 641.3885 | 1.1813 | 1.4911 | 1.9574 | 2.3004 | 2.7065 | 5.758e-05%
-65 | 23.5 | 625.9883 | 1.1465 | 1.4358 | 1.8674 | 2.1911 | 2.5782 | 4.241e-05%
-64.5 | 23.5 | 611.9312 | 1.0929 | 1.3598 | 1.7551 | 2.0498 | 2.4277 | 3.078e-05%
-64 | 23.5 | 599.3121 | 1.0162 | 1.2588 | 1.6164 | 1.882 | 2.2498 | 2.29e-05%
-63.5 | 23.5 | 588.2234 | 0.89282 | 1.1017 | 1.4084 | 1.6352 | 1.9485 | 1.309e-05%
-63 | 23.5 | 578.7534 | 0.75313 | 0.9269 | 1.1813 | 1.3691 | 1.6278 | 6.939e-06%
-62.5 | 23.5 | 570.9826 | 0.52807 | 0.64782 | 0.82252 | 0.95108 | 1.1278 | 1.999e-06%
-62 | 23.5 | 564.9812 | 0.20121 | 0.24989 | 0.32187 | 0.37544 | 0.44978 | 2.56e-07%
-61.5 | 23.5 | 560.8061 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 23.5 | 558.4982 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 23.5 | 558.0808 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 23.5 | 559.5581 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 23.5 | 562.9152 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 23.5 | 568.1186 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 24 | 1994.8268 | 1.5979 | 2.4488 | 3.697 | 4.7496 | 6.0653 | 0.002766%
-89.5 | 24 | 1963.9555 | 1.6838 | 2.5762 | 3.9326 | 5.085 | 6.4529 | 0.003189%
-89 | 24 | 1933.1285 | 1.7732 | 2.7072 | 4.1745 | 5.3581 | 6.8503 | 0.003566%
-88.5 | 24 | 1902.3483 | 1.8506 | 2.8225 | 4.3922 | 5.6076 | 7.2195 | 0.003949%
-88 | 24 | 1871.6175 | 1.915 | 2.9227 | 4.5889 | 5.8399 | 7.5731 | 0.004359%
-87.5 | 24 | 1840.939 | 1.9416 | 2.98 | 4.7248 | 6.0167 | 7.8646 | 0.004805%
-87 | 24 | 1810.3155 | 1.9064 | 2.9577 | 4.7255 | 6.0477 | 7.9558 | 0.005111%
-86.5 | 24 | 1779.7504 | 1.7835 | 2.8047 | 4.4803 | 5.7926 | 7.6306 | 0.004963%
-86 | 24 | 1749.247 | 1.5852 | 2.5262 | 3.9966 | 5.2472 | 6.881 | 0.004323%
-85.5 | 24 | 1718.8088 | 1.3876 | 2.2198 | 3.4594 | 4.5228 | 5.9877 | 0.003372%
-85 | 24 | 1688.4396 | 1.1977 | 1.8771 | 2.9651 | 3.8304 | 5.1557 | 0.002613%
-84.5 | 24 | 1658.1436 | 1.0789 | 1.6848 | 2.6996 | 3.4622 | 4.6359 | 0.002241%
-84 | 24 | 1627.9252 | 1.0764 | 1.7219 | 2.7986 | 3.6239 | 4.9077 | 0.002733%
-83.5 | 24 | 1597.7889 | 1.2004 | 2.0313 | 3.3478 | 4.4726 | 5.9387 | 0.004299%
-83 | 24 | 1567.74 | 1.5234 | 2.6686 | 4.6075 | 6.0533 | 8.1007 | 0.007418%
-82.5 | 24 | 1537.7837 | 2.1085 | 3.6668 | 6.3444 | 8.4168 | 11.6496 | 0.01209%
-82 | 24 | 1507.9258 | 2.7299 | 4.9777 | 8.3336 | 11.3632 | 14.8493 | 0.01741%
-81.5 | 24 | 1478.1727 | 3.1058 | 5.6391 | 9.6027 | 12.7527 | 16.8243 | 0.02054%
-81 | 24 | 1448.5311 | 2.951 | 5.3852 | 9.1029 | 12.2251 | 16.0674 | 0.01937%
-80.5 | 24 | 1419.0082 | 2.3937 | 4.2249 | 7.2414 | 9.7607 | 13.153 | 0.01449%
-80 | 24 | 1389.6119 | 1.6939 | 2.9801 | 5.2674 | 6.8935 | 9.4522 | 0.009432%
-79.5 | 24 | 1360.3507 | 1.2644 | 2.1482 | 3.5436 | 4.7756 | 6.3655 | 0.004842%
-79 | 24 | 1331.2337 | 1.0842 | 1.6799 | 2.6617 | 3.3763 | 4.4631 | 0.001946%
-78.5 | 24 | 1302.2709 | 1.0772 | 1.5665 | 2.372 | 2.853 | 3.5433 | 0.0007524%
-78 | 24 | 1273.4732 | 1.1532 | 1.6317 | 2.3752 | 2.7788 | 3.3405 | 0.0004233%
-77.5 | 24 | 1244.8521 | 1.2681 | 1.7885 | 2.5083 | 2.9243 | 3.5011 | 0.0003608%
-77 | 24 | 1216.4206 | 1.4015 | 1.9914 | 2.7095 | 3.1808 | 3.8394 | 0.0004001%
-76.5 | 24 | 1188.1923 | 1.5097 | 2.1684 | 2.9027 | 3.4385 | 4.1946 | 0.0004971%
-76 | 24 | 1160.1825 | 1.5878 | 2.2844 | 3.0532 | 3.6424 | 4.4802 | 0.0006022%
-75.5 | 24 | 1132.4077 | 1.6 | 2.3013 | 3.0939 | 3.7042 | 4.5754 | 0.0006644%
-75 | 24 | 1104.8857 | 1.55 | 2.2413 | 3.0131 | 3.6034 | 4.4452 | 0.0006334%
-74.5 | 24 | 1077.6362 | 1.4368 | 2.0547 | 2.815 | 3.3488 | 4.1057 | 0.000543%
-74 | 24 | 1050.6808 | 1.2931 | 1.8177 | 2.5529 | 3.0109 | 3.6541 | 0.0004246%
-73.5 | 24 | 1024.0427 | 1.1408 | 1.5702 | 2.272 | 2.6543 | 3.1857 | 0.0003219%
-73 | 24 | 997.7478 | 1.0682 | 1.439 | 2.0383 | 2.4383 | 2.907 | 0.0002279%
-72.5 | 24 | 971.8242 | 1.0404 | 1.3819 | 1.9252 | 2.3294 | 2.7805 | 0.0001822%
-72 | 24 | 946.3024 | 1.0441 | 1.3786 | 1.9075 | 2.3086 | 2.7687 | 0.0001686%
-71.5 | 24 | 921.2163 | 1.0767 | 1.4197 | 1.9612 | 2.3595 | 2.8362 | 0.0001697%
-71 | 24 | 896.6027 | 1.0923 | 1.4385 | 1.9842 | 2.38 | 2.8592 | 0.0001666%
-70.5 | 24 | 872.5016 | 1.0783 | 1.4138 | 1.9403 | 2.3323 | 2.7947 | 0.0001491%
-70 | 24 | 848.957 | 1.0325 | 1.3446 | 1.8304 | 2.2082 | 2.6469 | 0.0001212%
-69.5 | 24 | 826.0168 | 0.97354 | 1.259 | 1.7003 | 2.0412 | 2.4742 | 9.277e-05%
-69 | 24 | 803.7328 | 0.88536 | 1.1361 | 1.5204 | 1.8152 | 2.2348 | 6.483e-05%
-68.5 | 24 | 782.1614 | 0.81624 | 1.0441 | 1.3921 | 1.6582 | 2.0361 | 4.724e-05%
-68 | 24 | 761.3633 | 0.76313 | 0.97488 | 1.2978 | 1.5444 | 1.8943 | 3.798e-05%
-67.5 | 24 | 741.4038 | 0.71844 | 0.9174 | 1.2206 | 1.4522 | 1.7805 | 3.209e-05%
-67 | 24 | 722.3527 | 0.68361 | 0.87071 | 1.1551 | 1.3717 | 1.6783 | 2.561e-05%
-66.5 | 24 | 704.2837 | 0.66283 | 0.83799 | 1.1021 | 1.3019 | 1.583 | 1.74e-05%
-66 | 24 | 687.2746 | 0.6263 | 0.78468 | 1.0211 | 1.1985 | 1.4464 | 9.963e-06%
-65.5 | 24 | 671.406 | 0.61109 | 0.75653 | 0.97084 | 1.1299 | 1.35 | 5.13e-06%
-65 | 24 | 656.7608 | 0.56956 | 0.69901 | 0.88794 | 1.027 | 1.2182 | 2.572e-06%
-64.5 | 24 | 643.4226 | 0.52496 | 0.64091 | 0.80918 | 0.93246 | 1.1013 | 1.462e-06%
-64 | 24 | 631.4744 | 0.4356 | 0.5308 | 0.66867 | 0.7695 | 0.90737 | 7.241e-07%
-63.5 | 24 | 620.9965 | 0.33505 | 0.40744 | 0.51203 | 0.58838 | 0.69261 | 2.754e-07%
-63 | 24 | 612.0646 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 24 | 604.7472 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 24 | 599.1035 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 24 | 595.1813 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 24 | 593.0147 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 24 | 592.6229 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 24 | 594.0096 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 24 | 597.1622 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 24 | 602.0531 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 24.5 | 2002.154 | 1.921 | 2.9195 | 4.5653 | 5.7969 | 7.4823 | 0.004179%
-89.5 | 24.5 | 1971.5092 | 2.1352 | 3.2106 | 5.0912 | 6.38 | 8.3141 | 0.004961%
-89 | 24.5 | 1940.9136 | 2.3268 | 3.4897 | 5.4974 | 6.9336 | 9.1041 | 0.005729%
-88.5 | 24.5 | 1910.37 | 2.4568 | 3.7136 | 5.8256 | 7.3869 | 9.7605 | 0.00651%
-88 | 24.5 | 1879.8812 | 2.5783 | 3.9399 | 6.1791 | 7.8919 | 10.5165 | 0.007547%
-87.5 | 24.5 | 1849.4502 | 2.7083 | 4.2187 | 6.6509 | 8.588 | 11.5665 | 0.009207%
-87 | 24.5 | 1819.0802 | 2.7786 | 4.4268 | 7.0599 | 9.2296 | 12.4409 | 0.01089%
-86.5 | 24.5 | 1788.7747 | 2.6323 | 4.1948 | 6.7679 | 8.8585 | 12.036 | 0.01053%
-86 | 24.5 | 1758.5372 | 2.294 | 3.5657 | 5.8019 | 7.5108 | 10.1683 | 0.007926%
-85.5 | 24.5 | 1728.3717 | 1.8225 | 2.891 | 4.6818 | 6.0607 | 8.0762 | 0.005669%
-85 | 24.5 | 1698.2822 | 1.4633 | 2.3506 | 3.6856 | 4.8453 | 6.3845 | 0.003839%
-84.5 | 24.5 | 1668.2733 | 1.2086 | 1.9044 | 3.0092 | 3.8928 | 5.2308 | 0.002709%
-84 | 24.5 | 1638.3496 | 1.0714 | 1.6793 | 2.6999 | 3.4664 | 4.6475 | 0.002296%
-83.5 | 24.5 | 1608.5162 | 1.0492 | 1.6814 | 2.7516 | 3.566 | 4.834 | 0.002732%
-83 | 24.5 | 1578.7785 | 1.1075 | 1.8594 | 3.1027 | 4.1259 | 5.5724 | 0.003966%
-82.5 | 24.5 | 1549.1422 | 1.2317 | 2.2015 | 3.7252 | 5.1041 | 6.7208 | 0.005982%
-82 | 24.5 | 1519.6137 | 1.3799 | 2.5293 | 4.449 | 5.9405 | 8.0121 | 0.008047%
-81.5 | 24.5 | 1490.1997 | 1.4622 | 2.7101 | 4.8782 | 6.4233 | 8.7625 | 0.009312%
-81 | 24.5 | 1460.9072 | 1.3898 | 2.5997 | 4.6619 | 6.1981 | 8.4333 | 0.008983%
-80.5 | 24.5 | 1431.7441 | 1.1771 | 2.2197 | 3.8899 | 5.3564 | 7.1781 | 0.00739%
-80 | 24.5 | 1402.7188 | 0.92902 | 1.6492 | 2.966 | 4.0547 | 5.6322 | 0.005216%
-79.5 | 24.5 | 1373.8402 | 0.73929 | 1.2213 | 2.1952 | 2.9142 | 4.0358 | 0.002924%
-79 | 24.5 | 1345.118 | 0.62556 | 0.95945 | 1.5814 | 2.143 | 2.8559 | 0.001261%
-78.5 | 24.5 | 1316.5629 | 0.59767 | 0.85065 | 1.2848 | 1.651 | 2.216 | 0.0004207%
-78 | 24.5 | 1288.1861 | 0.63271 | 0.85108 | 1.2034 | 1.4856 | 1.9022 | 0.0001286%
-77.5 | 24.5 | 1260 | 0.69584 | 0.91716 | 1.2664 | 1.5409 | 1.9399 | 8.808e-05%
-77 | 24.5 | 1232.018 | 0.74981 | 0.99378 | 1.3811 | 1.6871 | 2.1338 | 0.0001224%
-76.5 | 24.5 | 1204.2545 | 0.79379 | 1.0642 | 1.4988 | 1.8459 | 2.3199 | 0.000175%
-76 | 24.5 | 1176.7253 | 0.82978 | 1.1235 | 1.6007 | 1.9854 | 2.4468 | 0.0002184%
-75.5 | 24.5 | 1149.4475 | 0.83454 | 1.1345 | 1.6242 | 2.0203 | 2.4808 | 0.0002375%
-75 | 24.5 | 1122.4397 | 0.81141 | 1.1011 | 1.5729 | 1.9539 | 2.4243 | 0.0002253%
-74.5 | 24.5 | 1095.7221 | 0.74654 | 1.0053 | 1.4234 | 1.7586 | 2.2539 | 0.0001869%
-74 | 24.5 | 1069.3166 | 0.67422 | 0.89475 | 1.2453 | 1.5227 | 1.9279 | 0.0001007%
-73.5 | 24.5 | 1043.2474 | 0.57538 | 0.74861 | 1.0181 | 1.2275 | 1.5286 | 3.727e-05%
-73 | 24.5 | 1017.5404 | 0.47223 | 0.59934 | 0.7918 | 0.93793 | 1.1442 | 8.517e-06%
-72.5 | 24.5 | 992.224 | 0.36634 | 0.45529 | 0.5869 | 0.68491 | 0.82099 | 1.466e-06%
-72 | 24.5 | 967.3292 | 0.20463 | 0.24877 | 0.31254 | 0.35908 | 0.42259 | 5.692e-08%
-71.5 | 24.5 | 942.8895 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 24.5 | 918.9416 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 24.5 | 895.5251 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 24.5 | 872.6831 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 24.5 | 850.4619 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 24.5 | 828.9118 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 24.5 | 808.0867 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 24.5 | 788.0442 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 24.5 | 768.8457 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 24.5 | 750.5561 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 24.5 | 733.2438 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 24.5 | 716.9795 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 24.5 | 701.8364 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 24.5 | 687.8886 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 24.5 | 675.2103 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 24.5 | 663.8744 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 24.5 | 653.9508 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 24.5 | 645.5047 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 24.5 | 638.5948 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 24.5 | 633.2715 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 24.5 | 629.5752 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 24.5 | 627.5344 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 24.5 | 627.1655 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 24.5 | 628.4714 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 24.5 | 631.4417 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 24.5 | 636.053 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 25 | 2009.9993 | 2.4746 | 3.7539 | 5.8946 | 7.4857 | 9.9086 | 0.006737%
-89.5 | 25 | 1979.5889 | 2.8194 | 4.3738 | 6.8009 | 8.7375 | 11.6721 | 0.009048%
-89 | 25 | 1949.2329 | 3.1354 | 4.951 | 7.618 | 9.8696 | 13.0005 | 0.01094%
-88.5 | 25 | 1918.934 | 3.38 | 5.3266 | 8.2179 | 10.6978 | 13.9475 | 0.01234%
-88 | 25 | 1888.6954 | 3.6749 | 5.7828 | 9.0651 | 11.8319 | 15.412 | 0.01478%
-87.5 | 25 | 1858.5203 | 4.2166 | 6.7305 | 11.0726 | 14.3238 | 19.2487 | 0.02176%
-87 | 25 | 1828.4123 | 4.8527 | 8.146 | 14.3017 | 19.6235 | 28.1193 | 0.03809%
-86.5 | 25 | 1798.3749 | 4.5679 | 7.7495 | 13.6264 | 18.5798 | 26.6108 | 0.03561%
-86 | 25 | 1768.4121 | 3.4848 | 5.8239 | 9.6567 | 12.8519 | 17.4152 | 0.01966%
-85.5 | 25 | 1738.528 | 2.5502 | 4.0804 | 6.6493 | 8.732 | 11.9317 | 0.0106%
-85 | 25 | 1708.7271 | 1.8284 | 2.9087 | 4.7279 | 6.1249 | 8.1857 | 0.005862%
-84.5 | 25 | 1679.0141 | 1.3793 | 2.2219 | 3.4753 | 4.554 | 6.0421 | 0.003511%
-84 | 25 | 1649.3941 | 1.1129 | 1.737 | 2.7734 | 3.5707 | 4.8033 | 0.002369%
-83.5 | 25 | 1619.8725 | 0.96891 | 1.5035 | 2.4534 | 3.1319 | 4.171 | 0.001949%
-83 | 25 | 1590.455 | 0.91404 | 1.4404 | 2.4038 | 3.0833 | 4.1291 | 0.00214%
-82.5 | 25 | 1561.1479 | 0.8824 | 1.4345 | 2.4634 | 3.2106 | 4.3812 | 0.002768%
-82 | 25 | 1531.9577 | 0.83486 | 1.4124 | 2.5208 | 3.351 | 4.6799 | 0.003658%
-81.5 | 25 | 1502.8916 | 0.79232 | 1.3794 | 2.5365 | 3.4139 | 4.8378 | 0.004296%
-81 | 25 | 1473.9572 | 0.73382 | 1.2845 | 2.4141 | 3.2509 | 4.6095 | 0.004241%
-80.5 | 25 | 1445.1627 | 0.65533 | 1.1264 | 2.1209 | 2.8681 | 4.0128 | 0.0035%
-80 | 25 | 1416.5169 | 0.55011 | 0.91687 | 1.6653 | 2.3561 | 3.2222 | 0.002493%
-79.5 | 25 | 1388.0294 | 0.44981 | 0.71944 | 1.2453 | 1.7386 | 2.4792 | 0.001467%
-79 | 25 | 1359.7103 | 0.37993 | 0.57579 | 0.93584 | 1.2575 | 1.7785 | 0.0006039%
-78.5 | 25 | 1331.5706 | 0.34506 | 0.49143 | 0.74276 | 0.95491 | 1.2823 | 0.0001633%
-78 | 25 | 1303.6223 | 0.35441 | 0.4728 | 0.66207 | 0.81254 | 1.0333 | 2.954e-05%
-77.5 | 25 | 1275.8783 | 0.37617 | 0.48039 | 0.63924 | 0.76056 | 0.93257 | 6.294e-06%
-77 | 25 | 1248.3524 | 0.40843 | 0.51445 | 0.67364 | 0.79368 | 0.96207 | 4.056e-06%
-76.5 | 25 | 1221.0596 | 0.43576 | 0.55173 | 0.72685 | 0.85953 | 1.0464 | 6.186e-06%
-76 | 25 | 1194.0162 | 0.46775 | 0.59464 | 0.78709 | 0.93345 | 1.1402 | 8.945e-06%
-75.5 | 25 | 1167.2398 | 0.48481 | 0.61659 | 0.81657 | 0.96871 | 1.1838 | 9.999e-06%
-75 | 25 | 1140.7495 | 0.47195 | 0.59946 | 0.79267 | 0.9395 | 1.1468 | 8.808e-06%
-74.5 | 25 | 1114.5659 | 0.43175 | 0.54636 | 0.71931 | 0.85029 | 1.0347 | 5.885e-06%
-74 | 25 | 1088.7114 | 0.36577 | 0.46 | 0.60125 | 0.7076 | 0.85663 | 2.79e-06%
-73.5 | 25 | 1063.2102 | 0.29273 | 0.36419 | 0.47006 | 0.54898 | 0.65864 | 8.272e-07%
-73 | 25 | 1038.0887 | 0.22474 | 0.27485 | 0.34771 | 0.40117 | 0.47448 | 1.208e-07%
-72.5 | 25 | 1013.3753 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 25 | 989.1009 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 25 | 965.2988 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 25 | 942.0051 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 25 | 919.2586 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 25 | 897.1011 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 25 | 875.5777 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 25 | 854.7364 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 25 | 834.6284 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 25 | 815.3084 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 25 | 796.8337 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 25 | 779.2646 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 25 | 762.664 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 25 | 747.0966 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 25 | 732.6283 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 25 | 719.3256 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 25 | 707.2544 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 25 | 696.4789 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 25 | 687.0601 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 25 | 679.0546 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 25 | 672.513 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 25 | 667.4782 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 25 | 663.9847 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 25 | 662.0569 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 25 | 661.7085 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 25 | 662.942 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 25 | 665.7486 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 25 | 670.1084 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 25.5 | 2018.3566 | 3.2772 | 5.191 | 8.0045 | 10.4167 | 13.6481 | 0.01196%
-89.5 | 25.5 | 1988.1883 | 4.0491 | 6.3784 | 10.2235 | 13.2187 | 17.4659 | 0.01826%
-89 | 25.5 | 1958.0794 | 4.8002 | 7.454 | 12.1184 | 15.5528 | 20.8431 | 0.02388%
-88.5 | 25.5 | 1928.033 | 5.174 | 7.9451 | 12.7981 | 16.4362 | 22.0444 | 0.02571%
-88 | 25.5 | 1898.0524 | 5.5701 | 8.651 | 13.8649 | 17.9078 | 24.179 | 0.02972%
-87.5 | 25.5 | 1868.1412 | 7.0924 | 12.2804 | 21.2719 | 29.0933 | 40.6178 | 0.06301%
-87 | 25.5 | 1838.3031 | 8.8461 | 15.4551 | 27.4205 | 36.7916 | 51.9468 | 0.08636%
-86.5 | 25.5 | 1808.5419 | 8.4868 | 15.017 | 26.8131 | 35.9356 | 50.6702 | 0.08355%
-86 | 25.5 | 1778.8618 | 6.0506 | 10.9513 | 19.6376 | 27.5465 | 38.9626 | 0.05876%
-85.5 | 25.5 | 1749.2674 | 3.5373 | 6.0011 | 10.2131 | 13.6583 | 18.812 | 0.02244%
-85 | 25.5 | 1719.7632 | 2.2921 | 3.5958 | 5.8957 | 7.6773 | 10.4654 | 0.008533%
-84.5 | 25.5 | 1690.3544 | 1.5498 | 2.4968 | 3.9753 | 5.2427 | 6.9233 | 0.004544%
-84 | 25.5 | 1661.0463 | 1.1591 | 1.821 | 2.9107 | 3.7788 | 5.1237 | 0.002717%
-83.5 | 25.5 | 1631.8447 | 0.94161 | 1.4419 | 2.3484 | 2.9963 | 3.988 | 0.001752%
-83 | 25.5 | 1602.7557 | 0.81707 | 1.2417 | 2.0245 | 2.6147 | 3.4345 | 0.00139%
-82.5 | 25.5 | 1573.7858 | 0.7275 | 1.1124 | 1.827 | 2.4173 | 3.1667 | 0.001346%
-82 | 25.5 | 1544.942 | 0.61589 | 0.95966 | 1.6112 | 2.208 | 2.927 | 0.001463%
-81.5 | 25.5 | 1516.2318 | 0.50965 | 0.81307 | 1.4032 | 1.9555 | 2.7018 | 0.001581%
-81 | 25.5 | 1487.6633 | 0.45706 | 0.73343 | 1.2744 | 1.7834 | 2.5305 | 0.001533%
-80.5 | 25.5 | 1459.2451 | 0.41662 | 0.66064 | 1.1321 | 1.5709 | 2.2918 | 0.001272%
-80 | 25.5 | 1430.9863 | 0.37189 | 0.57556 | 0.9587 | 1.3075 | 1.8819 | 0.0008%
-79.5 | 25.5 | 1402.897 | 0.32464 | 0.48621 | 0.7794 | 1.0385 | 1.4544 | 0.0003928%
-79 | 25.5 | 1374.9878 | 0.28082 | 0.40479 | 0.62049 | 0.80457 | 1.0913 | 0.0001491%
-78.5 | 25.5 | 1347.2702 | 0.24275 | 0.33587 | 0.49082 | 0.6182 | 0.81041 | 4.187e-05%
-78 | 25.5 | 1319.7565 | 0.20176 | 0.26901 | 0.37645 | 0.46182 | 0.58699 | 8.662e-06%
-77.5 | 25.5 | 1292.46 | 0.1624 | 0.20909 | 0.28088 | 0.33611 | 0.41492 | 1.154e-06%
-77 | 25.5 | 1265.3952 | 0.16321 | 0.20181 | 0.25862 | 0.30072 | 0.35895 | 1.038e-07%
-76.5 | 25.5 | 1238.5773 | 0.19059 | 0.23423 | 0.29801 | 0.34503 | 0.40974 | 1.052e-07%
-76 | 25.5 | 1212.0231 | 0.18647 | 0.23143 | 0.29786 | 0.34727 | 0.41579 | 1.97e-07%
-75.5 | 25.5 | 1185.7506 | 0.18494 | 0.23028 | 0.29751 | 0.34767 | 0.41741 | 2.389e-07%
-75 | 25.5 | 1159.7792 | 0.18234 | 0.22638 | 0.29147 | 0.33989 | 0.40708 | 1.889e-07%
-74.5 | 25.5 | 1134.1298 | 0.18226 | 0.22416 | 0.28545 | 0.33066 | 0.39292 | 9.731e-08%
-74 | 25.5 | 1108.8251 | 0.14257 | 0.17383 | 0.21913 | 0.25228 | 0.29763 | 2.331e-08%
-73.5 | 25.5 | 1083.8893 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 25.5 | 1059.3489 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 25.5 | 1035.2321 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 25.5 | 1011.5696 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 25.5 | 988.3942 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 25.5 | 965.7412 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 25.5 | 943.6484 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 25.5 | 922.1562 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 25.5 | 901.308 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 25.5 | 881.1497 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 25.5 | 861.7297 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 25.5 | 843.0993 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 25.5 | 825.3123 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 25.5 | 808.4244 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 25.5 | 792.4933 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 25.5 | 777.5779 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 25.5 | 763.7379 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 25.5 | 751.033 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 25.5 | 739.5216 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 25.5 | 729.2605 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 25.5 | 720.3032 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 25.5 | 712.6989 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 25.5 | 706.4915 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 25.5 | 701.7179 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 25.5 | 698.4077 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 25.5 | 696.5819 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 25.5 | 696.2519 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 25.5 | 697.4201 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 25.5 | 700.0788 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 25.5 | 704.2112 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 26 | 2027.2196 | 4.6162 | 7.1197 | 11.4925 | 14.6126 | 19.3699 | 0.02111%
-89.5 | 26 | 1997.3005 | 5.9654 | 9.4447 | 15.1365 | 19.7246 | 26.7425 | 0.03496%
-89 | 26 | 1967.4459 | 7.0445 | 11.4706 | 18.055 | 23.7918 | 31.7277 | 0.04608%
-88.5 | 26 | 1937.6594 | 7.4152 | 11.9768 | 18.8739 | 24.8886 | 32.9442 | 0.04901%
-88 | 26 | 1907.9443 | 7.9809 | 13.0467 | 21.3072 | 28.2488 | 38.0042 | 0.05996%
-87.5 | 26 | 1878.3044 | 10.2446 | 17.3374 | 30.3961 | 41.3083 | 59.0637 | 0.1009%
-87 | 26 | 1848.7436 | 13.7343 | 24.7403 | 43.3267 | 60.2006 | 83.6501 | 0.157%
-86.5 | 26 | 1819.2661 | 13.1931 | 23.5457 | 40.9229 | 56.606 | 78.2232 | 0.1469%
-86 | 26 | 1789.8763 | 8.4502 | 15.2121 | 27.8769 | 38.446 | 56.0614 | 0.08971%
-85.5 | 26 | 1760.579 | 4.5285 | 7.7037 | 13.4757 | 18.1919 | 25.8602 | 0.03443%
-85 | 26 | 1731.3792 | 2.5677 | 4.1195 | 6.7137 | 8.8242 | 12.0484 | 0.0108%
-84.5 | 26 | 1702.2821 | 1.6671 | 2.6789 | 4.3156 | 5.6481 | 7.5048 | 0.00519%
-84 | 26 | 1673.2934 | 1.1961 | 1.8932 | 3.031 | 3.9586 | 5.3557 | 0.002992%
-83.5 | 26 | 1644.4193 | 0.92707 | 1.4171 | 2.3135 | 2.9679 | 3.9755 | 0.001778%
-83 | 26 | 1615.6661 | 0.76033 | 1.1385 | 1.8247 | 2.3964 | 3.1485 | 0.001152%
-82.5 | 26 | 1587.0407 | 0.64658 | 0.9575 | 1.5148 | 2.0022 | 2.6552 | 0.0008372%
-82 | 26 | 1558.5505 | 0.51906 | 0.76678 | 1.2096 | 1.596 | 2.2097 | 0.0006466%
-81.5 | 26 | 1530.2033 | 0.38092 | 0.56557 | 0.89745 | 1.1884 | 1.6523 | 0.000433%
-81 | 26 | 1502.0075 | 0.32705 | 0.4855 | 0.77025 | 1.0199 | 1.4178 | 0.0003403%
-80.5 | 26 | 1473.9721 | 0.29828 | 0.43807 | 0.68636 | 0.9019 | 1.2426 | 0.0002411%
-80 | 26 | 1446.1068 | 0.2781 | 0.40032 | 0.6127 | 0.79373 | 1.0754 | 0.0001425%
-79.5 | 26 | 1418.4217 | 0.25427 | 0.35647 | 0.52896 | 0.67248 | 0.89128 | 6.504e-05%
-79 | 26 | 1390.9281 | 0.22501 | 0.30658 | 0.44002 | 0.54818 | 0.70947 | 2.283e-05%
-78.5 | 26 | 1363.6377 | 0.19241 | 0.25466 | 0.35333 | 0.4312 | 0.54473 | 5.892e-06%
-78 | 26 | 1336.5632 | 0.15659 | 0.20144 | 0.27034 | 0.32332 | 0.39886 | 1.013e-06%
-77.5 | 26 | 1309.7185 | 0.12706 | 0.15841 | 0.20497 | 0.23975 | 0.28815 | 9.097e-08%
-77 | 26 | 1283.118 | 0 | 0 | 0 | 0 | 0 | 0%
-76.5 | 26 | 1256.7778 | 0 | 0 | 0 | 0 | 0 | 0%
-76 | 26 | 1230.7146 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 26 | 1204.9468 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 26 | 1179.494 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 26 | 1154.3773 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 26 | 1129.6193 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 26 | 1105.2445 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 26 | 1081.2789 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 26 | 1057.7507 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 26 | 1034.6899 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 26 | 1012.1287 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 26 | 990.1014 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 26 | 968.6448 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 26 | 947.7979 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 26 | 927.6018 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 26 | 908.1003 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 26 | 889.3392 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 26 | 871.3666 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 26 | 854.2324 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 26 | 837.9883 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 26 | 822.687 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 26 | 808.3822 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 26 | 795.128 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 26 | 782.9779 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 26 | 771.9839 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 26 | 762.1964 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 26 | 753.6623 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 26 | 746.4248 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 26 | 740.522 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 26 | 735.986 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 26 | 732.8423 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 26 | 731.1088 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 26 | 730.7956 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 26 | 731.9045 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 26 | 734.4291 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 26 | 738.3549 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 26.5 | 2036.5816 | 6.5953 | 10.5672 | 16.7154 | 21.8836 | 29.3025 | 0.04056%
-89.5 | 26.5 | 2006.9184 | 8.0433 | 12.8802 | 20.4296 | 26.8452 | 35.4186 | 0.05493%
-89 | 26.5 | 1977.3252 | 9.3099 | 14.7027 | 23.6972 | 30.6714 | 40.8673 | 0.06817%
-88.5 | 26.5 | 1947.8054 | 9.4625 | 14.8794 | 23.9589 | 30.9385 | 41.1936 | 0.06915%
-88 | 26.5 | 1918.3626 | 9.3992 | 14.9986 | 24.5958 | 31.9093 | 42.9221 | 0.07247%
-87.5 | 26.5 | 1889.001 | 10.9627 | 18.0058 | 30.7109 | 40.9811 | 57.491 | 0.1022%
-87 | 26.5 | 1859.7245 | 13.5603 | 23.5231 | 40.0013 | 54.6183 | 75.2428 | 0.1454%
-86.5 | 26.5 | 1830.5377 | 12.9849 | 22.5138 | 38.497 | 52.4292 | 72.4898 | 0.1376%
-86 | 26.5 | 1801.4452 | 8.4516 | 14.9938 | 26.9867 | 36.5192 | 52.08 | 0.08498%
-85.5 | 26.5 | 1772.452 | 4.6007 | 7.6993 | 13.3063 | 17.8365 | 25.1551 | 0.03297%
-85 | 26.5 | 1743.5634 | 2.6481 | 4.2356 | 6.8394 | 8.9641 | 12.1696 | 0.01077%
-84.5 | 26.5 | 1714.7849 | 1.7175 | 2.747 | 4.4329 | 5.7763 | 7.6692 | 0.005311%
-84 | 26.5 | 1686.1225 | 1.2002 | 1.9058 | 3.0586 | 4.004 | 5.4166 | 0.003093%
-83.5 | 26.5 | 1657.5825 | 0.8981 | 1.3749 | 2.2601 | 2.9097 | 3.9138 | 0.001796%
-83 | 26.5 | 1629.1718 | 0.71265 | 1.0653 | 1.7039 | 2.265 | 2.994 | 0.001093%
-82.5 | 26.5 | 1600.8974 | 0.59209 | 0.8689 | 1.3601 | 1.7863 | 2.4204 | 0.0006815%
-82 | 26.5 | 1572.767 | 0.44675 | 0.64478 | 0.98985 | 1.2847 | 1.7444 | 0.0003345%
-81.5 | 26.5 | 1544.7889 | 0.30692 | 0.43432 | 0.65155 | 0.83385 | 1.1138 | 0.0001148%
-81 | 26.5 | 1516.9717 | 0.25904 | 0.35983 | 0.52824 | 0.66719 | 0.87752 | 5.278e-05%
-80.5 | 26.5 | 1489.3248 | 0.23045 | 0.31598 | 0.45688 | 0.57175 | 0.74388 | 2.908e-05%
-80 | 26.5 | 1461.858 | 0.21551 | 0.29151 | 0.41489 | 0.51423 | 0.66152 | 1.655e-05%
-79.5 | 26.5 | 1434.5821 | 0.19515 | 0.25938 | 0.36165 | 0.44267 | 0.56118 | 7.159e-06%
-79 | 26.5 | 1407.5085 | 0.1653 | 0.21577 | 0.29457 | 0.35598 | 0.44455 | 2.328e-06%
-78.5 | 26.5 | 1380.6493 | 0.15096 | 0.19158 | 0.25307 | 0.29976 | 0.36563 | 4.427e-07%
-78 | 26.5 | 1354.0175 | 0.12149 | 0.15051 | 0.1933 | 0.22507 | 0.26908 | 5.069e-08%
-77.5 | 26.5 | 1327.6272 | 0 | 0 | 0 | 0 | 0 | 0%
-77 | 26.5 | 1301.4933 | 0 | 0 | 0 | 0 | 0 | 0%
-76.5 | 26.5 | 1275.6318 | 0 | 0 | 0 | 0 | 0 | 0%
-76 | 26.5 | 1250.0599 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 26.5 | 1224.7961 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 26.5 | 1199.8601 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 26.5 | 1175.2729 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 26.5 | 1151.0572 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 26.5 | 1127.2372 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 26.5 | 1103.8388 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 26.5 | 1080.8895 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 26.5 | 1058.4189 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 26.5 | 1036.4582 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 26.5 | 1015.0409 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 26.5 | 994.2023 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 26.5 | 973.9797 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 26.5 | 954.4124 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 26.5 | 935.5419 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 26.5 | 917.4112 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 26.5 | 900.0654 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 26.5 | 883.5508 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 26.5 | 867.9149 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 26.5 | 853.2064 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 26.5 | 839.4741 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 26.5 | 826.7667 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 26.5 | 815.1324 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 26.5 | 804.6177 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 26.5 | 795.2673 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 26.5 | 787.1227 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 26.5 | 780.2217 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 26.5 | 774.5977 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 26.5 | 770.2787 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 26.5 | 767.2868 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 26.5 | 765.6375 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 26.5 | 765.3395 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 26.5 | 766.3945 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 26.5 | 768.7969 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 26.5 | 772.534 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 27 | 2046.4356 | 10.5525 | 17.336 | 29.4772 | 39.0354 | 54.2726 | 0.09589%
-89.5 | 27 | 2017.0349 | 10.7616 | 17.0876 | 28.3037 | 36.878 | 50.3058 | 0.09007%
-89 | 27 | 1987.7094 | 10.2843 | 15.9295 | 25.7584 | 32.9044 | 43.8426 | 0.0766%
-88.5 | 27 | 1958.4628 | 9.6404 | 15.0278 | 24.0661 | 30.957 | 41.0599 | 0.06927%
-88 | 27 | 1929.2989 | 8.5595 | 13.4816 | 21.2418 | 27.6447 | 36.3184 | 0.05741%
-87.5 | 27 | 1900.222 | 8.6358 | 14.1141 | 23.5485 | 31.1768 | 42.691 | 0.06973%
-87 | 27 | 1871.2363 | 9.586 | 16.1663 | 28.0472 | 37.429 | 52.5118 | 0.08938%
-86.5 | 27 | 1842.3467 | 8.8861 | 15.2979 | 26.8777 | 35.8884 | 50.3834 | 0.084%
-86 | 27 | 1813.5578 | 6.2004 | 10.6011 | 18.2482 | 25.2117 | 35.2604 | 0.05202%
-85.5 | 27 | 1784.8751 | 3.8567 | 6.2172 | 10.1038 | 13.1858 | 17.5755 | 0.01904%
-85 | 27 | 1756.3039 | 2.5764 | 4.0365 | 6.4498 | 8.3529 | 11.3136 | 0.009171%
-84.5 | 27 | 1727.8502 | 1.7693 | 2.8056 | 4.5227 | 5.8599 | 7.7491 | 0.005268%
-84 | 27 | 1699.5202 | 1.2267 | 1.956 | 3.1382 | 4.1194 | 5.5548 | 0.003246%
-83.5 | 27 | 1671.3204 | 0.89445 | 1.3768 | 2.2747 | 2.9398 | 3.972 | 0.001908%
-83 | 27 | 1643.258 | 0.66661 | 0.99715 | 1.5961 | 2.1249 | 2.8415 | 0.001028%
-82.5 | 27 | 1615.3402 | 0.53017 | 0.77913 | 1.2216 | 1.606 | 2.2138 | 0.0006134%
-82 | 27 | 1587.5752 | 0.37854 | 0.54749 | 0.84256 | 1.0952 | 1.4897 | 0.000264%
-81.5 | 27 | 1559.9714 | 0.22588 | 0.31761 | 0.47297 | 0.60257 | 0.80063 | 5.668e-05%
-81 | 27 | 1532.5377 | 0.17546 | 0.2332 | 0.32512 | 0.39795 | 0.50447 | 5.673e-06%
-80.5 | 27 | 1505.2838 | 0.16971 | 0.22093 | 0.30065 | 0.36262 | 0.45181 | 2.185e-06%
-80 | 27 | 1478.2199 | 0.16575 | 0.21288 | 0.28517 | 0.34066 | 0.4197 | 1.074e-06%
-79.5 | 27 | 1451.357 | 0.14578 | 0.185 | 0.24437 | 0.28945 | 0.35306 | 4.039e-07%
-79 | 27 | 1424.7067 | 0.1164 | 0.14573 | 0.18949 | 0.22229 | 0.2681 | 9.489e-08%
-78.5 | 27 | 1398.2814 | 0.091769 | 0.11255 | 0.14285 | 0.16514 | 0.19577 | 9.908e-09%
-78 | 27 | 1372.0945 | 0 | 0 | 0 | 0 | 0 | 0%
-77.5 | 27 | 1346.1602 | 0 | 0 | 0 | 0 | 0 | 0%
-77 | 27 | 1320.4935 | 0 | 0 | 0 | 0 | 0 | 0%
-76.5 | 27 | 1295.1108 | 0 | 0 | 0 | 0 | 0 | 0%
-76 | 27 | 1270.0292 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 27 | 1245.2673 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 27 | 1220.8448 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 27 | 1196.7827 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 27 | 1173.1035 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 27 | 1149.831 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 27 | 1126.9907 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 27 | 1104.6097 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 27 | 1082.7167 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 27 | 1061.3421 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 27 | 1040.518 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 27 | 1020.2785 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 27 | 1000.6592 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 27 | 981.6975 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 27 | 963.4324 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 27 | 945.9045 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 27 | 929.1556 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 27 | 913.2289 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 27 | 898.1682 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 27 | 884.0179 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 27 | 870.8226 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 27 | 858.6264 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 27 | 847.4726 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 27 | 837.403 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 27 | 828.4571 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 27 | 820.672 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 27 | 814.0808 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 27 | 808.7129 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 27 | 804.5929 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 27 | 801.74 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 27 | 800.1677 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 27 | 799.8837 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 27 | 800.8894 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 27 | 803.1798 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 27 | 806.744 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 27.5 | 2056.7746 | 14.6885 | 25.4805 | 42.9828 | 58.8612 | 80.6413 | 0.161%
-89.5 | 27.5 | 2027.6425 | 12.447 | 20.2463 | 33.7644 | 44.9139 | 62.1155 | 0.1176%
-89 | 27.5 | 1998.5907 | 9.7913 | 15.2793 | 24.6074 | 31.5894 | 41.9609 | 0.07157%
-88.5 | 27.5 | 1969.6233 | 8.2145 | 12.9316 | 20.163 | 26.3155 | 34.3165 | 0.05275%
-88 | 27.5 | 1940.7443 | 7.0538 | 11.1513 | 17.103 | 22.1101 | 29.1636 | 0.04024%
-87.5 | 27.5 | 1911.9581 | 6.3001 | 9.762 | 15.1489 | 19.4018 | 25.9141 | 0.03281%
-87 | 27.5 | 1883.2692 | 6.0464 | 9.5063 | 15.0729 | 19.5104 | 26.3174 | 0.03397%
-86.5 | 27.5 | 1854.6826 | 5.5329 | 8.6757 | 13.9955 | 18.1284 | 24.5593 | 0.03065%
-86 | 27.5 | 1826.2033 | 4.4215 | 6.8793 | 11.0982 | 14.1401 | 18.6611 | 0.02007%
-85.5 | 27.5 | 1797.8368 | 3.3271 | 5.2866 | 8.18 | 10.6673 | 13.8905 | 0.01244%
-85 | 27.5 | 1769.5888 | 2.5609 | 3.9647 | 6.2753 | 8.0562 | 10.8003 | 0.008197%
-84.5 | 27.5 | 1741.4655 | 1.8898 | 2.9675 | 4.8116 | 6.1679 | 8.1552 | 0.005601%
-84 | 27.5 | 1713.4733 | 1.3189 | 2.1292 | 3.4047 | 4.5019 | 6.0083 | 0.003738%
-83.5 | 27.5 | 1685.6189 | 0.95472 | 1.4932 | 2.4728 | 3.2269 | 4.4098 | 0.002384%
-83 | 27.5 | 1657.9098 | 0.66561 | 1.0094 | 1.6418 | 2.2071 | 2.9662 | 0.001233%
-82.5 | 27.5 | 1630.3537 | 0.4736 | 0.70024 | 1.1057 | 1.4599 | 2.0228 | 0.0005677%
-82 | 27.5 | 1602.9586 | 0.29692 | 0.43232 | 0.67051 | 0.87566 | 1.1978 | 0.0002017%
-81.5 | 27.5 | 1575.7334 | 0.14336 | 0.20581 | 0.31399 | 0.40597 | 0.54881 | 4.335e-05%
-81 | 27.5 | 1548.6873 | 0.10303 | 0.12985 | 0.17016 | 0.20057 | 0.24325 | 1.064e-07%
-80.5 | 27.5 | 1521.8301 | 0.10755 | 0.13427 | 0.17402 | 0.20375 | 0.24518 | 6.304e-08%
-80 | 27.5 | 1495.1724 | 0.10296 | 0.12712 | 0.16263 | 0.18891 | 0.22521 | 2.426e-08%
-79.5 | 27.5 | 1468.7252 | 0.072932 | 0.089302 | 0.11314 | 0.13064 | 0.15467 | 4.287e-09%
-79 | 27.5 | 1442.5006 | 0 | 0 | 0 | 0 | 0 | 0%
-78.5 | 27.5 | 1416.511 | 0 | 0 | 0 | 0 | 0 | 0%
-78 | 27.5 | 1390.7701 | 0 | 0 | 0 | 0 | 0 | 0%
-77.5 | 27.5 | 1365.2921 | 0 | 0 | 0 | 0 | 0 | 0%
-77 | 27.5 | 1340.0923 | 0 | 0 | 0 | 0 | 0 | 0%
-76.5 | 27.5 | 1315.187 | 0 | 0 | 0 | 0 | 0 | 0%
-76 | 27.5 | 1290.5935 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 27.5 | 1266.3302 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 27.5 | 1242.4168 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 27.5 | 1218.8742 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 27.5 | 1195.7244 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 27.5 | 1172.991 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 27.5 | 1150.6989 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 27.5 | 1128.8746 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 27.5 | 1107.5458 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 27.5 | 1086.742 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 27.5 | 1066.4942 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 27.5 | 1046.8347 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 27.5 | 1027.7977 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 27.5 | 1009.4186 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 27.5 | 991.734 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 27.5 | 974.782 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 27.5 | 958.6017 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 27.5 | 943.2329 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 27.5 | 928.716 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 27.5 | 915.0919 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 27.5 | 902.401 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 27.5 | 890.6834 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 27.5 | 879.9781 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 27.5 | 870.3225 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 27.5 | 861.7521 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 27.5 | 854.2996 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 27.5 | 847.9946 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 27.5 | 842.8628 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 27.5 | 838.9259 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 27.5 | 836.2008 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 27.5 | 834.6993 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 27.5 | 834.4281 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 27.5 | 835.3884 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 27.5 | 837.576 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 27.5 | 840.9812 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 28 | 2067.5913 | 15.1034 | 26.2331 | 43.7319 | 59.4438 | 81.0669 | 0.1657%
-89.5 | 28 | 2038.7333 | 11.7782 | 19.0886 | 32.0071 | 42.4122 | 58.8973 | 0.1087%
-89 | 28 | 2009.9609 | 8.3908 | 13.3906 | 21.3782 | 27.9736 | 37.0046 | 0.05869%
-88.5 | 28 | 1981.2783 | 6.7356 | 10.5031 | 16.1009 | 20.6479 | 27.2992 | 0.03588%
-88 | 28 | 1952.6898 | 5.8502 | 8.8603 | 13.7051 | 17.2852 | 22.6958 | 0.02618%
-87.5 | 28 | 1924.1998 | 5.2882 | 7.8849 | 12.3213 | 15.3916 | 19.9833 | 0.0211%
-87 | 28 | 1895.8132 | 4.8512 | 7.2643 | 11.4816 | 14.294 | 18.4842 | 0.01876%
-86.5 | 28 | 1867.535 | 4.3583 | 6.6465 | 10.438 | 13.2162 | 17.038 | 0.01667%
-86 | 28 | 1839.3706 | 3.7613 | 5.8536 | 9.0876 | 11.7826 | 15.0845 | 0.01396%
-85.5 | 28 | 1811.3255 | 3.1582 | 4.9998 | 7.6793 | 9.9498 | 13.0083 | 0.01096%
-85 | 28 | 1783.4058 | 2.5833 | 4.0134 | 6.3548 | 8.1697 | 10.9707 | 0.00846%
-84.5 | 28 | 1755.6178 | 2.0478 | 3.1997 | 5.2257 | 6.6701 | 8.8818 | 0.006409%
-84 | 28 | 1727.9681 | 1.5191 | 2.4671 | 3.9908 | 5.295 | 6.9918 | 0.004868%
-83.5 | 28 | 1700.4639 | 1.0501 | 1.6794 | 2.7889 | 3.688 | 5.1115 | 0.003202%
-83 | 28 | 1673.1125 | 0.74356 | 1.161 | 1.9539 | 2.6118 | 3.5794 | 0.001918%
-82.5 | 28 | 1645.922 | 0.47911 | 0.73337 | 1.2059 | 1.6319 | 2.3163 | 0.0009716%
-82 | 28 | 1618.9007 | 0.30771 | 0.47789 | 0.79925 | 1.0928 | 1.5774 | 0.0006443%
-81.5 | 28 | 1592.0577 | 0.263 | 0.42752 | 0.75415 | 1.0651 | 1.597 | 0.0009644%
-81 | 28 | 1565.4023 | 0.29287 | 0.48374 | 0.86939 | 1.2418 | 1.887 | 0.001333%
-80.5 | 28 | 1538.9447 | 0.33001 | 0.54599 | 0.98316 | 1.406 | 2.1394 | 0.001572%
-80 | 28 | 1512.6954 | 0.33173 | 0.54903 | 0.98906 | 1.4148 | 2.1535 | 0.001588%
-79.5 | 28 | 1486.666 | 0.32743 | 0.54138 | 0.97415 | 1.3925 | 2.1178 | 0.001546%
-79 | 28 | 1460.8683 | 0.28115 | 0.4638 | 0.83235 | 1.1879 | 1.8032 | 0.00125%
-78.5 | 28 | 1435.3152 | 0.20058 | 0.32985 | 0.58979 | 0.83984 | 1.2715 | 0.0007927%
-78 | 28 | 1410.0202 | 0.12712 | 0.20836 | 0.37111 | 0.52722 | 0.796 | 0.0004303%
-77.5 | 28 | 1384.9979 | 0.056874 | 0.092941 | 0.16496 | 0.23385 | 0.35219 | 0.0001503%
-77 | 28 | 1360.2635 | 0 | 0 | 0 | 0 | 0 | 0%
-76.5 | 28 | 1335.8333 | 0 | 0 | 0 | 0 | 0 | 0%
-76 | 28 | 1311.7246 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 28 | 1287.9558 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 28 | 1264.5461 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 28 | 1241.5162 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 28 | 1218.888 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 28 | 1196.6844 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 28 | 1174.9297 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 28 | 1153.6497 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 28 | 1132.8712 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 28 | 1112.6227 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 28 | 1092.9337 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 28 | 1073.8354 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 28 | 1055.3598 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 28 | 1037.5407 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 28 | 1020.4124 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 28 | 1004.0107 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 28 | 988.3717 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 28 | 973.5325 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 28 | 959.5304 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 28 | 946.4025 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 28 | 934.186 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 28 | 922.9171 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 28 | 912.6311 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 28 | 903.3617 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 28 | 895.1405 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 28 | 887.9968 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 28 | 881.9568 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 28 | 877.0433 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 28 | 873.2755 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 28 | 870.6683 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 28 | 869.232 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 28 | 868.9727 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 28 | 869.8912 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 28 | 871.9839 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 28 | 875.2423 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 28.5 | 2078.8781 | 11.1716 | 18.8054 | 32.4585 | 43.566 | 61.0052 | 0.1094%
-89.5 | 28.5 | 2050.2995 | 8.9536 | 14.9612 | 25.725 | 33.8076 | 46.5584 | 0.07816%
-89 | 28.5 | 2021.8118 | 6.7987 | 10.723 | 16.5345 | 21.336 | 28.215 | 0.03811%
-88.5 | 28.5 | 1993.4192 | 5.9986 | 9.1219 | 14.0626 | 17.7591 | 23.3536 | 0.02746%
-88 | 28.5 | 1965.1262 | 5.5842 | 8.3909 | 13.0216 | 16.3207 | 21.2724 | 0.02345%
-87.5 | 28.5 | 1936.9375 | 5.2993 | 7.92 | 12.3869 | 15.4798 | 20.1071 | 0.02137%
-87 | 28.5 | 1908.8581 | 4.964 | 7.4328 | 11.7488 | 14.6649 | 19.0221 | 0.01969%
-86.5 | 28.5 | 1880.8933 | 4.4919 | 6.846 | 10.8295 | 13.6471 | 17.6545 | 0.01775%
-86 | 28.5 | 1853.0485 | 3.9036 | 6.0806 | 9.5371 | 12.3004 | 15.8441 | 0.01525%
-85.5 | 28.5 | 1825.3295 | 3.3249 | 5.2905 | 8.2141 | 10.7341 | 13.9285 | 0.0126%
-85 | 28.5 | 1797.7426 | 2.7637 | 4.369 | 6.9153 | 8.9797 | 12.0318 | 0.01009%
-84.5 | 28.5 | 1770.2942 | 2.2745 | 3.543 | 5.7698 | 7.4433 | 10.0357 | 0.00777%
-84 | 28.5 | 1742.9913 | 1.7567 | 2.8402 | 4.7005 | 6.1153 | 8.1853 | 0.006237%
-83.5 | 28.5 | 1715.841 | 1.3203 | 2.1972 | 3.605 | 4.8588 | 6.5112 | 0.0048%
-83 | 28.5 | 1688.851 | 0.95288 | 1.5484 | 2.6487 | 3.5414 | 4.9795 | 0.003461%
-82.5 | 28.5 | 1662.0296 | 0.74896 | 1.2175 | 2.1478 | 2.9007 | 4.0922 | 0.002883%
-82 | 28.5 | 1635.3853 | 0.64621 | 1.0692 | 1.9256 | 2.6726 | 3.8194 | 0.002971%
-81.5 | 28.5 | 1608.9272 | 0.66951 | 1.1229 | 2.0546 | 2.8449 | 4.0992 | 0.003421%
-81 | 28.5 | 1582.6649 | 0.78304 | 1.3221 | 2.4078 | 3.2941 | 4.7582 | 0.004066%
-80.5 | 28.5 | 1556.6088 | 0.82112 | 1.3904 | 2.5187 | 3.4497 | 4.9897 | 0.0043%
-80 | 28.5 | 1530.7696 | 0.84263 | 1.428 | 2.5778 | 3.5312 | 5.1029 | 0.004401%
-79.5 | 28.5 | 1505.1587 | 0.7876 | 1.3315 | 2.4253 | 3.3204 | 4.8003 | 0.004124%
-79 | 28.5 | 1479.7884 | 0.66445 | 1.1175 | 2.0512 | 2.8457 | 4.1084 | 0.003477%
-78.5 | 28.5 | 1454.6716 | 0.56052 | 0.93721 | 1.7086 | 2.4298 | 3.4995 | 0.002887%
-78 | 28.5 | 1429.8218 | 0.39195 | 0.65069 | 1.1764 | 1.6864 | 2.5252 | 0.001941%
-77.5 | 28.5 | 1405.2536 | 0.26021 | 0.42927 | 0.77042 | 1.0995 | 1.6691 | 0.001137%
-77 | 28.5 | 1380.9822 | 0.12928 | 0.21217 | 0.37844 | 0.53811 | 0.81328 | 0.000447%
-76.5 | 28.5 | 1357.0239 | 0.052493 | 0.085745 | 0.15212 | 0.21558 | 0.32455 | 0.000135%
-76 | 28.5 | 1333.3958 | 0 | 0 | 0 | 0 | 0 | 0%
-75.5 | 28.5 | 1310.116 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 28.5 | 1287.2038 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 28.5 | 1264.6793 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 28.5 | 1242.5639 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 28.5 | 1220.88 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 28.5 | 1199.6515 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 28.5 | 1178.9029 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 28.5 | 1158.6605 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 28.5 | 1138.9513 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 28.5 | 1119.8039 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 28.5 | 1101.2476 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 28.5 | 1083.3132 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 28.5 | 1066.0321 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 28.5 | 1049.4368 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 28.5 | 1033.5607 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 28.5 | 1018.4374 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 28.5 | 1004.1011 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 28.5 | 990.5863 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 28.5 | 977.9271 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 28.5 | 966.1572 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 28.5 | 955.3097 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 28.5 | 945.4165 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 28.5 | 936.5079 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 28.5 | 928.6123 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 28.5 | 921.7559 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 28.5 | 915.962 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 28.5 | 911.251 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 28.5 | 907.6399 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 28.5 | 905.1417 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 28.5 | 903.7658 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 28.5 | 903.5174 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 28.5 | 904.3973 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 28.5 | 906.4022 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 28.5 | 909.5248 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 29 | 2090.6274 | 6.966 | 11.7044 | 19.205 | 25.9284 | 34.758 | 0.05274%
-89.5 | 29 | 2062.3331 | 6.5223 | 10.3393 | 16.1362 | 20.8757 | 27.7738 | 0.03722%
-89 | 29 | 2034.1348 | 6.2296 | 9.5735 | 14.7367 | 18.7077 | 24.7519 | 0.03034%
-88.5 | 29 | 2006.037 | 6.2139 | 9.5284 | 14.6478 | 18.566 | 24.5196 | 0.02984%
-88 | 29 | 1978.0442 | 6.2435 | 9.602 | 14.7816 | 18.7733 | 24.8519 | 0.03055%
-87.5 | 29 | 1950.1615 | 6.2125 | 9.59 | 14.8282 | 18.8843 | 25.0796 | 0.03109%
-87 | 29 | 1922.3938 | 5.9949 | 9.2415 | 14.3994 | 18.3417 | 24.3647 | 0.02975%
-86.5 | 29 | 1894.7467 | 5.5349 | 8.4645 | 13.3497 | 16.949 | 22.4283 | 0.02611%
-86 | 29 | 1867.2257 | 4.8478 | 7.408 | 11.8799 | 14.9909 | 19.695 | 0.02144%
-85.5 | 29 | 1839.837 | 3.9931 | 6.2841 | 10.0212 | 12.8999 | 16.795 | 0.01713%
-85 | 29 | 1812.5868 | 3.247 | 5.2445 | 8.2434 | 10.8533 | 14.1542 | 0.01339%
-84.5 | 29 | 1785.4818 | 2.6437 | 4.2199 | 6.7893 | 8.8682 | 11.9781 | 0.01042%
-84 | 29 | 1758.5291 | 2.1688 | 3.4404 | 5.6849 | 7.3707 | 9.9967 | 0.00814%
-83.5 | 29 | 1731.736 | 1.8122 | 2.9491 | 4.9486 | 6.4064 | 8.6214 | 0.006923%
-83 | 29 | 1705.1106 | 1.5156 | 2.5336 | 4.2338 | 5.638 | 7.5624 | 0.006092%
-82.5 | 29 | 1678.6609 | 1.2525 | 2.1389 | 3.6135 | 4.9434 | 6.6789 | 0.005556%
-82 | 29 | 1652.3959 | 1.2598 | 2.1716 | 3.6871 | 5.0673 | 6.8418 | 0.005893%
-81.5 | 29 | 1626.3248 | 1.2784 | 2.221 | 3.7789 | 5.1867 | 7.0323 | 0.006192%
-81 | 29 | 1600.4573 | 1.348 | 2.3382 | 3.9833 | 5.4226 | 7.3728 | 0.00654%
-80.5 | 29 | 1574.8039 | 1.3473 | 2.3429 | 4.0005 | 5.4488 | 7.4247 | 0.006651%
-80 | 29 | 1549.3754 | 1.3107 | 2.2902 | 3.9123 | 5.3531 | 7.3006 | 0.006579%
-79.5 | 29 | 1524.1834 | 1.2495 | 2.183 | 3.7445 | 5.1618 | 7.0342 | 0.006351%
-79 | 29 | 1499.2401 | 1.1601 | 2.0125 | 3.4888 | 4.8165 | 6.6143 | 0.005917%
-78.5 | 29 | 1474.5585 | 1.0208 | 1.7533 | 3.0926 | 4.2563 | 5.964 | 0.005249%
-78 | 29 | 1450.1522 | 0.85413 | 1.4504 | 2.6163 | 3.5873 | 5.173 | 0.004487%
-77.5 | 29 | 1426.0356 | 0.60565 | 1.0156 | 1.8576 | 2.6127 | 3.7676 | 0.003147%
-77 | 29 | 1402.224 | 0.39087 | 0.64846 | 1.1714 | 1.6785 | 2.5138 | 0.001924%
-76.5 | 29 | 1378.7335 | 0.20459 | 0.3367 | 0.60255 | 0.85848 | 1.3005 | 0.00082%
-76 | 29 | 1355.581 | 0.054095 | 0.088563 | 0.15753 | 0.22361 | 0.33728 | 0.0001454%
-75.5 | 29 | 1332.7843 | 0 | 0 | 0 | 0 | 0 | 0%
-75 | 29 | 1310.3625 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 29 | 1288.3352 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 29 | 1266.7233 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 29 | 1245.5487 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 29 | 1224.8343 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 29 | 1204.6042 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 29 | 1184.8832 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 29 | 1165.6976 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 29 | 1147.0744 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 29 | 1129.0416 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 29 | 1111.6282 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 29 | 1094.8639 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 29 | 1078.7793 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 29 | 1063.4052 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 29 | 1048.7732 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 29 | 1034.9149 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 29 | 1021.8618 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 29 | 1009.6455 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 29 | 998.2968 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 29 | 987.8456 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 29 | 978.3209 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 29 | 969.75 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 29 | 962.1587 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 29 | 955.5702 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 29 | 950.0056 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 29 | 945.4829 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 29 | 942.0173 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 29 | 939.6204 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 29 | 938.3006 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 29 | 938.0622 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 29 | 938.9063 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 29 | 940.8298 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 29 | 943.8261 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 29.5 | 2102.8313 | 5.7691 | 8.8044 | 13.6989 | 17.2957 | 22.7379 | 0.02649%
-89.5 | 29.5 | 2074.8258 | 6.2204 | 9.5532 | 14.6735 | 18.5846 | 24.5226 | 0.02987%
-89 | 29.5 | 2046.9214 | 6.7946 | 10.5672 | 16.0365 | 20.4408 | 26.866 | 0.03491%
-88.5 | 29.5 | 2019.1227 | 7.3833 | 11.6058 | 17.5029 | 22.4719 | 29.1285 | 0.04047%
-88 | 29.5 | 1991.4345 | 7.9135 | 12.3767 | 18.8705 | 24.3892 | 31.268 | 0.04595%
-87.5 | 29.5 | 1963.8618 | 8.1689 | 12.7625 | 19.5857 | 25.414 | 32.4298 | 0.049%
-87 | 29.5 | 1936.4099 | 7.9841 | 12.5297 | 19.2246 | 24.9424 | 31.956 | 0.04771%
-86.5 | 29.5 | 1909.0844 | 7.3343 | 11.6382 | 17.7358 | 22.9159 | 29.7724 | 0.0421%
-86 | 29.5 | 1881.891 | 6.3767 | 9.983 | 15.4833 | 19.8551 | 26.4103 | 0.03408%
-85.5 | 29.5 | 1854.8361 | 5.3925 | 8.2604 | 13.1004 | 16.616 | 21.9619 | 0.02537%
-85 | 29.5 | 1827.926 | 4.284 | 6.6934 | 10.757 | 13.664 | 17.8061 | 0.01871%
-84.5 | 29.5 | 1801.1675 | 3.4418 | 5.535 | 8.7339 | 11.5083 | 14.7999 | 0.01442%
-84 | 29.5 | 1774.568 | 2.9308 | 4.7319 | 7.4649 | 9.7606 | 12.8797 | 0.01153%
-83.5 | 29.5 | 1748.1349 | 2.6366 | 4.2132 | 6.744 | 8.7623 | 11.7932 | 0.01007%
-83 | 29.5 | 1721.8763 | 2.4123 | 3.8363 | 6.2384 | 8.0851 | 10.9605 | 0.009142%
-82.5 | 29.5 | 1695.8005 | 2.2769 | 3.623 | 5.9704 | 7.7471 | 10.5171 | 0.008784%
-82 | 29.5 | 1669.9166 | 2.1754 | 3.5013 | 5.8361 | 7.6015 | 10.3652 | 0.008896%
-81.5 | 29.5 | 1644.2337 | 2.1784 | 3.5207 | 5.8905 | 7.7028 | 10.5521 | 0.009257%
-81 | 29.5 | 1618.762 | 2.2311 | 3.6014 | 6.0236 | 7.9007 | 10.8618 | 0.009658%
-80.5 | 29.5 | 1593.5117 | 2.194 | 3.5634 | 5.9891 | 7.8736 | 10.8538 | 0.009797%
-80 | 29.5 | 1568.4939 | 2.0819 | 3.4218 | 5.8003 | 7.6339 | 10.5372 | 0.009637%
-79.5 | 29.5 | 1543.7202 | 1.9165 | 3.1981 | 5.4813 | 7.211 | 9.9486 | 0.009179%
-79 | 29.5 | 1519.2028 | 1.7272 | 2.9267 | 5.0786 | 6.6672 | 9.1754 | 0.008489%
-78.5 | 29.5 | 1494.9547 | 1.5159 | 2.6097 | 4.4944 | 6.0158 | 8.2447 | 0.00753%
-78 | 29.5 | 1470.9894 | 1.2859 | 2.2519 | 3.8448 | 5.2761 | 7.193 | 0.006483%
-77.5 | 29.5 | 1447.3213 | 1.0379 | 1.7843 | 3.1398 | 4.3221 | 6.0396 | 0.005319%
-77 | 29.5 | 1423.9655 | 0.74132 | 1.252 | 2.3007 | 3.15 | 4.5543 | 0.003918%
-76.5 | 29.5 | 1400.938 | 0.44978 | 0.74849 | 1.357 | 1.9488 | 2.8617 | 0.002266%
-76 | 29.5 | 1378.2553 | 0.22495 | 0.37057 | 0.66396 | 0.94664 | 1.4353 | 0.0009336%
-75.5 | 29.5 | 1355.9352 | 0.054028 | 0.088443 | 0.1573 | 0.22327 | 0.33674 | 0.0001449%
-75 | 29.5 | 1333.996 | 0 | 0 | 0 | 0 | 0 | 0%
-74.5 | 29.5 | 1312.4572 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 29.5 | 1291.3391 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 29.5 | 1270.6627 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 29.5 | 1250.4505 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 29.5 | 1230.7253 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 29.5 | 1211.5113 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 29.5 | 1192.8334 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 29.5 | 1174.7173 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 29.5 | 1157.1897 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 29.5 | 1140.278 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 29.5 | 1124.01 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 29.5 | 1108.4144 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 29.5 | 1093.5201 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 29.5 | 1079.3564 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 29.5 | 1065.9524 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 29.5 | 1053.3374 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 29.5 | 1041.5401 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 29.5 | 1030.5888 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 29.5 | 1020.5109 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 29.5 | 1011.3326 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 29.5 | 1003.0787 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 29.5 | 995.7722 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 29.5 | 989.4342 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 29.5 | 984.0836 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 29.5 | 979.7365 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 29.5 | 976.4065 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 29.5 | 974.1039 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 29.5 | 972.8361 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 29.5 | 972.6072 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 29.5 | 973.4179 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 29.5 | 975.2656 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 29.5 | 978.1444 | 0 | 0 | 0 | 0 | 0 | 0%
-90 | 30 | 2115.4819 | 6.0759 | 9.2512 | 14.163 | 17.8011 | 23.2785 | 0.02728%
-89.5 | 30 | 2087.7693 | 6.8154 | 10.578 | 15.9775 | 20.3044 | 26.6451 | 0.03437%
-89 | 30 | 2060.1629 | 7.8605 | 12.255 | 18.5501 | 23.8697 | 30.5687 | 0.04422%
-88.5 | 30 | 2032.6672 | 9.1064 | 13.9717 | 21.5545 | 27.5464 | 35.073 | 0.05608%
-88 | 30 | 2005.2874 | 10.7643 | 16.3426 | 26.0539 | 32.6054 | 42.4226 | 0.07584%
-87.5 | 30 | 1978.0285 | 11.8729 | 18.2437 | 29.1543 | 37.0733 | 49.1489 | 0.09312%
-87 | 30 | 1950.8959 | 11.6919 | 17.9276 | 28.6972 | 36.4409 | 48.2311 | 0.09058%
-86.5 | 30 | 1923.8954 | 10.264 | 15.7898 | 25.2895 | 31.8476 | 41.5378 | 0.07268%
-86 | 30 | 1897.033 | 8.3802 | 13.05 | 20.0333 | 25.9559 | 32.9749 | 0.05057%
-85.5 | 30 | 1870.3149 | 6.9563 | 10.9497 | 16.6079 | 21.2622 | 27.8073 | 0.0373%
-85 | 30 | 1843.7477 | 5.7206 | 8.7492 | 13.6337 | 17.1917 | 22.5676 | 0.02624%
-84.5 | 30 | 1817.3385 | 4.74 | 7.2148 | 11.5248 | 14.3262 | 18.4933 | 0.01925%
-84 | 30 | 1791.0945 | 4.0624 | 6.3197 | 9.9452 | 12.6653 | 16.1358 | 0.01569%
-83.5 | 30 | 1765.0234 | 3.5942 | 5.7006 | 8.8885 | 11.5938 | 14.6619 | 0.01379%
-83 | 30 | 1739.1334 | 3.3413 | 5.3681 | 8.3462 | 10.916 | 13.9491 | 0.01285%
-82.5 | 30 | 1713.4331 | 3.1624 | 5.1445 | 8.0263 | 10.5197 | 13.6147 | 0.01257%
-82 | 30 | 1687.9312 | 3.0572 | 5.0102 | 7.9003 | 10.4032 | 13.5863 | 0.01281%
-81.5 | 30 | 1662.6375 | 3.0703 | 5.065 | 8.0342 | 10.6328 | 13.9025 | 0.0135%
-81 | 30 | 1637.5617 | 3.1141 | 5.1512 | 8.2207 | 10.924 | 14.2695 | 0.01421%
-80.5 | 30 | 1612.7144 | 3.0889 | 5.1336 | 8.2291 | 10.9647 | 14.3663 | 0.0145%
-80 | 30 | 1588.1066 | 2.955 | 4.9232 | 7.9577 | 10.6154 | 14.0383 | 0.01415%
-79.5 | 30 | 1563.7499 | 2.7304 | 4.5269 | 7.4304 | 9.9042 | 13.2956 | 0.01319%
-79 | 30 | 1539.6566 | 2.4415 | 4.0137 | 6.7097 | 8.9205 | 12.226 | 0.01178%
-78.5 | 30 | 1515.8395 | 2.1173 | 3.4945 | 5.9453 | 7.8678 | 10.9305 | 0.01028%
-78 | 30 | 1492.3122 | 1.7673 | 2.9923 | 5.1855 | 6.8213 | 9.41 | 0.008776%
-77.5 | 30 | 1469.0887 | 1.4598 | 2.5228 | 4.3342 | 5.8336 | 7.9827 | 0.007256%
-77 | 30 | 1446.1842 | 1.1471 | 1.9855 | 3.4441 | 4.7502 | 6.5314 | 0.005804%
-76.5 | 30 | 1423.6141 | 0.75547 | 1.278 | 2.3447 | 3.2126 | 4.649 | 0.004023%
-76 | 30 | 1401.3951 | 0.43142 | 0.71759 | 1.3002 | 1.8665 | 2.7576 | 0.002167%
-75.5 | 30 | 1379.5443 | 0.20125 | 0.33108 | 0.59225 | 0.84358 | 1.2776 | 0.0007999%
-75 | 30 | 1358.0797 | 0.029644 | 0.04844 | 0.085972 | 0.12187 | 0.18353 | 6.624e-05%
-74.5 | 30 | 1337.0202 | 0 | 0 | 0 | 0 | 0 | 0%
-74 | 30 | 1316.3856 | 0 | 0 | 0 | 0 | 0 | 0%
-73.5 | 30 | 1296.1963 | 0 | 0 | 0 | 0 | 0 | 0%
-73 | 30 | 1276.4738 | 0 | 0 | 0 | 0 | 0 | 0%
-72.5 | 30 | 1257.2402 | 0 | 0 | 0 | 0 | 0 | 0%
-72 | 30 | 1238.5185 | 0 | 0 | 0 | 0 | 0 | 0%
-71.5 | 30 | 1220.3326 | 0 | 0 | 0 | 0 | 0 | 0%
-71 | 30 | 1202.707 | 0 | 0 | 0 | 0 | 0 | 0%
-70.5 | 30 | 1185.6668 | 0 | 0 | 0 | 0 | 0 | 0%
-70 | 30 | 1169.2378 | 0 | 0 | 0 | 0 | 0 | 0%
-69.5 | 30 | 1153.4465 | 0 | 0 | 0 | 0 | 0 | 0%
-69 | 30 | 1138.3195 | 0 | 0 | 0 | 0 | 0 | 0%
-68.5 | 30 | 1123.8837 | 0 | 0 | 0 | 0 | 0 | 0%
-68 | 30 | 1110.1665 | 0 | 0 | 0 | 0 | 0 | 0%
-67.5 | 30 | 1097.1947 | 0 | 0 | 0 | 0 | 0 | 0%
-67 | 30 | 1084.9955 | 0 | 0 | 0 | 0 | 0 | 0%
-66.5 | 30 | 1073.5951 | 0 | 0 | 0 | 0 | 0 | 0%
-66 | 30 | 1063.0196 | 0 | 0 | 0 | 0 | 0 | 0%
-65.5 | 30 | 1053.2938 | 0 | 0 | 0 | 0 | 0 | 0%
-65 | 30 | 1044.4415 | 0 | 0 | 0 | 0 | 0 | 0%
-64.5 | 30 | 1036.4854 | 0 | 0 | 0 | 0 | 0 | 0%
-64 | 30 | 1029.4462 | 0 | 0 | 0 | 0 | 0 | 0%
-63.5 | 30 | 1023.343 | 0 | 0 | 0 | 0 | 0 | 0%
-63 | 30 | 1018.1926 | 0 | 0 | 0 | 0 | 0 | 0%
-62.5 | 30 | 1014.0096 | 0 | 0 | 0 | 0 | 0 | 0%
-62 | 30 | 1010.8062 | 0 | 0 | 0 | 0 | 0 | 0%
-61.5 | 30 | 1008.5916 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 30 | 1007.3725 | 0 | 0 | 0 | 0 | 0 | 0%
-60.5 | 30 | 1007.1523 | 0 | 0 | 0 | 0 | 0 | 0%
-60 | 30 | 1007.9319 | 0 | 0 | 0 | 0 | 0 | 0%
-59.5 | 30 | 1009.7089 | 0 | 0 | 0 | 0 | 0 | 0%
-59 | 30 | 1012.478 | 0 | 0 | 0 | 0 | 0 | 0%
-61 | 1.5 | 962.3596 | 5.7741 | 9.3044 | 14.9629 | 19.3932 | 26.1666 | 0.03424%
-60.5 | 1.5 | 962.0939 | 6.9539 | 11.4978 | 17.9298 | 23.4932 | 30.5218 | 0.04451%
-60 | 1.5 | 963.035 | 8.0726 | 13.1218 | 20.8116 | 27.1127 | 34.7725 | 0.05507%
-59.5 | 1.5 | 965.1792 | 8.619 | 13.8901 | 22.1935 | 28.5633 | 36.7907 | 0.06012%
-59 | 1.5 | 968.5187 | 8.4852 | 13.7049 | 21.861 | 28.2169 | 36.3109 | 0.0589%
-58.5 | 1.5 | 973.0411 | 7.7124 | 12.6047 | 19.8851 | 26.1309 | 33.4093 | 0.05178%
-58 | 1.5 | 978.7301 | 6.5708 | 10.788 | 16.9773 | 22.1746 | 29.1396 | 0.04109%
-57.5 | 1.5 | 985.5653 | 5.3466 | 8.52 | 13.8606 | 17.8752 | 24.0921 | 0.03022%
-57 | 1.5 | 993.5232 | 4.01 | 6.5869 | 10.9639 | 14.0576 | 18.6003 | 0.02139%
-61 | 2 | 927.8243 | 4.3594 | 7.0908 | 11.8192 | 15.0849 | 20.085 | 0.02374%
-60.5 | 2 | 927.549 | 5.3012 | 8.4452 | 13.7643 | 17.7494 | 23.9202 | 0.02992%
-60 | 2 | 928.5241 | 5.965 | 9.6655 | 15.4722 | 20.103 | 26.9426 | 0.03597%
-59.5 | 2 | 930.7457 | 6.3088 | 10.3124 | 16.3578 | 21.3292 | 28.2619 | 0.039%
-59 | 2 | 934.205 | 6.2446 | 10.1945 | 16.2011 | 21.1144 | 28.0352 | 0.03847%
-58.5 | 2 | 938.8882 | 5.8051 | 9.3766 | 15.0812 | 19.5685 | 26.3716 | 0.03471%
-58 | 2 | 944.7771 | 5.0856 | 8.0606 | 13.2221 | 17.0092 | 22.8579 | 0.02799%
-57.5 | 2 | 951.8494 | 4.0295 | 6.622 | 11.0374 | 14.1418 | 18.7305 | 0.02163%
-57 | 2 | 960.0789 | 3.2121 | 5.4028 | 8.7729 | 11.7017 | 15.2444 | 0.01626%
-61 | 2.5 | 893.2899 | 3.172 | 5.349 | 8.6812 | 11.6055 | 15.1173 | 0.01611%
-60.5 | 2.5 | 893.0041 | 3.662 | 6.0934 | 10.0565 | 13.0996 | 17.2494 | 0.01933%
-60 | 2.5 | 894.0159 | 4.1067 | 6.745 | 11.2851 | 14.414 | 19.1352 | 0.02234%
-59.5 | 2.5 | 896.3207 | 4.3767 | 7.1303 | 11.8924 | 15.1986 | 20.2678 | 0.02409%
-59 | 2.5 | 899.9087 | 4.3432 | 7.0872 | 11.8328 | 15.1192 | 20.157 | 0.02394%
-58.5 | 2.5 | 904.7645 | 4.0043 | 6.6018 | 11.0173 | 14.1332 | 18.737 | 0.02171%
-58 | 2.5 | 910.868 | 3.513 | 5.8696 | 9.6386 | 12.6481 | 16.6059 | 0.01833%
-57.5 | 2.5 | 918.194 | 3.0129 | 5.101 | 8.2283 | 11.0056 | 14.4112 | 0.01496%
-57 | 2.5 | 926.7138 | 2.5766 | 4.2551 | 7.0009 | 9.26 | 12.4934 | 0.01196%
-61 | 3 | 858.7564 | 2.4497 | 4.0127 | 6.6368 | 8.7392 | 11.9115 | 0.01109%
-60.5 | 3 | 858.4595 | 2.6927 | 4.4735 | 7.3114 | 9.6926 | 12.9639 | 0.01264%
-60 | 3 | 859.5108 | 2.9104 | 4.8912 | 7.9003 | 10.5212 | 13.8653 | 0.014%
-59.5 | 3 | 861.9053 | 3.0279 | 5.1131 | 8.2229 | 10.978 | 14.3623 | 0.01479%
-59 | 3 | 865.632 | 3.0207 | 5.1007 | 8.197 | 10.9387 | 14.3172 | 0.01471%
-58.5 | 3 | 870.6737 | 2.8678 | 4.8092 | 7.7847 | 10.3575 | 13.6878 | 0.01373%
-58 | 3 | 877.0076 | 2.6359 | 4.3617 | 7.144 | 9.4518 | 12.6949 | 0.01221%
-57.5 | 3 | 884.6061 | 2.3579 | 3.8441 | 6.3912 | 8.3969 | 11.5365 | 0.01058%
-57 | 3 | 893.4369 | 2.0799 | 3.4063 | 5.7304 | 7.4619 | 10.1717 | 0.008954%
-61 | 3.5 | 824.2239 | 2.3001 | 3.654 | 5.9754 | 7.6941 | 10.3512 | 0.008395%
-60.5 | 3.5 | 823.915 | 2.353 | 3.7682 | 6.171 | 7.995 | 10.8339 | 0.009153%
-60 | 3.5 | 825.0091 | 2.4502 | 3.9487 | 6.4377 | 8.3732 | 11.3985 | 0.009916%
-59.5 | 3.5 | 827.5007 | 2.5335 | 4.0957 | 6.6391 | 8.6471 | 11.701 | 0.01028%
-59 | 3.5 | 831.3773 | 2.4679 | 3.9903 | 6.5124 | 8.4898 | 11.5518 | 0.01019%
-58.5 | 3.5 | 836.6196 | 2.3494 | 3.7846 | 6.2318 | 8.112 | 11.0535 | 0.00961%
-58 | 3.5 | 843.202 | 2.1541 | 3.4852 | 5.8103 | 7.5381 | 10.2312 | 0.008755%
-57.5 | 3.5 | 851.0936 | 1.8938 | 3.1278 | 5.2987 | 6.8415 | 9.2337 | 0.007896%
-57 | 3.5 | 860.2583 | 1.7257 | 2.8754 | 4.8732 | 6.3066 | 8.4419 | 0.007044%
-61 | 4 | 789.6928 | 2.8249 | 4.4589 | 6.8411 | 8.6939 | 11.4965 | 0.008743%
-60.5 | 4 | 789.3706 | 2.6564 | 4.1967 | 6.5669 | 8.3738 | 11.1376 | 0.008617%
-60 | 4 | 790.5112 | 2.5063 | 3.9671 | 6.3223 | 8.0928 | 10.8122 | 0.008523%
-59.5 | 4 | 793.1082 | 2.4524 | 3.8869 | 6.2382 | 7.9994 | 10.7098 | 0.008524%
-59 | 4 | 797.1474 | 2.32 | 3.6736 | 5.9765 | 7.67 | 10.2786 | 0.008175%
-58.5 | 4 | 802.6069 | 2.1174 | 3.3917 | 5.609 | 7.1933 | 9.6319 | 0.007719%
-58 | 4 | 809.4581 | 1.8507 | 3.0378 | 5.1307 | 6.5669 | 8.7726 | 0.007176%
-57.5 | 4 | 817.6658 | 1.6282 | 2.7226 | 4.5748 | 5.9742 | 7.9429 | 0.006453%
-57 | 4 | 827.1899 | 1.47 | 2.4868 | 4.1423 | 5.5104 | 7.2813 | 0.005825%
-61 | 4.5 | 755.163 | 3.3506 | 5.2711 | 7.8726 | 10.048 | 12.7786 | 0.01003%
-60.5 | 4.5 | 754.8265 | 3.1128 | 4.9467 | 7.4465 | 9.5104 | 12.3039 | 0.009639%
-60 | 4.5 | 756.0178 | 2.8488 | 4.5205 | 6.979 | 8.9302 | 11.7871 | 0.009329%
-59.5 | 4.5 | 758.7296 | 2.6576 | 4.2115 | 6.6208 | 8.479 | 11.3348 | 0.009001%
-59 | 4.5 | 762.9456 | 2.4264 | 3.836 | 6.1633 | 7.8943 | 10.5549 | 0.008311%
-58.5 | 4.5 | 768.6412 | 2.137 | 3.407 | 5.6133 | 7.1823 | 9.5912 | 0.007556%
-58 | 4.5 | 775.7837 | 1.798 | 2.9575 | 4.9869 | 6.3912 | 8.5083 | 0.006872%
-57.5 | 4.5 | 784.3336 | 1.457 | 2.476 | 4.1382 | 5.5172 | 7.3145 | 0.005952%
-57 | 4.5 | 794.2454 | 1.2216 | 2.093 | 3.5189 | 4.7841 | 6.3969 | 0.005171%
-61 | 5 | 720.6348 | 4.1373 | 6.2503 | 9.5153 | 12.0457 | 14.9494 | 0.01285%
-60.5 | 5 | 720.2827 | 3.8002 | 5.8487 | 8.9009 | 11.479 | 14.2696 | 0.01229%
-60 | 5 | 721.5294 | 3.4328 | 5.412 | 8.2579 | 10.6779 | 13.5664 | 0.01162%
-59.5 | 5 | 724.3667 | 3.0097 | 4.8298 | 7.4844 | 9.7011 | 12.6837 | 0.01084%
-59 | 5 | 728.776 | 2.7248 | 4.3664 | 6.9166 | 8.9601 | 11.9564 | 0.01015%
-58.5 | 5 | 734.7289 | 2.3185 | 3.7003 | 6.0705 | 7.8586 | 10.6391 | 0.008888%
-58 | 5 | 742.1885 | 1.8604 | 3.0818 | 5.232 | 6.7521 | 9.1081 | 0.007794%
-57.5 | 5 | 751.1096 | 1.5495 | 2.6335 | 4.4497 | 5.8729 | 7.8576 | 0.006635%
-57 | 5 | 761.441 | 1.221 | 2.1137 | 3.5765 | 4.8865 | 6.551 | 0.005517%
-61 | 5.5 | 686.1084 | 5.3864 | 7.8543 | 12.0033 | 14.6431 | 18.4899 | 0.01764%
-60.5 | 5.5 | 685.7391 | 5.019 | 7.3414 | 11.4091 | 13.9626 | 17.6795 | 0.01666%
-60 | 5.5 | 687.0467 | 4.5929 | 6.8764 | 10.7176 | 13.361 | 16.9843 | 0.01609%
-59.5 | 5.5 | 690.0219 | 4.111 | 6.329 | 9.9055 | 12.6214 | 16.1134 | 0.01539%
-59 | 5.5 | 694.6432 | 3.5139 | 5.6072 | 8.8093 | 11.5606 | 14.8066 | 0.01423%
-58.5 | 5.5 | 700.8779 | 2.9521 | 4.8197 | 7.6401 | 10.0419 | 13.238 | 0.0123%
-58 | 5.5 | 708.6836 | 2.3555 | 3.817 | 6.3239 | 8.2857 | 11.3767 | 0.01023%
-57.5 | 5.5 | 718.0089 | 1.7349 | 2.9557 | 5.1126 | 6.6594 | 9.0811 | 0.008332%
-57 | 5.5 | 728.7955 | 1.4215 | 2.4708 | 4.1962 | 5.6306 | 7.5773 | 0.006669%
-61 | 6 | 651.5842 | 7.0782 | 10.5155 | 15.2551 | 18.8942 | 24.2857 | 0.02814%
-60.5 | 6 | 651.1958 | 6.6797 | 9.9247 | 14.6489 | 18.1979 | 23.4732 | 0.02671%
-60 | 6 | 652.5708 | 6.2867 | 9.3891 | 14.1348 | 17.6537 | 22.9149 | 0.02598%
-59.5 | 6 | 655.6982 | 5.7674 | 8.6676 | 13.3742 | 16.795 | 21.9402 | 0.02459%
-59 | 6 | 660.5529 | 5.109 | 7.7048 | 12.2326 | 15.4033 | 20.1869 | 0.02192%
-58.5 | 6 | 667.0974 | 4.0972 | 6.4822 | 10.4726 | 13.4321 | 17.5948 | 0.01868%
-58 | 6 | 675.2825 | 3.1463 | 5.2042 | 8.3172 | 11.0618 | 14.4802 | 0.01455%
-57.5 | 6 | 685.0493 | 2.2984 | 3.7616 | 6.3195 | 8.3438 | 11.5342 | 0.0108%
-57 | 6 | 696.3313 | 1.7077 | 2.9234 | 5.0699 | 6.6093 | 9.0175 | 0.008336%
-61 | 6.5 | 617.0625 | 9.9967 | 14.2801 | 20.8341 | 26.114 | 32.0398 | 0.04882%
-60.5 | 6.5 | 616.6529 | 9.4498 | 13.718 | 20.123 | 25.4042 | 31.4375 | 0.04683%
-60 | 6.5 | 618.1027 | 8.8239 | 13.0705 | 19.3339 | 24.532 | 30.8108 | 0.04478%
-59.5 | 6.5 | 621.3989 | 7.9847 | 12.1403 | 18.1185 | 23.1148 | 29.5995 | 0.0414%
-59 | 6.5 | 626.5122 | 6.9533 | 10.7561 | 16.3355 | 20.8996 | 27.4376 | 0.03611%
-58.5 | 6.5 | 633.3988 | 5.7096 | 8.7852 | 13.853 | 17.6928 | 23.5762 | 0.02833%
-58 | 6.5 | 642.0015 | 4.3198 | 6.8265 | 11.1683 | 14.2533 | 18.8656 | 0.02091%
-57.5 | 6.5 | 652.2523 | 3.0442 | 5.0603 | 8.1226 | 10.8267 | 14.2955 | 0.01439%
-57 | 6.5 | 664.075 | 2.1079 | 3.4841 | 5.91 | 7.7767 | 10.7317 | 0.009957%
-61 | 7 | 582.5437 | 14.1173 | 19.8938 | 28.7518 | 34.6848 | 43.2257 | 0.0891%
-60.5 | 7 | 582.1104 | 13.3171 | 18.7854 | 27.5543 | 33.3228 | 41.6493 | 0.08159%
-60 | 7 | 583.6438 | 12.408 | 17.6453 | 26.4497 | 32.2357 | 40.6585 | 0.07583%
-59.5 | 7 | 587.1283 | 11.495 | 16.826 | 26.1727 | 32.6121 | 42.2156 | 0.07651%
-59 | 7 | 592.5296 | 9.8834 | 15.5714 | 25.8747 | 34.3175 | 47.7993 | 0.08085%
-58.5 | 7 | 599.7958 | 7.4324 | 11.6831 | 17.9294 | 23.265 | 30.3441 | 0.0432%
-58 | 7 | 608.8601 | 5.5049 | 8.451 | 13.4347 | 17.2013 | 22.9883 | 0.02727%
-57.5 | 7 | 619.6437 | 3.8259 | 6.1009 | 9.8544 | 12.8333 | 16.9091 | 0.01776%
-57 | 7 | 632.0585 | 2.5452 | 4.1121 | 6.7571 | 8.9281 | 12.1757 | 0.01122%
-61 | 7.5 | 548.0284 | 19.8134 | 27.8521 | 38.3734 | 46.6315 | 58.5035 | 0.1713%
-60.5 | 7.5 | 547.5685 | 18.1656 | 25.9701 | 35.8062 | 43.531 | 54.7455 | 0.1463%
-60 | 7.5 | 549.1958 | 16.9997 | 25.025 | 36.3943 | 45.5505 | 59.0852 | 0.1446%
-59.5 | 7.5 | 552.8919 | 16.002 | 24.6758 | 37.7339 | 48.6248 | 64.1469 | 0.1467%
-59 | 7.5 | 558.6156 | 14.0847 | 22.7262 | 36.9822 | 49.0944 | 66.3825 | 0.1357%
-58.5 | 7.5 | 566.3054 | 10.3698 | 16.804 | 28.476 | 37.4032 | 51.5078 | 0.09077%
-58 | 7.5 | 575.8826 | 6.6225 | 10.187 | 15.7413 | 20.2571 | 26.9536 | 0.03489%
-57.5 | 7.5 | 587.2548 | 4.5209 | 6.8955 | 11.0114 | 14.0318 | 18.5027 | 0.01932%
-57 | 7.5 | 600.3201 | 3.0095 | 4.7718 | 7.5555 | 9.9294 | 13.2143 | 0.01184%
-61 | 8 | 513.5172 | 30.2678 | 40.7293 | 57.6135 | 68.0252 | 82.4689 | 0.4196%
-60.5 | 8 | 513.0272 | 27.157 | 36.3096 | 50.9779 | 61.6696 | 74.6093 | 0.3247%
-60 | 8 | 514.761 | 23.6428 | 33.2905 | 48.5991 | 60.7375 | 76.5963 | 0.2561%
-59.5 | 8 | 518.6963 | 20.8458 | 31.3619 | 48.7 | 62.8056 | 82.0984 | 0.2235%
-59 | 8 | 524.7835 | 17.1081 | 28.2454 | 51.2611 | 70.742 | 100.6605 | 0.1967%
-58.5 | 8 | 532.9489 | 10.5272 | 15.1878 | 22.8484 | 28.6924 | 36.624 | 0.06035%
-58 | 8 | 543.0988 | 7.2631 | 10.7699 | 16.0035 | 20.2417 | 26.5084 | 0.03308%
-57.5 | 8 | 555.1242 | 5.0995 | 7.429 | 11.5175 | 14.4625 | 18.8919 | 0.01862%
-57 | 8 | 568.9063 | 3.3726 | 5.1407 | 7.8617 | 10.1797 | 13.3538 | 0.01086%
-90 | 15 | 1956.2095 | 172.6554 | 220.7961 | 294.288 | 330.0232 | 376.9813 | 64.01%
-89.5 | 15 | 1922.9542 | 159.8313 | 202.9874 | 268.3741 | 309.9406 | 352.9148 | 46.79%
-89 | 15 | 1889.6964 | 160.1887 | 206.5121 | 277.8549 | 319.4074 | 367.0116 | 38.62%
-88.5 | 15 | 1856.4361 | 146.5833 | 186.7979 | 247.9552 | 294.5686 | 337.517 | 28.69%
-88 | 15 | 1823.1732 | 125.8721 | 161.9718 | 214.0349 | 253.5761 | 307.2304 | 15.95%
-90 | 15.5 | 1953.6146 | 166.5924 | 216.2337 | 293.2563 | 332.9325 | 385.3446 | 41.43%
-89.5 | 15.5 | 1920.3979 | 156.7152 | 200.4769 | 267.3074 | 310.5209 | 356.0471 | 37.77%
-89 | 15.5 | 1887.1783 | 180.2125 | 241.6155 | 324.0558 | 371.4149 | 435.8837 | 43.26%
-88.5 | 15.5 | 1853.956 | 172.6408 | 226.3392 | 305.2958 | 346.6195 | 402.2951 | 45%
-88 | 15.5 | 1820.731 | 166.292 | 213.7443 | 286.5891 | 325.5702 | 373.587 | 48.19%
-90 | 16 | 1951.5777 | 138.1367 | 176.3476 | 234.5705 | 279.0203 | 326.6004 | 22.11%
-89.5 | 16 | 1918.4109 | 136.1317 | 171.9525 | 225.9049 | 266.693 | 314.4253 | 24.14%
-89 | 16 | 1885.2415 | 150.3382 | 194.1954 | 261.8857 | 308.0028 | 356.1936 | 27.18%
-88.5 | 16 | 1852.0696 | 160.1295 | 205.8741 | 276.1163 | 318.0367 | 365.6398 | 39.33%
-88 | 16 | 1818.8951 | 167.2593 | 213.6695 | 284.4378 | 322.6627 | 368.3727 | 54.94%
-90 | 16.5 | 1950.1004 | 78.1644 | 104.7 | 144.5703 | 172.1069 | 211.177 | 3.697%
-89.5 | 16.5 | 1916.9952 | 91.2919 | 126.4155 | 167.0321 | 196.6055 | 238.0494 | 6.25%
-89 | 16.5 | 1883.8878 | 111.202 | 149.1693 | 196.6338 | 232.6125 | 283.3095 | 10.56%
-88.5 | 16.5 | 1850.7785 | 130.6626 | 164.8713 | 216.0492 | 254.6617 | 304.5113 | 21.03%
-88 | 16.5 | 1817.6672 | 143.0165 | 179.7116 | 234.668 | 276.016 | 320.5612 | 31.85%
-90 | 17 | 1949.1841 | 48.9029 | 66.915 | 92.24 | 112.1254 | 140.968 | 1.178%
-89.5 | 17 | 1916.1519 | 48.4332 | 65.018 | 86.1873 | 102.305 | 125.1009 | 1.325%
-89 | 17 | 1883.1185 | 61.1266 | 79.1852 | 107.1447 | 128.7797 | 154.2939 | 2.291%
-88.5 | 17 | 1850.084 | 82.4762 | 113.9571 | 156.3626 | 185.4348 | 226.5117 | 4.176%
-88 | 17 | 1817.0486 | 101.5723 | 138.6088 | 180.7862 | 212.4906 | 256.8513 | 8.905%
-90 | 17.5 | 1948.8296 | 29.8681 | 39.1962 | 53.8442 | 64.3292 | 78.3356 | 0.3986%
-89.5 | 17.5 | 1915.8819 | 29.3607 | 37.7507 | 50.6347 | 60.0113 | 70.7316 | 0.383%
-89 | 17.5 | 1882.9342 | 33.2445 | 43.4872 | 59.1362 | 67.9283 | 79.9256 | 0.5423%
-88.5 | 17.5 | 1849.9868 | 40.9794 | 55.4877 | 71.6335 | 82.912 | 98.4303 | 0.977%
-88 | 17.5 | 1817.0399 | 56.1559 | 71.9241 | 94.6119 | 111.7812 | 134.6921 | 2.071%
-90 | 18 | 1949.0371 | 19.1898 | 26.2014 | 34.6935 | 41.1533 | 50.283 | 0.1432%
-89.5 | 18 | 1916.1853 | 18.6814 | 25.2617 | 32.4855 | 37.7079 | 44.9159 | 0.1226%
-89 | 18 | 1883.3352 | 21.2211 | 28.2233 | 36.4931 | 42.6669 | 51.2556 | 0.1688%
-88.5 | 18 | 1850.487 | 26.5557 | 33.7797 | 44.744 | 53.0869 | 63.5501 | 0.2901%
-88 | 18 | 1817.6412 | 31.8328 | 41.1629 | 55.5799 | 64.0735 | 74.5412 | 0.4846%
-90 | 18.5 | 1949.8066 | 13.4714 | 17.6294 | 24.1387 | 28.6011 | 34.4331 | 0.05841%
-89.5 | 18.5 | 1917.062 | 13.8792 | 18.3895 | 25.5467 | 30.6351 | 37.8706 | 0.06964%
-89 | 18.5 | 1884.321 | 16.1059 | 22.2138 | 32.0584 | 39.9308 | 51.6668 | 0.1172%
-88.5 | 18.5 | 1851.5841 | 18.8127 | 26.3493 | 37.0804 | 45.6448 | 58.2597 | 0.1574%
-88 | 18.5 | 1818.8518 | 21.8623 | 29.6063 | 40.0302 | 48.0914 | 59.7052 | 0.1979%

## Cyclones (hidden)
[5 empty] | 2% | 1% | 0.4% | 0.2% | 0.1%
[5 empty] | 50 yrs | 100 yrs | 250 yrs | 500 yrs | 1000 yrs
DATA |  | Longitudes (x) | Latitudes (y) | Distance | km/h | km/h | km/h | km/h | km/h | Probability
1 | 9-50 | -50.0371 | 9.0318 | 840.825 | 58.6607 | 78.6239 | 109.8222 | 137.2144 | 165.868 | 0.1487%
2 | 9-50.5 | -50.3084 | 9.0318 | 825.3029 | 58.4648 | 78.3498 | 109.5191 | 136.9663 | 165.7242 | 0.148%
3 | 9-50.5 | -50.5797 | 9.0318 | 809.8969 | 58.2791 | 78.0862 | 109.2333 | 136.7533 | 165.6298 | 0.1475%
4 | 9-51 | -50.851 | 9.0318 | 794.6139 | 58.1121 | 77.8497 | 108.9878 | 136.5981 | 165.6118 | 0.1471%
5 | 9-51 | -51.1224 | 9.0318 | 779.4611 | 57.9734 | 77.6589 | 108.8073 | 136.5243 | 165.6983 | 0.147%
6 | 9-51.5 | -51.3937 | 9.0318 | 764.4463 | 57.8549 | 77.5061 | 108.6644 | 136.4809 | 165.8065 | 0.147%
7 | 9-51.5 | -51.665 | 9.0318 | 749.5777 | 57.7728 | 77.4206 | 108.5893 | 136.4952 | 165.9572 | 0.1471%
8 | 9-52 | -51.9363 | 9.0318 | 734.8643 | 57.7466 | 77.4333 | 108.6128 | 136.5986 | 166.1794 | 0.1475%
9 | 9-52 | -52.2077 | 9.0318 | 720.3155 | 57.7672 | 77.5192 | 108.7147 | 136.7815 | 166.4656 | 0.1482%
10 | 9-52.5 | -52.479 | 9.0318 | 705.9417 | 57.8514 | 77.688 | 108.894 | 137.039 | 166.8141 | 0.149%
11 | 9-53 | -52.7503 | 9.0318 | 691.7536 | 58.0131 | 77.948 | 109.1528 | 137.3691 | 167.224 | 0.15%
12 | 9-53 | -53.0216 | 9.0318 | 677.763 | 58.1983 | 78.2241 | 109.415 | 137.6889 | 167.6099 | 0.151%
13 | 9-53.5 | -53.2929 | 9.0318 | 663.9824 | 58.4354 | 78.542 | 109.7085 | 138.0251 | 168.0009 | 0.152%
14 | 9-53.5 | -53.5643 | 9.0318 | 650.4251 | 58.7459 | 78.9227 | 110.054 | 138.3949 | 168.4119 | 0.1531%
15 | 9-54 | -53.8356 | 9.0318 | 637.1054 | 59.0824 | 79.3188 | 110.3919 | 138.7244 | 168.7431 | 0.1541%
16 | 9-54 | -54.1069 | 9.0318 | 624.0385 | 59.4734 | 79.7528 | 110.7388 | 139.0281 | 169.011 | 0.1549%
17 | 9-54.5 | -54.3782 | 9.0318 | 611.2408 | 59.9271 | 80.235 | 111.1014 | 139.3097 | 169.2186 | 0.1557%
18 | 9-54.5 | -54.6495 | 9.0318 | 598.7293 | 60.3983 | 80.7176 | 111.4248 | 139.5151 | 169.3089 | 0.1562%
19 | 9-55 | -54.9209 | 9.0318 | 586.5225 | 60.8965 | 81.2108 | 111.738 | 139.6948 | 169.3624 | 0.1566%
20 | 9-55 | -55.1922 | 9.0318 | 574.6398 | 61.4097 | 81.6946 | 112.0285 | 139.8444 | 169.3862 | 0.1569%
21 | 9-55.5 | -55.4635 | 9.0318 | 563.1018 | 61.8762 | 82.102 | 112.2383 | 139.9107 | 169.3354 | 0.157%
22 | 9-55.5 | -55.7348 | 9.0318 | 551.93 | 62.304 | 82.4563 | 112.3871 | 139.9055 | 169.2182 | 0.1568%
23 | 9-56 | -56.0061 | 9.0318 | 541.1471 | 62.6805 | 82.7482 | 112.4721 | 139.826 | 169.0313 | 0.1564%
24 | 9-56.5 | -56.2775 | 9.0318 | 530.777 | 62.9579 | 82.9322 | 112.4552 | 139.6392 | 168.7421 | 0.1557%
25 | 9-56.5 | -56.5488 | 9.0318 | 520.8441 | 63.1885 | 83.0828 | 112.4155 | 139.4334 | 168.4435 | 0.1549%
26 | 9-57 | -56.8201 | 9.0318 | 511.3741 | 63.3628 | 83.1905 | 112.3495 | 139.208 | 168.1358 | 0.1541%
27 | 9-57 | -57.0914 | 9.0318 | 502.3931 | 63.4307 | 83.1943 | 112.2079 | 138.9096 | 167.7522 | 0.1531%
28 | 9-57.5 | -57.3628 | 9.0318 | 493.9277 | 63.4399 | 83.1453 | 112.0536 | 138.6178 | 167.4004 | 0.1521%
29 | 9-57.5 | -57.6341 | 9.0318 | 486.0051 | 63.3651 | 83.0256 | 111.8665 | 138.3136 | 167.0599 | 0.1512%
30 | 9-58 | -57.9054 | 9.0318 | 478.652 | 63.1576 | 82.7892 | 111.5847 | 137.9234 | 166.6345 | 0.15%
31 | 9-58 | -58.1767 | 9.0318 | 471.8951 | 62.8609 | 82.462 | 111.2614 | 137.5036 | 166.1836 | 0.1487%
32 | 9-58.5 | -58.448 | 9.0318 | 465.7605 | 62.472 | 82.0454 | 110.8896 | 137.0463 | 165.6998 | 0.1474%
33 | 9-58.5 | -58.7194 | 9.0318 | 460.2729 | 61.9722 | 81.5361 | 110.4472 | 136.5208 | 165.1454 | 0.1459%
34 | 9-59 | -58.9907 | 9.0318 | 455.4558 | 61.4089 | 80.9705 | 109.9753 | 135.9687 | 164.5543 | 0.1443%
35 | 9-59.5 | -59.262 | 9.0318 | 451.3307 | 60.7673 | 80.3229 | 109.4404 | 135.3556 | 163.8966 | 0.1427%
36 | 9-59.5 | -59.5333 | 9.0318 | 447.9166 | 60.0272 | 79.5562 | 108.7813 | 134.6125 | 163.1098 | 0.1407%
37 | 9-60 | -59.8046 | 9.0318 | 445.23 | 59.2265 | 78.7107 | 108.0348 | 133.7732 | 162.2258 | 0.1385%
38 | 9-60 | -60.076 | 9.0318 | 443.284 | 58.3544 | 77.775 | 107.1749 | 132.8181 | 161.2056 | 0.1359%
39 | 9-60.5 | -60.3473 | 9.0318 | 442.0884 | 57.4054 | 76.7403 | 106.1709 | 131.7204 | 160.0076 | 0.1331%
40 | 9-60.5 | -60.6186 | 9.0318 | 441.6494 | 56.4168 | 75.6528 | 105.0659 | 130.53 | 158.7021 | 0.13%
41 | 9-61 | -60.8899 | 9.0318 | 441.9692 | 55.4354 | 74.581 | 103.9732 | 129.3783 | 157.4255 | 0.1271%
42 | 9-61 | -61.1613 | 9.0318 | 443.0462 | 54.5364 | 73.6288 | 103.059 | 128.4583 | 156.3797 | 0.125%
43 | 9-61.5 | -61.4326 | 9.0318 | 444.8748 | 53.7605 | 72.8347 | 102.3903 | 127.8249 | 155.6603 | 0.1236%
44 | 9-61.5 | -61.7039 | 9.0318 | 447.4458 | 53.044 | 72.1169 | 101.8015 | 127.293 | 155.0887 | 0.1226%
45 | 9-62 | -61.9752 | 9.0318 | 450.7466 | 52.3126 | 71.3664 | 101.1234 | 126.6763 | 154.4961 | 0.1214%
46 | 9-62 | -62.2465 | 9.0318 | 454.7612 | 51.5852 | 70.5905 | 100.388 | 126.012 | 153.9333 | 0.1202%
47 | 9-62.5 | -62.5179 | 9.0318 | 459.4709 | 50.8578 | 69.8026 | 99.6101 | 125.2974 | 153.3495 | 0.1189%
48 | 9-63 | -62.7892 | 9.0318 | 464.8546 | 50.1419 | 69.0297 | 98.8295 | 124.5736 | 152.7286 | 0.1176%
49 | 9-63 | -63.0605 | 9.0318 | 470.8892 | 49.456 | 68.3049 | 98.1092 | 123.9143 | 152.1408 | 0.1164%
50 | 9-63.5 | -63.3318 | 9.0318 | 477.5499 | 48.8014 | 67.6247 | 97.4478 | 123.3267 | 151.6171 | 0.1154%
51 | 9-63.5 | -63.6031 | 9.0318 | 484.811 | 48.1859 | 66.9997 | 96.8643 | 122.8286 | 151.205 | 0.1147%
52 | 9-64 | -63.8745 | 9.0318 | 492.646 | 47.6171 | 66.4441 | 96.3923 | 122.4508 | 150.9528 | 0.1143%
53 | 9-64 | -64.1458 | 9.0318 | 501.0278 | 47.0351 | 65.8715 | 95.8808 | 122.0321 | 150.6765 | 0.1138%
54 | 9-64.5 | -64.4171 | 9.0318 | 509.9296 | 46.3578 | 65.1617 | 95.1413 | 121.3234 | 150.1392 | 0.1128%
55 | 9-64.5 | -64.6884 | 9.0318 | 519.3245 | 45.5118 | 64.2207 | 94.0338 | 120.1171 | 149.1669 | 0.1108%
56 | 9-65 | -64.9598 | 9.0318 | 529.1863 | 44.6159 | 63.2035 | 92.7846 | 118.7731 | 148.0146 | 0.1085%
57 | 9-65 | -65.2311 | 9.0318 | 539.4894 | 43.7842 | 62.2785 | 91.6719 | 117.6204 | 146.9684 | 0.1065%
58 | 9-65.5 | -65.5024 | 9.0318 | 550.209 | 43.0898 | 61.5532 | 90.8863 | 116.8172 | 146.2085 | 0.1053%
59 | 9-66 | -65.7737 | 9.0318 | 561.3212 | 42.4589 | 60.9188 | 90.2481 | 116.1787 | 145.5606 | 0.1045%
60 | 9-66 | -66.045 | 9.0318 | 572.8032 | 41.8629 | 60.3267 | 89.6752 | 115.645 | 145.0198 | 0.1038%
61 | 9-66.5 | -66.3164 | 9.0318 | 584.6331 | 41.2963 | 59.7685 | 89.1551 | 115.2057 | 144.6304 | 0.1034%
62 | 9-66.5 | -66.5877 | 9.0318 | 596.7902 | 40.7131 | 59.1853 | 88.5723 | 114.7223 | 144.228 | 0.1029%
63 | 9-67 | -66.859 | 9.0318 | 609.255 | 40.0976 | 58.5622 | 87.9007 | 114.1378 | 143.741 | 0.1023%
64 | 9-67 | -67.1303 | 9.0318 | 622.009 | 39.4485 | 57.8972 | 87.1455 | 113.438 | 143.14 | 0.1014%
65 | 9-67.5 | -67.4016 | 9.0318 | 635.0347 | 38.788 | 57.2109 | 86.3367 | 112.6401 | 142.464 | 0.1004%
66 | 9-67.5 | -67.673 | 9.0318 | 648.3156 | 38.1743 | 56.5942 | 85.6278 | 111.9125 | 141.9007 | 0.09965%
67 | 9-68 | -67.9443 | 9.0318 | 661.8366 | 37.6308 | 56.0907 | 85.0885 | 111.3686 | 141.5233 | 0.09922%
68 | 9-68 | -68.2156 | 9.0318 | 675.583 | 37.2096 | 55.713 | 84.7624 | 111.1232 | 141.3273 | 0.09919%
69 | 9-68.5 | -68.4869 | 9.0318 | 689.5414 | 36.7956 | 55.3037 | 84.4168 | 110.8441 | 141.0367 | 0.09904%
70 | 9-69 | -68.7583 | 9.0318 | 703.6993 | 36.3294 | 54.7887 | 83.9327 | 110.3824 | 140.5373 | 0.09854%
71 | 9-69 | -69.0296 | 9.0318 | 718.0447 | 35.8641 | 54.2668 | 83.4224 | 109.9798 | 140.1021 | 0.09813%
72 | 9-69.5 | -69.3009 | 9.0318 | 732.5666 | 35.4683 | 53.8491 | 83.0661 | 109.8357 | 139.9125 | 0.09815%
73 | 9-69.5 | -69.5722 | 9.0318 | 747.2548 | 35.1673 | 53.5735 | 82.929 | 109.992 | 140.0063 | 0.09868%
74 | 9-70 | -69.8435 | 9.0318 | 762.0996 | 34.9106 | 53.3685 | 82.905 | 110.272 | 140.2707 | 0.09947%
75 | 9-70 | -70.1149 | 9.0318 | 777.0921 | 34.7403 | 53.2951 | 83.0957 | 110.811 | 140.8711 | 0.1008%
76 | 9-70.5 | -70.3862 | 9.0318 | 792.2237 | 34.6607 | 53.3575 | 83.503 | 111.63 | 141.8232 | 0.1026%
77 | 9-70.5 | -70.6575 | 9.0318 | 807.4868 | 34.571 | 53.386 | 83.8275 | 112.2759 | 142.5693 | 0.1041%
78 | 9-71 | -70.9288 | 9.0318 | 822.8738 | 34.4422 | 53.3607 | 84.0417 | 112.7376 | 143.0606 | 0.1052%
79 | 9-71 | -71.2001 | 9.0318 | 838.3781 | 34.2784 | 53.2875 | 84.1456 | 113.028 | 143.3248 | 0.1059%
80 | 9-71.5 | -71.4715 | 9.0318 | 853.9933 | 34.1288 | 53.2449 | 84.2653 | 113.3402 | 143.6819 | 0.1068%
81 | 9-71.5 | -71.7428 | 9.0318 | 869.7132 | 33.9411 | 53.2153 | 84.3441 | 113.5963 | 144.1341 | 0.1076%
82 | 9-72 | -72.0141 | 9.0318 | 885.5324 | 33.7225 | 53.1937 | 84.3827 | 113.7958 | 144.6423 | 0.1085%
83 | 9-72.5 | -72.2854 | 9.0318 | 901.4455 | 33.5302 | 53.1817 | 84.4135 | 113.9684 | 145.1329 | 0.1094%
84 | 9-72.5 | -72.5568 | 9.0318 | 917.4478 | 33.3134 | 53.0769 | 84.3098 | 113.9143 | 145.2884 | 0.1097%
85 | 9-73 | -72.8281 | 9.0318 | 933.5345 | 33.0694 | 52.8739 | 84.0578 | 113.5953 | 145.1077 | 0.1094%
86 | 9-73 | -73.0994 | 9.0318 | 949.7014 | 32.7797 | 52.5639 | 83.6212 | 112.9827 | 144.652 | 0.1086%
87 | 9-73.5 | -73.3707 | 9.0318 | 965.9444 | 32.5012 | 52.2212 | 83.1072 | 112.2476 | 144.0331 | 0.1076%
88 | 9-73.5 | -73.642 | 9.0318 | 982.2598 | 32.2635 | 51.8812 | 82.5777 | 111.4619 | 143.309 | 0.1064%
89 | 9-74 | -73.9134 | 9.0318 | 998.6439 | 32.1532 | 51.6478 | 82.2075 | 110.871 | 142.6674 | 0.1053%
90 | 9-74 | -74.1847 | 9.0318 | 1015.0935 | 32.2802 | 51.7036 | 82.3077 | 110.9245 | 142.6765 | 0.1052%
91 | 9-74.5 | -74.456 | 9.0318 | 1031.6054 | 32.6367 | 52.0359 | 82.8374 | 111.5479 | 143.3149 | 0.1061%
92 | 9-74.5 | -74.7273 | 9.0318 | 1048.1766 | 33.1726 | 52.5863 | 83.6861 | 112.631 | 144.5159 | 0.1077%
93 | 9-75 | -74.9986 | 9.0318 | 1064.8043 | 33.849 | 53.2806 | 84.7365 | 113.9866 | 145.9786 | 0.1098%
94 | 9-75.5 | -75.27 | 9.0318 | 1081.4859 | 34.6485 | 54.0788 | 85.9247 | 115.5073 | 147.5376 | 0.112%
95 | 9-75.5 | -75.5413 | 9.0318 | 1098.219 | 35.5197 | 54.9137 | 87.1284 | 117.0004 | 148.9911 | 0.1142%
96 | 9-76 | -75.8126 | 9.0318 | 1115.0012 | 36.4184 | 55.7914 | 88.3249 | 118.4409 | 150.4204 | 0.1163%
97 | 9-76 | -76.0839 | 9.0318 | 1131.8303 | 37.3431 | 56.7141 | 89.5112 | 119.8216 | 151.8969 | 0.1185%
98 | 9-76.5 | -76.3553 | 9.0318 | 1148.7042 | 38.3085 | 57.6886 | 90.6924 | 121.1698 | 153.4471 | 0.1207%
99 | 9-76.5 | -76.6266 | 9.0318 | 1165.621 | 39.3458 | 58.7431 | 91.9206 | 122.5518 | 155.0363 | 0.123%
100 | 9-77 | -76.8979 | 9.0318 | 1182.5788 | 40.4781 | 59.9077 | 93.2281 | 124.0155 | 156.6926 | 0.1255%
101 | 9-77 | -77.1692 | 9.0318 | 1199.5758 | 41.7116 | 61.1809 | 94.5994 | 125.5325 | 158.3733 | 0.1282%
102 | 9-77.5 | -77.4405 | 9.0318 | 1216.6104 | 42.9868 | 62.4878 | 95.9048 | 126.9005 | 159.9146 | 0.1307%
103 | 9-77.5 | -77.7119 | 9.0318 | 1233.6811 | 44.2328 | 63.7457 | 97.0472 | 128.0257 | 161.2036 | 0.1327%
104 | 9-78 | -77.9832 | 9.0318 | 1250.7862 | 45.4042 | 64.9066 | 97.9871 | 128.8753 | 162.1668 | 0.1342%
105 | 9-78.5 | -78.2545 | 9.0318 | 1267.9245 | 46.5562 | 66.0356 | 98.845 | 129.5519 | 162.8383 | 0.1352%
106 | 9-78.5 | -78.5258 | 9.0318 | 1285.0945 | 47.6806 | 67.1095 | 99.6183 | 130.0685 | 163.2367 | 0.1359%
107 | 9-79 | -78.7971 | 9.0318 | 1302.295 | 48.8047 | 68.1497 | 100.3716 | 130.5394 | 163.5306 | 0.1365%
108 | 9-79 | -79.0685 | 9.0318 | 1319.5247 | 49.9623 | 69.233 | 101.226 | 131.1513 | 163.9735 | 0.1374%
109 | 9-79.5 | -79.3398 | 9.0318 | 1336.7827 | 51.058 | 70.274 | 102.0809 | 131.8046 | 164.4809 | 0.1385%
110 | 9-79.5 | -79.6111 | 9.0318 | 1354.0676 | 52.0398 | 71.2256 | 102.8798 | 132.4408 | 164.9758 | 0.1397%
111 | 9-80 | -79.8824 | 9.0318 | 1371.3785 | 52.9087 | 72.0872 | 103.6258 | 133.0532 | 165.414 | 0.1409%
112 | 9-80 | -80.1537 | 9.0318 | 1388.7145 | 53.5818 | 72.773 | 104.226 | 133.5402 | 165.7218 | 0.1418%
113 | 9-80.5 | -80.4251 | 9.0318 | 1406.0745 | 53.9923 | 73.2203 | 104.6125 | 133.8224 | 165.8393 | 0.1424%
114 | 9-80.5 | -80.6964 | 9.0318 | 1423.4576 | 54.1132 | 73.4037 | 104.7552 | 133.8596 | 165.7338 | 0.1424%
115 | 9-81 | -80.9677 | 9.0318 | 1440.8631 | 53.8682 | 73.2052 | 104.514 | 133.4863 | 165.2612 | 0.1414%
116 | 9-81 | -81.239 | 9.0318 | 1458.2901 | 53.2962 | 72.6702 | 103.9353 | 132.7572 | 164.477 | 0.1397%
117 | 9-81.5 | -81.5104 | 9.0318 | 1475.7377 | 52.4717 | 71.8709 | 103.1129 | 131.7891 | 163.4782 | 0.1375%
118 | 9-82 | -81.7817 | 9.0318 | 1493.2053 | 51.4059 | 70.7949 | 101.9805 | 130.5129 | 162.1861 | 0.1347%
119 | 9-82 | -82.053 | 9.0318 | 1510.6922 | 50.1495 | 69.5022 | 100.5595 | 128.9135 | 160.5859 | 0.1312%
120 | 9-82.5 | -82.3243 | 9.0318 | 1528.1977 | 48.7454 | 68.0632 | 98.9059 | 127.0177 | 158.6996 | 0.1273%
121 | 9-82.5 | -82.5956 | 9.0318 | 1545.7211 | 47.2911 | 66.5415 | 97.1379 | 125.017 | 156.7633 | 0.1233%
122 | 9-83 | -82.867 | 9.0318 | 1563.2617 | 45.914 | 65.0491 | 95.386 | 123.053 | 154.9073 | 0.1196%
123 | 9-83 | -83.1383 | 9.0318 | 1580.8191 | 44.6806 | 63.6616 | 93.7248 | 121.2019 | 153.1692 | 0.1161%
124 | 9-83.5 | -83.4096 | 9.0318 | 1598.3927 | 43.5297 | 62.2909 | 91.9595 | 119.152 | 151.1432 | 0.1122%
125 | 9-83.5 | -83.6809 | 9.0318 | 1615.9818 | 42.5119 | 60.9667 | 90.1195 | 116.927 | 148.8382 | 0.1079%
126 | 9-84 | -83.9522 | 9.0318 | 1633.586 | 41.6654 | 59.7344 | 88.2787 | 114.611 | 146.3114 | 0.1032%
127 | 9-84 | -84.2236 | 9.0318 | 1651.2047 | 40.992 | 58.6328 | 86.5294 | 112.323 | 143.7088 | 0.09841%
128 | 9-84.5 | -84.4949 | 9.0318 | 1668.8376 | 40.5233 | 57.7601 | 85.0184 | 110.255 | 141.231 | 0.09395%
129 | 9-85 | -84.7662 | 9.0318 | 1686.4841 | 40.2678 | 57.1343 | 83.788 | 108.4813 | 138.9822 | 0.08992%
130 | 9-85 | -85.0375 | 9.0318 | 1704.1437 | 40.2252 | 56.7849 | 82.8654 | 107.0151 | 136.9898 | 0.08633%
131 | 9-85.5 | -85.3089 | 9.0318 | 1721.8161 | 40.4063 | 56.8076 | 82.3685 | 105.9842 | 135.4087 | 0.08345%
132 | 9-85.5 | -85.5802 | 9.0318 | 1739.5009 | 40.8025 | 57.1819 | 82.2421 | 105.3763 | 134.2505 | 0.08124%
133 | 9-86 | -85.8515 | 9.0318 | 1757.1977 | 41.4112 | 57.8324 | 82.4209 | 105.1395 | 133.4661 | 0.07955%
134 | 9-86 | -86.1228 | 9.0318 | 1774.906 | 42.1973 | 58.6949 | 82.8173 | 105.1259 | 132.8817 | 0.0781%
135 | 9-86.5 | -86.3941 | 9.0318 | 1792.6255 | 43.1833 | 59.7655 | 83.4135 | 105.3141 | 132.4609 | 0.0768%
136 | 9-86.5 | -86.6655 | 9.0318 | 1810.3559 | 44.2708 | 60.9055 | 84.0885 | 105.5576 | 132.0451 | 0.07544%
137 | 9-87 | -86.9368 | 9.0318 | 1828.0969 | 45.5483 | 62.242 | 85.0806 | 106.2168 | 132.0779 | 0.0748%
138 | 9-87 | -87.2081 | 9.0318 | 1845.848 | 47.0801 | 63.8537 | 86.4763 | 107.3887 | 132.6443 | 0.07507%
139 | 9-87.5 | -87.4794 | 9.0318 | 1863.6091 | 48.8088 | 65.6827 | 88.1915 | 108.9564 | 133.6667 | 0.07616%
140 | 9-88 | -87.7507 | 9.0318 | 1881.3797 | 50.6346 | 67.6123 | 90.0533 | 110.7164 | 134.9471 | 0.0778%
141 | 9-88 | -88.0221 | 9.0318 | 1899.1597 | 52.6025 | 69.6651 | 92.0623 | 112.6583 | 136.4752 | 0.07994%
142 | 9-88.5 | -88.2934 | 9.0318 | 1916.9487 | 54.7415 | 71.8674 | 94.2388 | 114.7938 | 138.2513 | 0.08266%
143 | 9-88.5 | -88.5647 | 9.0318 | 1934.7465 | 56.9705 | 74.1078 | 96.4582 | 117.0029 | 140.1545 | 0.08578%
144 | 9-89 | -88.836 | 9.0318 | 1952.5527 | 59.251 | 76.2814 | 98.6427 | 119.202 | 142.1017 | 0.08916%
145 | 9-89 | -89.1074 | 9.0318 | 1970.3673 | 61.5782 | 78.4043 | 100.8589 | 121.4415 | 144.1311 | 0.09298%
146 | 9-89.5 | -89.3787 | 9.0318 | 1988.1898 | 63.9347 | 80.5282 | 103.1502 | 123.7749 | 146.31 | 0.09753%
147 | 9-89.5 | -89.65 | 9.0318 | 2006.0201 | 66.2065 | 82.5724 | 105.3856 | 126.0552 | 148.4588 | 0.1025%
148 | 9-90 | -89.9213 | 9.0318 | 2023.858 | 68.3663 | 84.533 | 107.5772 | 128.2899 | 150.5969 | 0.1079%
149 | 9-90 | -90.1926 | 9.0318 | 2041.7032 | 70.5091 | 86.5467 | 109.8644 | 130.6516 | 152.9458 | 0.1143%
150 | 9-90.5 | -90.464 | 9.0318 | 2059.5555 | 72.5941 | 88.5815 | 112.2303 | 133.1294 | 155.5094 | 0.122%
151 | 9-90.5 | -90.7353 | 9.0318 | 2077.4147 | 74.5569 | 90.6037 | 114.6618 | 135.7213 | 158.2903 | 0.131%
152 | 9-50 | -50.0371 | 9.3032 | 830.8422 | 63.7165 | 84.5798 | 117.451 | 145.4255 | 174.5809 | 0.1751%
153 | 9-50.5 | -50.3084 | 9.3032 | 815.1449 | 63.5162 | 84.3121 | 117.1501 | 145.1884 | 174.448 | 0.1743%
154 | 9-50.5 | -50.5797 | 9.3032 | 799.5581 | 63.3226 | 84.0488 | 116.8586 | 144.9777 | 174.3523 | 0.1736%
155 | 9-51 | -50.851 | 9.3032 | 784.0883 | 63.1442 | 83.807 | 116.6006 | 144.8176 | 174.323 | 0.1731%
156 | 9-51 | -51.1224 | 9.3032 | 768.7427 | 62.9918 | 83.6064 | 116.4016 | 144.7323 | 174.3898 | 0.1728%
157 | 9-51.5 | -51.3937 | 9.3032 | 753.5287 | 62.8585 | 83.4397 | 116.2358 | 144.6728 | 174.474 | 0.1727%
158 | 9-51.5 | -51.665 | 9.3032 | 738.4547 | 62.7617 | 83.3354 | 116.1321 | 144.6641 | 174.5947 | 0.1727%
159 | 9-52 | -51.9363 | 9.3032 | 723.5293 | 62.7219 | 83.3213 | 116.1178 | 144.7342 | 174.7776 | 0.173%
160 | 9-52 | -52.2077 | 9.3032 | 708.7619 | 62.7275 | 83.37 | 116.1716 | 144.8717 | 175.0121 | 0.1735%
161 | 9-52.5 | -52.479 | 9.3032 | 694.1628 | 62.7948 | 83.4902 | 116.2942 | 145.0753 | 175.3018 | 0.1742%
162 | 9-53 | -52.7503 | 9.3032 | 679.7426 | 62.9374 | 83.688 | 116.4897 | 145.3446 | 175.6487 | 0.1752%
163 | 9-53 | -53.0216 | 9.3032 | 665.513 | 63.1003 | 83.8973 | 116.6851 | 145.5996 | 175.9675 | 0.1761%
164 | 9-53.5 | -53.2929 | 9.3032 | 651.4866 | 63.3119 | 84.1453 | 116.9112 | 145.87 | 176.2917 | 0.1771%
165 | 9-53.5 | -53.5643 | 9.3032 | 637.6769 | 63.5954 | 84.4532 | 117.1889 | 146.1735 | 176.6375 | 0.1781%
166 | 9-54 | -53.8356 | 9.3032 | 624.0981 | 63.9048 | 84.7777 | 117.4634 | 146.4426 | 176.9138 | 0.1791%
167 | 9-54 | -54.1069 | 9.3032 | 610.7656 | 64.2724 | 85.1431 | 117.7521 | 146.6922 | 177.1388 | 0.18%
168 | 9-54.5 | -54.3782 | 9.3032 | 597.6961 | 64.7093 | 85.5597 | 118.0609 | 146.9256 | 177.3145 | 0.1808%
169 | 9-54.5 | -54.6495 | 9.3032 | 584.9072 | 65.1688 | 85.9789 | 118.3287 | 147.0814 | 177.3711 | 0.1814%
170 | 9-55 | -54.9209 | 9.3032 | 572.4175 | 65.661 | 86.4108 | 118.5832 | 147.2086 | 177.3855 | 0.1819%
171 | 9-55 | -55.1922 | 9.3032 | 560.2473 | 66.1746 | 86.8378 | 118.8147 | 147.3054 | 177.3665 | 0.1822%
172 | 9-55.5 | -55.4635 | 9.3032 | 548.4178 | 66.6475 | 87.2018 | 118.9719 | 147.3253 | 177.2755 | 0.1823%
173 | 9-55.5 | -55.7348 | 9.3032 | 536.9514 | 67.0909 | 87.5293 | 119.0773 | 147.2821 | 177.1244 | 0.1822%
174 | 9-56 | -56.0061 | 9.3032 | 525.872 | 67.4938 | 87.8145 | 119.13 | 147.1745 | 176.9114 | 0.1818%
175 | 9-56.5 | -56.2775 | 9.3032 | 515.2046 | 67.8075 | 88.0172 | 119.0927 | 146.971 | 176.604 | 0.1811%
176 | 9-56.5 | -56.5488 | 9.3032 | 504.9752 | 68.0856 | 88.2027 | 119.0428 | 146.7569 | 176.2949 | 0.1804%
177 | 9-57 | -56.8201 | 9.3032 | 495.2111 | 68.3192 | 88.3629 | 118.9794 | 146.5349 | 175.9893 | 0.1796%
178 | 9-57 | -57.0914 | 9.3032 | 485.9402 | 68.4576 | 88.4451 | 118.8638 | 146.2675 | 175.6424 | 0.1786%
179 | 9-57.5 | -57.3628 | 9.3032 | 477.1913 | 68.5474 | 88.4956 | 118.756 | 146.0291 | 175.3535 | 0.1778%
180 | 9-57.5 | -57.6341 | 9.3032 | 468.9938 | 68.5607 | 88.4939 | 118.6344 | 145.7982 | 175.0983 | 0.177%
181 | 9-58 | -57.9054 | 9.3032 | 461.3768 | 68.4425 | 88.3857 | 118.4286 | 145.4914 | 174.7662 | 0.176%
182 | 9-58 | -58.1767 | 9.3032 | 454.3698 | 68.2433 | 88.1994 | 118.2009 | 145.1732 | 174.4303 | 0.1749%
183 | 9-58.5 | -58.448 | 9.3032 | 448.0012 | 67.9577 | 87.9351 | 117.9431 | 144.8354 | 174.0831 | 0.1737%
184 | 9-58.5 | -58.7194 | 9.3032 | 442.2988 | 67.5611 | 87.5843 | 117.6272 | 144.4446 | 173.6853 | 0.1724%
185 | 9-59 | -58.9907 | 9.3032 | 437.2884 | 67.1015 | 87.1789 | 117.2908 | 144.0396 | 173.268 | 0.171%
186 | 9-59.5 | -59.262 | 9.3032 | 432.9943 | 66.5622 | 86.6917 | 116.9004 | 143.5844 | 172.7997 | 0.1695%
187 | 9-59.5 | -59.5333 | 9.3032 | 429.4378 | 65.9197 | 86.0819 | 116.3947 | 143.0069 | 172.2139 | 0.1676%
188 | 9-60 | -59.8046 | 9.3032 | 426.6374 | 65.2134 | 85.3879 | 115.8092 | 142.3399 | 171.5422 | 0.1654%
189 | 9-60 | -60.076 | 9.3032 | 424.6082 | 64.4263 | 84.5908 | 115.1102 | 141.5544 | 170.7337 | 0.1628%
190 | 9-60.5 | -60.3473 | 9.3032 | 423.3611 | 63.5435 | 83.6677 | 114.2494 | 140.6045 | 169.7228 | 0.1598%
191 | 9-60.5 | -60.6186 | 9.3032 | 422.903 | 62.6023 | 82.6573 | 113.2542 | 139.5255 | 168.5585 | 0.1563%
192 | 9-61 | -60.8899 | 9.3032 | 423.2367 | 61.6579 | 81.6424 | 112.2588 | 138.4673 | 167.401 | 0.153%
193 | 9-61 | -61.1613 | 9.3032 | 424.3601 | 60.798 | 80.7474 | 111.4606 | 137.651 | 166.4889 | 0.1505%
194 | 9-61.5 | -61.4326 | 9.3032 | 426.2671 | 60.0688 | 80.0213 | 110.9318 | 137.1434 | 165.9328 | 0.1491%
195 | 9-61.5 | -61.7039 | 9.3032 | 428.9472 | 59.3934 | 79.369 | 110.4831 | 136.7385 | 165.5261 | 0.1481%
196 | 9-62 | -61.9752 | 9.3032 | 432.386 | 58.6901 | 78.6699 | 109.9274 | 136.2288 | 165.0711 | 0.1468%
197 | 9-62 | -62.2465 | 9.3032 | 436.5656 | 57.9829 | 77.9356 | 109.3015 | 135.6542 | 164.6198 | 0.1454%
198 | 9-62.5 | -62.5179 | 9.3032 | 441.4649 | 57.2676 | 77.1793 | 108.6226 | 135.0146 | 164.1269 | 0.1439%
199 | 9-63 | -62.7892 | 9.3032 | 447.0602 | 56.5564 | 76.4293 | 107.9318 | 134.355 | 163.5825 | 0.1423%
200 | 9-63 | -63.0605 | 9.3032 | 453.3259 | 55.8706 | 75.7211 | 107.2908 | 133.7514 | 163.0604 | 0.1409%
201 | 9-63.5 | -63.3318 | 9.3032 | 460.2345 | 55.2107 | 75.0502 | 106.6973 | 133.2087 | 162.5872 | 0.1397%
202 | 9-63.5 | -63.6031 | 9.3032 | 467.7575 | 54.5896 | 74.434 | 106.1772 | 132.7526 | 162.2204 | 0.1387%
203 | 9-64 | -63.8745 | 9.3032 | 475.8657 | 54.0236 | 73.8989 | 105.7788 | 132.43 | 162.028 | 0.1382%
204 | 9-64 | -64.1458 | 9.3032 | 484.5299 | 53.438 | 73.3347 | 105.315 | 132.0424 | 161.7773 | 0.1375%
205 | 9-64.5 | -64.4171 | 9.3032 | 493.7207 | 52.7345 | 72.5958 | 104.548 | 131.3014 | 161.1791 | 0.1359%
206 | 9-64.5 | -64.6884 | 9.3032 | 503.4092 | 51.8289 | 71.5724 | 103.3109 | 129.9747 | 160.0277 | 0.1329%
207 | 9-65 | -64.9598 | 9.3032 | 513.5672 | 50.8676 | 70.464 | 101.9223 | 128.4975 | 158.6797 | 0.1296%
208 | 9-65 | -65.2311 | 9.3032 | 524.1676 | 49.9856 | 69.4731 | 100.7239 | 127.2529 | 157.4941 | 0.1269%
209 | 9-65.5 | -65.5024 | 9.3032 | 535.1839 | 49.2652 | 68.7243 | 99.9283 | 126.4204 | 156.6803 | 0.1252%
210 | 9-66 | -65.7737 | 9.3032 | 546.5911 | 48.612 | 68.0751 | 99.2958 | 125.7662 | 155.9972 | 0.1239%
211 | 9-66 | -66.045 | 9.3032 | 558.3651 | 47.9906 | 67.4644 | 98.7212 | 125.2113 | 155.4125 | 0.1229%
212 | 9-66.5 | -66.3164 | 9.3032 | 570.4832 | 47.3955 | 66.8837 | 98.1905 | 124.7432 | 154.9668 | 0.1222%
213 | 9-66.5 | -66.5877 | 9.3032 | 582.924 | 46.7672 | 66.2511 | 97.5484 | 124.1966 | 154.4641 | 0.1213%
214 | 9-67 | -66.859 | 9.3032 | 595.6672 | 46.0875 | 65.5484 | 96.7624 | 123.5108 | 153.8305 | 0.12%
215 | 9-67 | -67.1303 | 9.3032 | 608.6938 | 45.3562 | 64.7754 | 95.8418 | 122.6742 | 153.041 | 0.1185%
216 | 9-67.5 | -67.4016 | 9.3032 | 621.986 | 44.6034 | 63.965 | 94.8377 | 121.7183 | 152.1508 | 0.1167%
217 | 9-67.5 | -67.673 | 9.3032 | 635.5271 | 43.9032 | 63.2339 | 93.949 | 120.8364 | 151.3999 | 0.1153%
218 | 9-68 | -67.9443 | 9.3032 | 649.3016 | 43.2868 | 62.638 | 93.273 | 120.1617 | 150.8896 | 0.1143%
219 | 9-68 | -68.2156 | 9.3032 | 663.2949 | 42.823 | 62.2175 | 92.9 | 119.8791 | 150.665 | 0.1141%
220 | 9-68.5 | -68.4869 | 9.3032 | 677.4933 | 42.3713 | 61.7727 | 92.5157 | 119.5815 | 150.3536 | 0.1138%
221 | 9-69 | -68.7583 | 9.3032 | 691.8843 | 41.8594 | 61.2084 | 91.9599 | 119.0724 | 149.7957 | 0.113%
222 | 9-69 | -69.0296 | 9.3032 | 706.4561 | 41.3349 | 60.6132 | 91.3352 | 118.5892 | 149.2585 | 0.1122%
223 | 9-69.5 | -69.3009 | 9.3032 | 721.1978 | 40.8866 | 60.1315 | 90.8817 | 118.3798 | 148.9901 | 0.1119%
224 | 9-69.5 | -69.5722 | 9.3032 | 736.099 | 40.5469 | 59.8135 | 90.6862 | 118.5021 | 149.0501 | 0.1123%
225 | 9-70 | -69.8435 | 9.3032 | 751.1502 | 40.246 | 59.557 | 90.5862 | 118.7379 | 149.2717 | 0.113%
226 | 9-70 | -70.1149 | 9.3032 | 766.3427 | 40.04 | 59.4453 | 90.724 | 119.249 | 149.8517 | 0.1143%
227 | 9-70.5 | -70.3862 | 9.3032 | 781.6682 | 39.9365 | 59.4882 | 91.1104 | 120.0629 | 150.8127 | 0.1162%
228 | 9-70.5 | -70.6575 | 9.3032 | 797.119 | 39.8393 | 59.5226 | 91.4571 | 120.7354 | 151.6058 | 0.1179%
229 | 9-71 | -70.9288 | 9.3032 | 812.6878 | 39.7117 | 59.516 | 91.7154 | 121.2403 | 152.1647 | 0.1191%
230 | 9-71 | -71.2001 | 9.3032 | 828.3682 | 39.5563 | 59.4721 | 91.8808 | 121.6017 | 152.5119 | 0.12%
231 | 9-71.5 | -71.4715 | 9.3032 | 844.1537 | 39.4221 | 59.4692 | 92.0787 | 122.0116 | 152.9623 | 0.1211%
232 | 9-71.5 | -71.7428 | 9.3032 | 860.0387 | 39.2397 | 59.4611 | 92.2031 | 122.3212 | 153.4679 | 0.1221%
233 | 9-72 | -72.0141 | 9.3032 | 876.0176 | 39.0151 | 59.4419 | 92.2545 | 122.5335 | 153.9915 | 0.123%
234 | 9-72.5 | -72.2854 | 9.3032 | 892.0855 | 38.812 | 59.4285 | 92.2971 | 122.7208 | 154.502 | 0.1239%
235 | 9-72.5 | -72.5568 | 9.3032 | 908.2376 | 38.5846 | 59.3243 | 92.2116 | 122.6899 | 154.6871 | 0.1242%
236 | 9-73 | -72.8281 | 9.3032 | 924.4694 | 38.3278 | 59.1186 | 91.973 | 122.3935 | 154.5316 | 0.1239%
237 | 9-73 | -73.0994 | 9.3032 | 940.7768 | 38.0128 | 58.7803 | 91.4991 | 121.7548 | 154.0395 | 0.1229%
238 | 9-73.5 | -73.3707 | 9.3032 | 957.1559 | 37.7162 | 58.4148 | 90.9528 | 120.9908 | 153.3748 | 0.1216%
239 | 9-73.5 | -73.642 | 9.3032 | 973.6032 | 37.4713 | 58.0638 | 90.4063 | 120.1829 | 152.6082 | 0.1202%
240 | 9-74 | -73.9134 | 9.3032 | 990.1151 | 37.3735 | 57.848 | 90.0655 | 119.603 | 151.9664 | 0.119%
241 | 9-74 | -74.1847 | 9.3032 | 1006.6885 | 37.5297 | 57.9434 | 90.2276 | 119.6909 | 152.0072 | 0.119%
242 | 9-74.5 | -74.456 | 9.3032 | 1023.3204 | 37.9287 | 58.3315 | 90.8401 | 120.3636 | 152.6978 | 0.1202%
243 | 9-74.5 | -74.7273 | 9.3032 | 1040.0079 | 38.5095 | 58.9379 | 91.7677 | 121.4921 | 153.9452 | 0.1222%
244 | 9-75 | -74.9986 | 9.3032 | 1056.7485 | 39.2339 | 59.689 | 92.894 | 122.8908 | 155.4537 | 0.1248%
245 | 9-75.5 | -75.27 | 9.3032 | 1073.5395 | 40.0835 | 60.544 | 94.1561 | 124.4533 | 157.0585 | 0.1276%
246 | 9-75.5 | -75.5413 | 9.3032 | 1090.3787 | 41.0046 | 61.4325 | 95.4266 | 125.9825 | 158.5512 | 0.1303%
247 | 9-76 | -75.8126 | 9.3032 | 1107.2638 | 41.9471 | 62.3469 | 96.6499 | 127.4248 | 159.9705 | 0.1329%
248 | 9-76 | -76.0839 | 9.3032 | 1124.1928 | 42.9061 | 63.2848 | 97.8142 | 128.7626 | 161.375 | 0.1354%
249 | 9-76.5 | -76.3553 | 9.3032 | 1141.1637 | 43.8938 | 64.2523 | 98.9238 | 130.0209 | 162.7866 | 0.1379%
250 | 9-76.5 | -76.6266 | 9.3032 | 1158.1746 | 44.9535 | 65.3008 | 100.0757 | 131.3135 | 164.2268 | 0.1405%
251 | 9-77 | -76.8979 | 9.3032 | 1175.2237 | 46.106 | 66.4595 | 101.3076 | 132.6873 | 165.7343 | 0.1434%
252 | 9-77 | -77.1692 | 9.3032 | 1192.3095 | 47.3511 | 67.7196 | 102.5998 | 134.1103 | 167.2648 | 0.1464%
253 | 9-77.5 | -77.4405 | 9.3032 | 1209.4303 | 48.6216 | 68.9903 | 103.7906 | 135.3531 | 168.6153 | 0.1492%
254 | 9-77.5 | -77.7119 | 9.3032 | 1226.5846 | 49.8431 | 70.1889 | 104.7868 | 136.3272 | 169.6816 | 0.1513%
255 | 9-78 | -77.9832 | 9.3032 | 1243.7711 | 50.9726 | 71.2747 | 105.564 | 137.0134 | 170.41 | 0.1528%
256 | 9-78.5 | -78.2545 | 9.3032 | 1260.9884 | 52.0789 | 72.3292 | 106.2679 | 137.5335 | 170.8623 | 0.1539%
257 | 9-78.5 | -78.5258 | 9.3032 | 1278.2353 | 53.1588 | 73.3356 | 106.9065 | 137.9164 | 171.0789 | 0.1547%
258 | 9-79 | -78.7971 | 9.3032 | 1295.5105 | 54.2423 | 74.3219 | 107.5529 | 138.2883 | 171.2451 | 0.1553%
259 | 9-79 | -79.0685 | 9.3032 | 1312.8129 | 55.3655 | 75.3663 | 108.3285 | 138.836 | 171.6146 | 0.1566%
260 | 9-79.5 | -79.3398 | 9.3032 | 1330.1415 | 56.4259 | 76.3694 | 109.1116 | 139.432 | 172.0612 | 0.158%
261 | 9-79.5 | -79.6111 | 9.3032 | 1347.4952 | 57.3715 | 77.2809 | 109.8413 | 140.0085 | 172.4944 | 0.1595%
262 | 9-80 | -79.8824 | 9.3032 | 1364.873 | 58.2088 | 78.1074 | 110.5338 | 140.5711 | 172.8889 | 0.161%
263 | 9-80 | -80.1537 | 9.3032 | 1382.274 | 58.8552 | 78.7666 | 111.105 | 141.0332 | 173.1919 | 0.1622%
264 | 9-80.5 | -80.4251 | 9.3032 | 1399.6973 | 59.2484 | 79.1986 | 111.4853 | 141.3179 | 173.3438 | 0.163%
265 | 9-80.5 | -80.6964 | 9.3032 | 1417.1421 | 59.363 | 79.3789 | 111.6386 | 141.3795 | 173.3007 | 0.1632%
266 | 9-81 | -80.9677 | 9.3032 | 1434.6076 | 59.119 | 79.1861 | 111.4212 | 141.0506 | 172.9149 | 0.1622%
267 | 9-81 | -81.239 | 9.3032 | 1452.093 | 58.5565 | 78.6646 | 110.8746 | 140.3799 | 172.2315 | 0.1604%
268 | 9-81.5 | -81.5104 | 9.3032 | 1469.5975 | 57.7535 | 77.8878 | 110.0914 | 139.4792 | 171.3395 | 0.1579%
269 | 9-82 | -81.7817 | 9.3032 | 1487.1206 | 56.7043 | 76.8222 | 108.9751 | 138.2477 | 170.1203 | 0.1546%
270 | 9-82 | -82.053 | 9.3032 | 1504.6614 | 55.4549 | 75.5205 | 107.5311 | 136.6467 | 168.527 | 0.1503%
271 | 9-82.5 | -82.3243 | 9.3032 | 1522.2195 | 54.0514 | 74.0523 | 105.8128 | 134.6846 | 166.567 | 0.1453%
272 | 9-82.5 | -82.5956 | 9.3032 | 1539.7941 | 52.5902 | 72.4906 | 103.9609 | 132.5792 | 164.511 | 0.1402%
273 | 9-83 | -82.867 | 9.3032 | 1557.3847 | 51.2034 | 70.9578 | 102.1292 | 130.5086 | 162.5382 | 0.1354%
274 | 9-83 | -83.1383 | 9.3032 | 1574.9908 | 49.9594 | 69.5318 | 100.4005 | 128.5671 | 160.7126 | 0.1311%
275 | 9-83.5 | -83.4096 | 9.3032 | 1592.6118 | 48.7896 | 68.1145 | 98.5669 | 126.4305 | 158.6165 | 0.1263%
276 | 9-83.5 | -83.6809 | 9.3032 | 1610.2471 | 47.7293 | 66.7216 | 96.6423 | 124.1076 | 156.2377 | 0.1211%
277 | 9-84 | -83.9522 | 9.3032 | 1627.8964 | 46.8075 | 65.3972 | 94.695 | 121.6733 | 153.6201 | 0.1155%
278 | 9-84 | -84.2236 | 9.3032 | 1645.5591 | 46.036 | 64.1921 | 92.8324 | 119.2661 | 150.9279 | 0.11%
279 | 9-84.5 | -84.4949 | 9.3032 | 1663.2349 | 45.4586 | 63.2066 | 91.202 | 117.076 | 148.3621 | 0.1049%
280 | 9-85 | -84.7662 | 9.3032 | 1680.9232 | 45.0812 | 62.4559 | 89.8435 | 115.176 | 146.0267 | 0.1004%
281 | 9-85 | -85.0375 | 9.3032 | 1698.6236 | 44.8949 | 61.9537 | 88.7522 | 113.5432 | 143.9154 | 0.09629%
282 | 9-85.5 | -85.3089 | 9.3032 | 1716.3358 | 44.9237 | 61.8098 | 88.0651 | 112.3329 | 142.2189 | 0.09304%
283 | 9-85.5 | -85.5802 | 9.3032 | 1734.0594 | 45.1639 | 62.0152 | 87.761 | 111.567 | 140.9823 | 0.09063%
284 | 9-86 | -85.8515 | 9.3032 | 1751.7941 | 45.6109 | 62.4923 | 87.7769 | 111.2104 | 140.1639 | 0.08894%
285 | 9-86 | -86.1228 | 9.3032 | 1769.5393 | 46.2309 | 63.1645 | 88.0072 | 111.0982 | 139.5608 | 0.08758%
286 | 9-86.5 | -86.3941 | 9.3032 | 1787.2949 | 47.0492 | 64.0243 | 88.44 | 111.2105 | 139.1336 | 0.08646%
287 | 9-86.5 | -86.6655 | 9.3032 | 1805.0605 | 47.9794 | 64.9651 | 88.9742 | 111.4133 | 138.7307 | 0.08535%
288 | 9-87 | -86.9368 | 9.3032 | 1822.8358 | 49.1218 | 66.1273 | 89.8666 | 112.0789 | 138.8085 | 0.08513%
289 | 9-87 | -87.2081 | 9.3032 | 1840.6205 | 50.5582 | 67.6012 | 91.2155 | 113.2938 | 139.4521 | 0.08599%
290 | 9-87.5 | -87.4794 | 9.3032 | 1858.4143 | 52.2414 | 69.3409 | 92.9351 | 114.9382 | 140.5786 | 0.08781%
291 | 9-88 | -87.7507 | 9.3032 | 1876.2169 | 54.0638 | 71.2243 | 94.8299 | 116.7827 | 141.9636 | 0.09023%
292 | 9-88 | -88.0221 | 9.3032 | 1894.0281 | 56.0595 | 73.2713 | 96.9039 | 118.8217 | 143.6026 | 0.09327%
293 | 9-88.5 | -88.2934 | 9.3032 | 1911.8475 | 58.2582 | 75.5067 | 99.1834 | 121.0716 | 145.5027 | 0.09704%
294 | 9-88.5 | -88.5647 | 9.3032 | 1929.675 | 60.5805 | 77.8296 | 101.5711 | 123.4475 | 147.5744 | 0.1015%
295 | 9-89 | -88.836 | 9.3032 | 1947.5103 | 62.9883 | 80.138 | 103.9946 | 125.8706 | 149.7393 | 0.1064%
296 | 9-89 | -89.1074 | 9.3032 | 1965.3532 | 65.4715 | 82.4336 | 106.4852 | 128.3667 | 152.0155 | 0.112%
297 | 9-89.5 | -89.3787 | 9.3032 | 1983.2034 | 68.0082 | 84.7678 | 109.0786 | 130.9793 | 154.463 | 0.1187%
298 | 9-89.5 | -89.65 | 9.3032 | 2001.0607 | 70.4593 | 87.0399 | 111.6163 | 133.5296 | 156.8729 | 0.1259%
299 | 9-90 | -89.9213 | 9.3032 | 2018.925 | 72.7922 | 89.2555 | 114.1046 | 136.0166 | 159.2611 | 0.1337%
300 | 9-90 | -90.1926 | 9.3032 | 2036.7959 | 75.0846 | 91.5311 | 116.6714 | 138.6037 | 161.8454 | 0.1429%
301 | 9-90.5 | -90.464 | 9.3032 | 2054.6734 | 77.3014 | 93.8308 | 119.2894 | 141.2729 | 164.6179 | 0.1534%
302 | 9-90.5 | -90.7353 | 9.3032 | 2072.5572 | 79.3847 | 96.1099 | 121.9299 | 144.0169 | 167.5582 | 0.1653%
303 | 10-50 | -50.0371 | 9.5745 | 821.1615 | 68.7962 | 90.5043 | 125.0787 | 153.5896 | 183.198 | 0.206%
304 | 10-50.5 | -50.3084 | 9.5745 | 805.2909 | 68.5918 | 90.2506 | 124.7921 | 153.3688 | 183.0816 | 0.2051%
305 | 10-50.5 | -50.5797 | 9.5745 | 789.5248 | 68.3898 | 89.9932 | 124.5065 | 153.1621 | 182.9851 | 0.2043%
306 | 10-51 | -50.851 | 9.5745 | 773.8696 | 68.1985 | 89.7492 | 124.246 | 152.9936 | 182.9374 | 0.2035%
307 | 10-51 | -51.1224 | 9.5745 | 758.3322 | 68.0305 | 89.5384 | 124.036 | 152.8883 | 182.97 | 0.2031%
308 | 10-51.5 | -51.3937 | 9.5745 | 742.92 | 67.8799 | 89.3546 | 123.8522 | 152.801 | 183.0119 | 0.2027%
309 | 10-51.5 | -51.665 | 9.5745 | 727.641 | 67.7658 | 89.2252 | 123.7227 | 152.7576 | 183.0852 | 0.2025%
310 | 10-52 | -51.9363 | 9.5745 | 712.5037 | 67.7083 | 89.1725 | 123.6725 | 152.7845 | 183.2155 | 0.2027%
311 | 10-52 | -52.2077 | 9.5745 | 697.5175 | 67.6938 | 89.168 | 123.6806 | 152.8693 | 183.3889 | 0.203%
312 | 10-52.5 | -52.479 | 9.5745 | 682.6922 | 67.7375 | 89.2184 | 123.7496 | 153.0138 | 183.6138 | 0.2035%
313 | 10-53 | -52.7503 | 9.5745 | 668.0386 | 67.8518 | 89.3306 | 123.8845 | 153.2191 | 183.8947 | 0.2043%
314 | 10-53 | -53.0216 | 9.5745 | 653.5683 | 67.9833 | 89.4511 | 124.0157 | 153.4059 | 184.1427 | 0.2051%
315 | 10-53.5 | -53.2929 | 9.5745 | 639.2937 | 68.1603 | 89.6082 | 124.1748 | 153.6066 | 184.3966 | 0.2059%
316 | 10-53.5 | -53.5643 | 9.5745 | 625.2282 | 68.4069 | 89.8235 | 124.3826 | 153.8392 | 184.6738 | 0.2069%
317 | 10-54 | -53.8356 | 9.5745 | 611.3863 | 68.6811 | 90.0581 | 124.5912 | 154.046 | 184.8968 | 0.2078%
318 | 10-54 | -54.1069 | 9.5745 | 597.7836 | 69.0182 | 90.3388 | 124.8191 | 154.2452 | 185.0893 | 0.2087%
319 | 10-54.5 | -54.3782 | 9.5745 | 584.4368 | 69.4312 | 90.6774 | 125.0719 | 154.4397 | 185.2535 | 0.2097%
320 | 10-54.5 | -54.6495 | 9.5745 | 571.3637 | 69.8722 | 91.022 | 125.2856 | 154.5602 | 185.3039 | 0.2103%
321 | 10-55 | -54.9209 | 9.5745 | 558.5837 | 70.3516 | 91.3833 | 125.4866 | 154.6516 | 185.3104 | 0.2109%
322 | 10-55 | -55.1922 | 9.5745 | 546.1173 | 70.8591 | 91.7482 | 125.668 | 154.7143 | 185.283 | 0.2114%
323 | 10-55.5 | -55.4635 | 9.5745 | 533.9865 | 71.3344 | 92.0659 | 125.7843 | 154.7069 | 185.1858 | 0.2116%
324 | 10-55.5 | -55.7348 | 9.5745 | 522.2147 | 71.7914 | 92.3657 | 125.8584 | 154.6449 | 185.0345 | 0.2116%
325 | 10-56 | -56.0061 | 9.5745 | 510.8268 | 72.2208 | 92.6461 | 125.8908 | 154.5279 | 184.8282 | 0.2114%
326 | 10-56.5 | -56.2775 | 9.5745 | 499.8489 | 72.5745 | 92.8662 | 125.8445 | 154.3226 | 184.5296 | 0.2108%
327 | 10-56.5 | -56.5488 | 9.5745 | 489.3088 | 72.9048 | 93.0788 | 125.7934 | 154.1137 | 184.2343 | 0.2102%
328 | 10-57 | -56.8201 | 9.5745 | 479.2352 | 73.2032 | 93.2785 | 125.739 | 153.9066 | 183.9513 | 0.2096%
329 | 10-57 | -57.0914 | 9.5745 | 469.6583 | 73.4187 | 93.4269 | 125.6506 | 153.6746 | 183.6499 | 0.2089%
330 | 10-57.5 | -57.3628 | 9.5745 | 460.609 | 73.5947 | 93.5652 | 125.5826 | 153.483 | 183.416 | 0.2083%
331 | 10-57.5 | -57.6341 | 9.5745 | 452.119 | 73.7022 | 93.6716 | 125.5148 | 153.3115 | 183.2258 | 0.2078%
332 | 10-58 | -57.9054 | 9.5745 | 444.2205 | 73.6829 | 93.6893 | 125.3769 | 153.0768 | 182.9692 | 0.207%
333 | 10-58 | -58.1767 | 9.5745 | 436.9454 | 73.5891 | 93.65 | 125.236 | 152.8531 | 182.735 | 0.2061%
334 | 10-58.5 | -58.448 | 9.5745 | 430.3254 | 73.4129 | 93.5489 | 125.082 | 152.6298 | 182.5126 | 0.2053%
335 | 10-58.5 | -58.7194 | 9.5745 | 424.3911 | 73.124 | 93.3679 | 124.8798 | 152.3651 | 182.2535 | 0.2042%
336 | 10-59 | -58.9907 | 9.5745 | 419.1718 | 72.7706 | 93.1383 | 124.6651 | 152.0968 | 181.9885 | 0.2031%
337 | 10-59.5 | -59.262 | 9.5745 | 414.6944 | 72.3349 | 92.8314 | 124.4038 | 151.7887 | 181.6866 | 0.2019%
338 | 10-59.5 | -59.5333 | 9.5745 | 410.9831 | 71.7909 | 92.4039 | 124.0335 | 151.3689 | 181.2834 | 0.2001%
339 | 10-60 | -59.8046 | 9.5745 | 408.0589 | 71.1793 | 91.8955 | 123.5906 | 150.8723 | 180.8148 | 0.1981%
340 | 10-60 | -60.076 | 9.5745 | 405.9388 | 70.4822 | 91.2821 | 123.0364 | 150.2636 | 180.2213 | 0.1956%
341 | 10-60.5 | -60.3473 | 9.5745 | 404.6354 | 69.6782 | 90.5303 | 122.3134 | 149.4842 | 179.4207 | 0.1924%
342 | 10-60.5 | -60.6186 | 9.5745 | 404.1567 | 68.8045 | 89.665 | 121.4425 | 148.5601 | 178.4483 | 0.1887%
343 | 10-61 | -60.8899 | 9.5745 | 404.5054 | 67.9178 | 88.7738 | 120.5616 | 147.6455 | 177.4707 | 0.1851%
344 | 10-61 | -61.1613 | 9.5745 | 405.6796 | 67.1093 | 87.9875 | 119.879 | 146.9689 | 176.7357 | 0.1825%
345 | 10-61.5 | -61.4326 | 9.5745 | 407.6721 | 66.4283 | 87.3587 | 119.4676 | 146.5987 | 176.3547 | 0.181%
346 | 10-61.5 | -61.7039 | 9.5745 | 410.471 | 65.7939 | 86.7883 | 119.1292 | 146.3196 | 176.1091 | 0.18%
347 | 10-62 | -61.9752 | 9.5745 | 414.0598 | 65.1222 | 86.1534 | 118.6696 | 145.9174 | 175.7917 | 0.1786%
348 | 10-62 | -62.2465 | 9.5745 | 418.4184 | 64.4421 | 85.4748 | 118.1324 | 145.4399 | 175.4633 | 0.177%
349 | 10-62.5 | -62.5179 | 9.5745 | 423.5228 | 63.7481 | 84.7644 | 117.5344 | 144.8858 | 175.0772 | 0.1752%
350 | 10-63 | -62.7892 | 9.5745 | 429.3466 | 63.0524 | 84.0497 | 116.9167 | 144.2986 | 174.6219 | 0.1733%
351 | 10-63 | -63.0605 | 9.5745 | 435.8608 | 62.3787 | 83.3686 | 116.3413 | 143.7544 | 174.1696 | 0.1716%
352 | 10-63.5 | -63.3318 | 9.5745 | 443.035 | 61.7269 | 82.716 | 115.8053 | 143.2556 | 173.743 | 0.1701%
353 | 10-63.5 | -63.6031 | 9.5745 | 450.8377 | 61.1101 | 82.1134 | 115.3386 | 142.8334 | 173.4061 | 0.1688%
354 | 10-64 | -63.8745 | 9.5745 | 459.2369 | 60.5504 | 81.5954 | 114.9976 | 142.5456 | 173.2423 | 0.168%
355 | 10-64 | -64.1458 | 9.5745 | 468.2004 | 59.967 | 81.0417 | 114.5814 | 142.1801 | 173.0009 | 0.167%
356 | 10-64.5 | -64.4171 | 9.5745 | 477.6964 | 59.256 | 80.2982 | 113.8399 | 141.4351 | 172.3757 | 0.1649%
357 | 10-64.5 | -64.6884 | 9.5745 | 487.694 | 58.3308 | 79.2506 | 112.5955 | 140.0715 | 171.1524 | 0.161%
358 | 10-65 | -64.9598 | 9.5745 | 498.1627 | 57.3461 | 78.1125 | 111.1912 | 138.5481 | 169.7202 | 0.1566%
359 | 10-65 | -65.2311 | 9.5745 | 509.0736 | 56.4441 | 77.098 | 109.9879 | 137.2675 | 168.4652 | 0.153%
360 | 10-65.5 | -65.5024 | 9.5745 | 520.3989 | 55.7111 | 76.3379 | 109.2067 | 136.4188 | 167.61 | 0.1508%
361 | 10-66 | -65.7737 | 9.5745 | 532.112 | 55.0447 | 75.6769 | 108.5904 | 135.7469 | 166.883 | 0.1491%
362 | 10-66 | -66.045 | 9.5745 | 544.188 | 54.4073 | 75.0507 | 108.0279 | 135.1671 | 166.2429 | 0.1476%
363 | 10-66.5 | -66.3164 | 9.5745 | 556.6031 | 53.7941 | 74.4518 | 107.5053 | 134.6689 | 165.7329 | 0.1464%
364 | 10-66.5 | -66.5877 | 9.5745 | 569.3353 | 53.1275 | 73.7694 | 106.8383 | 134.0538 | 165.1176 | 0.1449%
365 | 10-67 | -66.859 | 9.5745 | 582.3636 | 52.3859 | 72.9798 | 105.962 | 133.2565 | 164.319 | 0.1429%
366 | 10-67 | -67.1303 | 9.5745 | 595.6686 | 51.5703 | 72.085 | 104.8897 | 132.2679 | 163.3167 | 0.1404%
367 | 10-67.5 | -67.4016 | 9.5745 | 609.2323 | 50.7257 | 71.1416 | 103.7152 | 131.1489 | 162.2022 | 0.1377%
368 | 10-67.5 | -67.673 | 9.5745 | 623.0376 | 49.9351 | 70.2803 | 102.6582 | 130.112 | 161.2402 | 0.1353%
369 | 10-68 | -67.9443 | 9.5745 | 637.0689 | 49.2329 | 69.5621 | 101.8238 | 129.2977 | 160.5422 | 0.1336%
370 | 10-68 | -68.2156 | 9.5745 | 651.3116 | 48.7059 | 69.0558 | 101.3542 | 128.9286 | 160.2014 | 0.133%
371 | 10-68.5 | -68.4869 | 9.5745 | 665.752 | 48.2074 | 68.5513 | 100.9192 | 128.5777 | 159.8179 | 0.1323%
372 | 10-69 | -68.7583 | 9.5745 | 680.3776 | 47.6614 | 67.9479 | 100.3504 | 128.0374 | 159.2166 | 0.1311%
373 | 10-69 | -69.0296 | 9.5745 | 695.1766 | 47.1001 | 67.3094 | 99.71 | 127.5164 | 158.6274 | 0.13%
374 | 10-69.5 | -69.3009 | 9.5745 | 710.1383 | 46.6193 | 66.7914 | 99.2506 | 127.2823 | 158.3274 | 0.1295%
375 | 10-69.5 | -69.5722 | 9.5745 | 725.2524 | 46.2538 | 66.4483 | 99.0625 | 127.3996 | 158.3864 | 0.1298%
376 | 10-70 | -69.8435 | 9.5745 | 740.5097 | 45.9102 | 66.1373 | 98.9175 | 127.5926 | 158.5601 | 0.1303%
377 | 10-70 | -70.1149 | 9.5745 | 755.9016 | 45.6623 | 65.9713 | 98.9797 | 128.0552 | 159.0838 | 0.1315%
378 | 10-70.5 | -70.3862 | 9.5745 | 771.4198 | 45.523 | 65.9684 | 99.2985 | 128.8245 | 159.9917 | 0.1335%
379 | 10-70.5 | -70.6575 | 9.5745 | 787.0569 | 45.4128 | 65.9935 | 99.6455 | 129.5032 | 160.7994 | 0.1352%
380 | 10-71 | -70.9288 | 9.5745 | 802.806 | 45.2797 | 65.9897 | 99.9286 | 130.0344 | 161.4018 | 0.1366%
381 | 10-71 | -71.2001 | 9.5745 | 818.6606 | 45.1245 | 65.9578 | 100.1384 | 130.4376 | 161.8149 | 0.1377%
382 | 10-71.5 | -71.4715 | 9.5745 | 834.6146 | 45.0055 | 65.9908 | 100.4226 | 130.9179 | 162.3658 | 0.139%
383 | 10-71.5 | -71.7428 | 9.5745 | 850.6625 | 44.835 | 66.0139 | 100.625 | 131.289 | 162.9585 | 0.1402%
384 | 10-72 | -72.0141 | 9.5745 | 866.799 | 44.6152 | 66.0148 | 100.7343 | 131.5465 | 163.5474 | 0.1413%
385 | 10-72.5 | -72.2854 | 9.5745 | 883.0192 | 44.3981 | 65.993 | 100.7864 | 131.7467 | 164.0823 | 0.1422%
386 | 10-72.5 | -72.5568 | 9.5745 | 899.3186 | 44.1536 | 65.8763 | 100.7029 | 131.7248 | 164.2878 | 0.1425%
387 | 10-73 | -72.8281 | 9.5745 | 915.6929 | 43.8765 | 65.653 | 100.4584 | 131.4298 | 164.1429 | 0.1421%
388 | 10-73 | -73.0994 | 9.5745 | 932.1382 | 43.5345 | 65.2833 | 99.95 | 130.7654 | 163.6221 | 0.1409%
389 | 10-73.5 | -73.3707 | 9.5745 | 948.6508 | 43.2287 | 64.9144 | 99.4063 | 130.0055 | 162.9652 | 0.1394%
390 | 10-73.5 | -73.642 | 9.5745 | 965.2272 | 42.9948 | 64.5899 | 98.9125 | 129.2356 | 162.2494 | 0.1378%
391 | 10-74 | -73.9134 | 9.5745 | 981.8641 | 42.9303 | 64.434 | 98.6831 | 128.7368 | 161.7152 | 0.1368%
392 | 10-74 | -74.1847 | 9.5745 | 998.5586 | 43.1263 | 64.5944 | 98.952 | 128.9001 | 161.8532 | 0.1371%
393 | 10-74.5 | -74.456 | 9.5745 | 1015.3077 | 43.5693 | 65.0488 | 99.6595 | 129.6366 | 162.6216 | 0.1386%
394 | 10-74.5 | -74.7273 | 9.5745 | 1032.1087 | 44.1905 | 65.7122 | 100.6514 | 130.8023 | 163.9055 | 0.1412%
395 | 10-75 | -74.9986 | 9.5745 | 1048.9592 | 44.9431 | 66.4968 | 101.7888 | 132.1986 | 165.3966 | 0.1442%
396 | 10-75.5 | -75.27 | 9.5745 | 1065.8568 | 45.8092 | 67.3631 | 103.0141 | 133.725 | 166.9401 | 0.1475%
397 | 10-75.5 | -75.5413 | 9.5745 | 1082.7993 | 46.7372 | 68.2453 | 104.215 | 135.1986 | 168.3493 | 0.1506%
398 | 10-76 | -75.8126 | 9.5745 | 1099.7846 | 47.6884 | 69.1527 | 105.3615 | 136.5812 | 169.6812 | 0.1535%
399 | 10-76 | -76.0839 | 9.5745 | 1116.8106 | 48.6528 | 70.0757 | 106.4282 | 137.8423 | 170.9728 | 0.1564%
400 | 10-76.5 | -76.3553 | 9.5745 | 1133.8757 | 49.6359 | 71.0132 | 107.4122 | 138.9922 | 172.2226 | 0.1591%
401 | 10-76.5 | -76.6266 | 9.5745 | 1150.9779 | 50.6851 | 72.0257 | 108.4378 | 140.1633 | 173.4801 | 0.1619%
402 | 10-77 | -76.8979 | 9.5745 | 1168.1156 | 51.8183 | 73.1409 | 109.5432 | 141.4074 | 174.795 | 0.1651%
403 | 10-77 | -77.1692 | 9.5745 | 1185.2874 | 53.0324 | 74.3468 | 110.7047 | 142.6951 | 176.1303 | 0.1684%
404 | 10-77.5 | -77.4405 | 9.5745 | 1202.4917 | 54.2619 | 75.5479 | 111.747 | 143.7851 | 177.2655 | 0.1714%
405 | 10-77.5 | -77.7119 | 9.5745 | 1219.7271 | 55.4317 | 76.6621 | 112.5811 | 144.5932 | 178.1021 | 0.1737%
406 | 10-78 | -77.9832 | 9.5745 | 1236.9923 | 56.5014 | 77.6544 | 113.1938 | 145.1107 | 178.6018 | 0.1752%
407 | 10-78.5 | -78.2545 | 9.5745 | 1254.286 | 57.5481 | 78.6161 | 113.748 | 145.4731 | 178.8479 | 0.1763%
408 | 10-78.5 | -78.5258 | 9.5745 | 1271.6071 | 58.5717 | 79.539 | 114.2643 | 145.7278 | 178.9074 | 0.1771%
409 | 10-79 | -78.7971 | 9.5745 | 1288.9545 | 59.6046 | 80.4569 | 114.8197 | 146.0099 | 178.9756 | 0.178%
410 | 10-79 | -79.0685 | 9.5745 | 1306.327 | 60.6836 | 81.446 | 115.5251 | 146.4955 | 179.2881 | 0.1796%
411 | 10-79.5 | -79.3398 | 9.5745 | 1323.7237 | 61.6997 | 82.3952 | 116.2413 | 147.0333 | 179.6828 | 0.1814%
412 | 10-79.5 | -79.6111 | 9.5745 | 1341.1436 | 62.6029 | 83.2542 | 116.9111 | 147.5542 | 180.068 | 0.1832%
413 | 10-80 | -79.8824 | 9.5745 | 1358.5859 | 63.4085 | 84.0404 | 117.5652 | 148.0836 | 180.4496 | 0.1851%
414 | 10-80 | -80.1537 | 9.5745 | 1376.0495 | 64.0314 | 84.6707 | 118.1153 | 148.5374 | 180.7762 | 0.1867%
415 | 10-80.5 | -80.4251 | 9.5745 | 1393.5338 | 64.4103 | 85.085 | 118.491 | 148.8336 | 180.9772 | 0.1878%
416 | 10-80.5 | -80.6964 | 9.5745 | 1411.0378 | 64.5205 | 85.2598 | 118.6556 | 148.9205 | 180.9958 | 0.1881%
417 | 10-81 | -80.9677 | 9.5745 | 1428.561 | 64.2772 | 85.0756 | 118.467 | 148.6373 | 180.6935 | 0.1872%
418 | 10-81 | -81.239 | 9.5745 | 1446.1025 | 63.7253 | 84.5763 | 117.9633 | 148.0305 | 180.1126 | 0.1852%
419 | 10-81.5 | -81.5104 | 9.5745 | 1463.6617 | 62.947 | 83.8357 | 117.2344 | 147.2081 | 179.3367 | 0.1825%
420 | 10-82 | -81.7817 | 9.5745 | 1481.2379 | 61.9178 | 82.7952 | 116.1381 | 146.0311 | 178.1986 | 0.1786%
421 | 10-82 | -82.053 | 9.5745 | 1498.8306 | 60.6789 | 81.4956 | 114.6608 | 144.4324 | 176.6125 | 0.1735%
422 | 10-82.5 | -82.3243 | 9.5745 | 1516.4391 | 59.2775 | 80.0044 | 112.8537 | 142.4079 | 174.5683 | 0.1672%
423 | 10-82.5 | -82.5956 | 9.5745 | 1534.0628 | 57.8108 | 78.4064 | 110.8939 | 140.2018 | 172.375 | 0.1608%
424 | 10-83 | -82.867 | 9.5745 | 1551.7013 | 56.4138 | 76.8341 | 108.9561 | 138.0203 | 170.2569 | 0.1547%
425 | 10-83 | -83.1383 | 9.5745 | 1569.3539 | 55.1555 | 75.3667 | 107.1287 | 135.9733 | 168.3008 | 0.1492%
426 | 10-83.5 | -83.4096 | 9.5745 | 1587.0203 | 53.9598 | 73.8974 | 105.1935 | 133.7281 | 166.0829 | 0.1433%
427 | 10-83.5 | -83.6809 | 9.5745 | 1604.6999 | 52.8492 | 72.4343 | 103.1589 | 131.2931 | 163.5904 | 0.137%
428 | 10-84 | -83.9522 | 9.5745 | 1622.3923 | 51.8529 | 71.023 | 101.0896 | 128.7399 | 160.8634 | 0.1304%
429 | 10-84 | -84.2236 | 9.5745 | 1640.097 | 50.9996 | 69.7249 | 99.1047 | 126.225 | 158.0833 | 0.124%
430 | 10-84.5 | -84.4949 | 9.5745 | 1657.8137 | 50.3338 | 68.6373 | 97.3465 | 123.9288 | 155.4385 | 0.1181%
431 | 10-85 | -84.7662 | 9.5745 | 1675.5419 | 49.8542 | 67.7715 | 95.8499 | 121.9204 | 153.0282 | 0.1129%
432 | 10-85 | -85.0375 | 9.5745 | 1693.2813 | 49.5394 | 67.1217 | 94.5738 | 120.1351 | 150.8056 | 0.1082%
433 | 10-85.5 | -85.3089 | 9.5745 | 1711.0314 | 49.4287 | 66.8134 | 93.6999 | 118.7623 | 149.0055 | 0.1045%
434 | 10-85.5 | -85.5802 | 9.5745 | 1728.792 | 49.524 | 66.8496 | 93.2349 | 117.8579 | 147.7062 | 0.1018%
435 | 10-86 | -85.8515 | 9.5745 | 1746.5627 | 49.8193 | 67.1511 | 93.1157 | 117.3953 | 146.8711 | 0.1001%
436 | 10-86 | -86.1228 | 9.5745 | 1764.3432 | 50.2802 | 67.6253 | 93.2059 | 117.1915 | 146.2632 | 0.09878%
437 | 10-86.5 | -86.3941 | 9.5745 | 1782.1331 | 50.9344 | 68.261 | 93.4969 | 117.2319 | 145.8394 | 0.09781%
438 | 10-86.5 | -86.6655 | 9.5745 | 1799.9322 | 51.7082 | 68.9927 | 93.9072 | 117.3969 | 145.4565 | 0.09694%
439 | 10-87 | -86.9368 | 9.5745 | 1817.7401 | 52.7118 | 69.9749 | 94.7097 | 118.0575 | 145.5773 | 0.09713%
440 | 10-87 | -87.2081 | 9.5745 | 1835.5567 | 54.0443 | 71.3114 | 96.0135 | 119.2974 | 146.2865 | 0.09859%
441 | 10-87.5 | -87.4794 | 9.5745 | 1853.3815 | 55.6654 | 72.9577 | 97.7338 | 120.995 | 147.4968 | 0.1012%
442 | 10-88 | -87.7507 | 9.5745 | 1871.2145 | 57.4579 | 74.7807 | 99.6554 | 122.8972 | 148.9597 | 0.1045%
443 | 10-88 | -88.0221 | 9.5745 | 1889.0552 | 59.4533 | 76.8016 | 101.7881 | 125.0026 | 150.6766 | 0.1085%
444 | 10-88.5 | -88.2934 | 9.5745 | 1906.9035 | 61.6806 | 79.048 | 104.1655 | 127.3321 | 152.6618 | 0.1134%
445 | 10-88.5 | -88.5647 | 9.5745 | 1924.7592 | 64.0667 | 81.434 | 106.7163 | 129.8433 | 154.8667 | 0.1193%
446 | 10-89 | -88.836 | 9.5745 | 1942.6219 | 66.5756 | 83.8678 | 109.3645 | 132.4636 | 157.2198 | 0.126%
447 | 10-89 | -89.1074 | 9.5745 | 1960.4916 | 69.1927 | 86.3451 | 112.1216 | 135.1974 | 159.7231 | 0.1338%
448 | 10-89.5 | -89.3787 | 9.5745 | 1978.368 | 71.8918 | 88.9195 | 115.0174 | 138.0822 | 162.4342 | 0.143%
449 | 10-89.5 | -89.65 | 9.5745 | 1996.2509 | 74.5042 | 91.4638 | 117.8622 | 140.9005 | 165.1043 | 0.1531%
450 | 10-90 | -89.9213 | 9.5745 | 2014.14 | 76.9947 | 93.9946 | 120.6574 | 143.6442 | 167.7466 | 0.1639%
451 | 10-90 | -90.1926 | 9.5745 | 2032.0353 | 79.4582 | 96.6016 | 123.5194 | 146.4651 | 170.5739 | 0.1764%
452 | 10-90.5 | -90.464 | 9.5745 | 2049.9365 | 81.8549 | 99.2276 | 126.4063 | 149.3431 | 173.561 | 0.1906%
453 | 10-90.5 | -90.7353 | 9.5745 | 2067.8435 | 84.1126 | 101.8039 | 129.2658 | 152.2484 | 176.6556 | 0.2062%
454 | 10-50 | -50.0371 | 9.8458 | 811.7937 | 73.8215 | 96.2428 | 132.554 | 161.503 | 191.4283 | 0.2411%
455 | 10-50.5 | -50.3084 | 9.8458 | 795.752 | 73.6156 | 96.015 | 132.2876 | 161.3055 | 191.3367 | 0.2401%
456 | 10-50.5 | -50.5797 | 9.8458 | 779.8088 | 73.407 | 95.7753 | 132.0125 | 161.1082 | 191.2453 | 0.2391%
457 | 10-51 | -50.851 | 9.8458 | 763.9701 | 73.2044 | 95.5385 | 131.7525 | 160.9345 | 191.1821 | 0.2381%
458 | 10-51 | -51.1224 | 9.8458 | 748.2426 | 73.0212 | 95.324 | 131.5323 | 160.8092 | 191.1796 | 0.2375%
459 | 10-51.5 | -51.3937 | 9.8458 | 732.6335 | 72.8528 | 95.1248 | 131.3292 | 160.6916 | 191.1749 | 0.2368%
460 | 10-51.5 | -51.665 | 9.8458 | 717.1506 | 72.7188 | 94.9656 | 131.1715 | 160.6099 | 191.196 | 0.2363%
461 | 10-52 | -51.9363 | 9.8458 | 701.8022 | 72.6384 | 94.8658 | 131.0827 | 160.5906 | 191.2704 | 0.2362%
462 | 10-52 | -52.2077 | 9.8458 | 686.5974 | 72.5959 | 94.8049 | 131.0433 | 160.6214 | 191.3825 | 0.2363%
463 | 10-52.5 | -52.479 | 9.8458 | 671.5458 | 72.6055 | 94.7916 | 131.0579 | 160.7069 | 191.5448 | 0.2366%
464 | 10-53 | -52.7503 | 9.8458 | 656.6582 | 72.6787 | 94.8345 | 131.1326 | 160.85 | 191.7639 | 0.2372%
465 | 10-53 | -53.0216 | 9.8458 | 641.9458 | 72.7659 | 94.8831 | 131.2007 | 160.9719 | 191.9482 | 0.2377%
466 | 10-53.5 | -53.2929 | 9.8458 | 627.4211 | 72.8956 | 94.966 | 131.2944 | 161.1072 | 192.1405 | 0.2384%
467 | 10-53.5 | -53.5643 | 9.8458 | 613.0974 | 73.0923 | 95.1052 | 131.4338 | 161.2739 | 192.3594 | 0.2392%
468 | 10-54 | -53.8356 | 9.8458 | 598.9891 | 73.3178 | 95.2654 | 131.5777 | 161.424 | 192.541 | 0.2401%
469 | 10-54 | -54.1069 | 9.8458 | 585.1118 | 73.6092 | 95.4766 | 131.7464 | 161.5794 | 192.7151 | 0.241%
470 | 10-54.5 | -54.3782 | 9.8458 | 571.4825 | 73.9793 | 95.7516 | 131.9455 | 161.7431 | 192.8842 | 0.242%
471 | 10-54.5 | -54.6495 | 9.8458 | 558.1192 | 74.3817 | 96.0372 | 132.1091 | 161.8387 | 192.949 | 0.2429%
472 | 10-55 | -54.9209 | 9.8458 | 545.0415 | 74.8274 | 96.3462 | 132.2621 | 161.9076 | 192.9719 | 0.2436%
473 | 10-55 | -55.1922 | 9.8458 | 532.2706 | 75.3086 | 96.672 | 132.4011 | 161.9525 | 192.9634 | 0.2443%
474 | 10-55.5 | -55.4635 | 9.8458 | 519.8289 | 75.7708 | 96.9706 | 132.4858 | 161.9353 | 192.8889 | 0.2448%
475 | 10-55.5 | -55.7348 | 9.8458 | 507.7409 | 76.2301 | 97.2643 | 132.5388 | 161.8725 | 192.7666 | 0.245%
476 | 10-56 | -56.0061 | 9.8458 | 496.0322 | 76.679 | 97.5523 | 132.5613 | 161.7643 | 192.5957 | 0.2451%
477 | 10-56.5 | -56.2775 | 9.8458 | 484.7305 | 77.0699 | 97.7912 | 132.5144 | 161.5728 | 192.3313 | 0.2448%
478 | 10-56.5 | -56.5488 | 9.8458 | 473.8649 | 77.4511 | 98.0317 | 132.4694 | 161.3822 | 192.0711 | 0.2445%
479 | 10-57 | -56.8201 | 9.8458 | 463.466 | 77.8139 | 98.2689 | 132.4293 | 161.1996 | 191.826 | 0.2442%
480 | 10-57 | -57.0914 | 9.8458 | 453.5659 | 78.1073 | 98.4653 | 132.3675 | 161.0025 | 191.5702 | 0.2438%
481 | 10-57.5 | -57.3628 | 9.8458 | 444.1981 | 78.371 | 98.6596 | 132.3326 | 160.8475 | 191.3764 | 0.2435%
482 | 10-57.5 | -57.6341 | 9.8458 | 435.3968 | 78.5779 | 98.8322 | 132.3084 | 160.7191 | 191.2264 | 0.2434%
483 | 10-58 | -57.9054 | 9.8458 | 427.1972 | 78.673 | 98.9291 | 132.233 | 160.5461 | 191.0279 | 0.2428%
484 | 10-58 | -58.1767 | 9.8458 | 419.6344 | 78.7066 | 99.0048 | 132.1775 | 160.411 | 190.8835 | 0.2425%
485 | 10-58.5 | -58.448 | 9.8458 | 412.7436 | 78.6665 | 99.0446 | 132.1279 | 160.2983 | 190.776 | 0.2421%
486 | 10-58.5 | -58.7194 | 9.8458 | 406.5589 | 78.5142 | 99.0133 | 132.0382 | 160.1525 | 190.6399 | 0.2415%
487 | 10-59 | -58.9907 | 9.8458 | 401.1129 | 78.2945 | 98.9411 | 131.9423 | 160.0106 | 190.5069 | 0.2408%
488 | 10-59.5 | -59.262 | 9.8458 | 396.4361 | 77.9891 | 98.7981 | 131.8063 | 159.8376 | 190.3483 | 0.2399%
489 | 10-59.5 | -59.5333 | 9.8458 | 392.556 | 77.5704 | 98.5399 | 131.5686 | 159.5648 | 190.1064 | 0.2385%
490 | 10-60 | -59.8046 | 9.8458 | 389.4965 | 77.08 | 98.2081 | 131.2678 | 159.2318 | 189.8252 | 0.2368%
491 | 10-60 | -60.076 | 9.8458 | 387.2769 | 76.4978 | 97.7741 | 130.8618 | 158.798 | 189.4376 | 0.2345%
492 | 10-60.5 | -60.3473 | 9.8458 | 385.9118 | 75.7988 | 97.1976 | 130.2864 | 158.1956 | 188.8486 | 0.2314%
493 | 10-60.5 | -60.6186 | 9.8458 | 385.4103 | 75.0201 | 96.5035 | 129.5601 | 157.4473 | 188.0894 | 0.2276%
494 | 10-61 | -60.8899 | 9.8458 | 385.7757 | 74.2175 | 95.7768 | 128.8188 | 156.7051 | 187.324 | 0.2239%
495 | 10-61 | -61.1613 | 9.8458 | 387.0055 | 73.4794 | 95.1447 | 128.2665 | 156.1918 | 186.7922 | 0.2212%
496 | 10-61.5 | -61.4326 | 9.8458 | 389.0916 | 72.8536 | 94.6579 | 127.9696 | 155.9651 | 186.5895 | 0.2199%
497 | 10-61.5 | -61.7039 | 9.8458 | 392.0203 | 72.2594 | 94.1969 | 127.7284 | 155.8083 | 186.4958 | 0.2188%
498 | 10-62 | -61.9752 | 9.8458 | 395.7729 | 71.6152 | 93.6466 | 127.3513 | 155.5109 | 186.309 | 0.2173%
499 | 10-62 | -62.2465 | 9.8458 | 400.3262 | 70.9577 | 93.044 | 126.8928 | 155.1339 | 186.1062 | 0.2155%
500 | 10-62.5 | -62.5179 | 9.8458 | 405.6532 | 70.2799 | 92.3993 | 126.3672 | 154.6721 | 185.8352 | 0.2135%
501 | 10-63 | -62.7892 | 9.8458 | 411.724 | 69.5947 | 91.7387 | 125.8129 | 154.1642 | 185.4767 | 0.2113%
502 | 10-63 | -63.0605 | 9.8458 | 418.5061 | 68.9285 | 91.1009 | 125.2911 | 153.6833 | 185.0971 | 0.2092%
503 | 10-63.5 | -63.3318 | 9.8458 | 425.9655 | 68.2806 | 90.4807 | 124.7978 | 153.23 | 184.7154 | 0.2072%
504 | 10-63.5 | -63.6031 | 9.8458 | 434.0674 | 67.6661 | 89.9035 | 124.3664 | 152.8396 | 184.4017 | 0.2055%
505 | 10-64 | -63.8745 | 9.8458 | 442.7764 | 67.111 | 89.4102 | 124.0593 | 152.5796 | 184.2524 | 0.2044%
506 | 10-64 | -64.1458 | 9.8458 | 452.0575 | 66.5324 | 88.8786 | 123.674 | 152.2369 | 184.018 | 0.203%
507 | 10-64.5 | -64.4171 | 9.8458 | 461.8762 | 65.8268 | 88.1551 | 122.9607 | 151.511 | 183.3947 | 0.2003%
508 | 10-64.5 | -64.6884 | 9.8458 | 472.1989 | 64.9089 | 87.1277 | 121.7438 | 150.1654 | 182.1712 | 0.1954%
509 | 10-65 | -64.9598 | 9.8458 | 482.9933 | 63.9305 | 86.0059 | 120.3626 | 148.6541 | 180.7314 | 0.19%
510 | 10-65 | -65.2311 | 9.8458 | 494.2284 | 63.0334 | 85.0031 | 119.1779 | 147.3788 | 179.4603 | 0.1856%
511 | 10-65.5 | -65.5024 | 9.8458 | 505.875 | 62.3045 | 84.2512 | 118.4151 | 146.5305 | 178.5829 | 0.1827%
512 | 10-66 | -65.7737 | 9.8458 | 517.9051 | 61.6396 | 83.5924 | 117.811 | 145.8472 | 177.8159 | 0.1803%
513 | 10-66 | -66.045 | 9.8458 | 530.2928 | 61.0017 | 82.9635 | 117.2546 | 145.2458 | 177.1207 | 0.1783%
514 | 10-66.5 | -66.3164 | 9.8458 | 543.0136 | 60.3855 | 82.3585 | 116.7343 | 144.7199 | 176.5467 | 0.1765%
515 | 10-66.5 | -66.5877 | 9.8458 | 556.0445 | 59.696 | 81.6397 | 116.0424 | 144.0425 | 175.8241 | 0.1742%
516 | 10-67 | -66.859 | 9.8458 | 569.3642 | 58.9082 | 80.778 | 115.1091 | 143.1436 | 174.8708 | 0.1713%
517 | 10-67 | -67.1303 | 9.8458 | 582.953 | 58.0237 | 79.7766 | 113.9275 | 142.0164 | 173.6704 | 0.1676%
518 | 10-67.5 | -67.4016 | 9.8458 | 596.7924 | 57.1038 | 78.7181 | 112.6324 | 140.7525 | 172.3534 | 0.1637%
519 | 10-67.5 | -67.673 | 9.8458 | 610.8655 | 56.2358 | 77.7394 | 111.4534 | 139.5706 | 171.1909 | 0.1602%
520 | 10-68 | -67.9443 | 9.8458 | 625.1563 | 55.4551 | 76.9025 | 110.497 | 138.6119 | 170.2943 | 0.1576%
521 | 10-68 | -68.2156 | 9.8458 | 639.6503 | 54.8642 | 76.3015 | 109.9517 | 138.1294 | 169.7967 | 0.1563%
522 | 10-68.5 | -68.4869 | 9.8458 | 654.3341 | 54.321 | 75.7339 | 109.478 | 137.7045 | 169.3085 | 0.1551%
523 | 10-69 | -68.7583 | 9.8458 | 669.1949 | 53.7509 | 75.1012 | 108.9022 | 137.1312 | 168.6564 | 0.1535%
524 | 10-69 | -69.0296 | 9.8458 | 684.2214 | 53.1638 | 74.4316 | 108.2538 | 136.5776 | 168.0188 | 0.1519%
525 | 10-69.5 | -69.3009 | 9.8458 | 699.4029 | 52.6557 | 73.8809 | 107.7893 | 136.3163 | 167.6816 | 0.1511%
526 | 10-69.5 | -69.5722 | 9.8458 | 714.7293 | 52.262 | 73.504 | 107.6008 | 136.4138 | 167.7179 | 0.1513%
527 | 10-70 | -69.8435 | 9.8458 | 730.1917 | 51.8689 | 73.1228 | 107.402 | 136.5356 | 167.8001 | 0.1515%
528 | 10-70 | -70.1149 | 9.8458 | 745.7815 | 51.5675 | 72.8777 | 107.3726 | 136.9031 | 168.1953 | 0.1524%
529 | 10-70.5 | -70.3862 | 9.8458 | 761.4908 | 51.3758 | 72.7956 | 107.5721 | 137.5635 | 168.9497 | 0.1541%
530 | 10-70.5 | -70.6575 | 9.8458 | 777.3125 | 51.2423 | 72.789 | 107.8759 | 138.2031 | 169.7018 | 0.1558%
531 | 10-71 | -70.9288 | 9.8458 | 793.2397 | 51.0982 | 72.7741 | 108.1502 | 138.7322 | 170.3039 | 0.1573%
532 | 10-71 | -71.2001 | 9.8458 | 809.2663 | 50.942 | 72.7478 | 108.3887 | 139.1638 | 170.7625 | 0.1585%
533 | 10-71.5 | -71.4715 | 9.8458 | 825.3864 | 50.8381 | 72.8134 | 108.7462 | 139.7068 | 171.4039 | 0.1601%
534 | 10-71.5 | -71.7428 | 9.8458 | 841.5946 | 50.6832 | 72.8713 | 109.0028 | 140.1438 | 172.0927 | 0.1615%
535 | 10-72 | -72.0141 | 9.8458 | 857.8859 | 50.4741 | 72.9006 | 109.1543 | 140.4605 | 172.7697 | 0.1628%
536 | 10-72.5 | -72.2854 | 9.8458 | 874.2557 | 50.2444 | 72.8702 | 109.2134 | 140.6757 | 173.3352 | 0.1637%
537 | 10-72.5 | -72.5568 | 9.8458 | 890.6996 | 49.9862 | 72.7436 | 109.1312 | 140.6646 | 173.5647 | 0.164%
538 | 10-73 | -72.8281 | 9.8458 | 907.2135 | 49.6957 | 72.5104 | 108.8822 | 140.377 | 173.438 | 0.1635%
539 | 10-73 | -73.0994 | 9.8458 | 923.7938 | 49.3395 | 72.1291 | 108.3581 | 139.7113 | 172.9222 | 0.162%
540 | 10-73.5 | -73.3707 | 9.8458 | 940.4368 | 49.04 | 71.7828 | 107.8455 | 138.9996 | 172.339 | 0.1604%
541 | 10-73.5 | -73.642 | 9.8458 | 957.1393 | 48.8336 | 71.5153 | 107.4378 | 138.3291 | 171.7697 | 0.1589%
542 | 10-74 | -73.9134 | 9.8458 | 973.8981 | 48.8172 | 71.4492 | 107.3481 | 137.9795 | 171.4532 | 0.1582%
543 | 10-74 | -74.1847 | 9.8458 | 990.7105 | 49.0547 | 71.6841 | 107.7268 | 138.2565 | 171.7554 | 0.159%
544 | 10-74.5 | -74.456 | 9.8458 | 1007.5737 | 49.531 | 72.1955 | 108.5096 | 139.0658 | 172.6253 | 0.1611%
545 | 10-74.5 | -74.7273 | 9.8458 | 1024.4852 | 50.1713 | 72.8901 | 109.5242 | 140.2488 | 173.9249 | 0.1642%
546 | 10-75 | -74.9986 | 9.8458 | 1041.4426 | 50.9231 | 73.6703 | 110.6241 | 141.6027 | 175.3455 | 0.1677%
547 | 10-75.5 | -75.27 | 9.8458 | 1058.4437 | 51.7705 | 74.5001 | 111.7755 | 143.0396 | 176.7538 | 0.1713%
548 | 10-75.5 | -75.5413 | 9.8458 | 1075.4864 | 52.6682 | 75.3256 | 112.8839 | 144.4061 | 178.0112 | 0.1747%
549 | 10-76 | -75.8126 | 9.8458 | 1092.5688 | 53.596 | 76.1857 | 113.9483 | 145.7006 | 179.2229 | 0.1781%
550 | 10-76 | -76.0839 | 9.8458 | 1109.6889 | 54.5364 | 77.062 | 114.9324 | 146.8738 | 180.3958 | 0.1813%
551 | 10-76.5 | -76.3553 | 9.8458 | 1126.8451 | 55.4834 | 77.94 | 115.8182 | 147.91 | 181.4872 | 0.1843%
552 | 10-76.5 | -76.6266 | 9.8458 | 1144.0357 | 56.4916 | 78.8825 | 116.7343 | 148.9449 | 182.5523 | 0.1874%
553 | 10-77 | -76.8979 | 9.8458 | 1161.2591 | 57.5782 | 79.9171 | 117.7223 | 150.0379 | 183.655 | 0.1908%
554 | 10-77 | -77.1692 | 9.8458 | 1178.514 | 58.7377 | 81.0322 | 118.7617 | 151.168 | 184.7742 | 0.1944%
555 | 10-77.5 | -77.4405 | 9.8458 | 1195.7988 | 59.9053 | 82.1311 | 119.6713 | 152.0912 | 185.686 | 0.1976%
556 | 10-77.5 | -77.7119 | 9.8458 | 1213.1124 | 61.0058 | 83.1333 | 120.3662 | 152.7256 | 186.2936 | 0.2%
557 | 10-78 | -77.9832 | 9.8458 | 1230.4535 | 62.0018 | 84.0081 | 120.8412 | 153.0712 | 186.5718 | 0.2015%
558 | 10-78.5 | -78.2545 | 9.8458 | 1247.8209 | 62.9771 | 84.8543 | 121.2653 | 153.2782 | 186.6287 | 0.2026%
559 | 10-78.5 | -78.5258 | 9.8458 | 1265.2135 | 63.9361 | 85.6756 | 121.6748 | 153.4156 | 186.5612 | 0.2035%
560 | 10-79 | -78.7971 | 9.8458 | 1282.6303 | 64.913 | 86.5112 | 122.1503 | 153.6215 | 186.5651 | 0.2046%
561 | 10-79 | -79.0685 | 9.8458 | 1300.0703 | 65.942 | 87.4305 | 122.7896 | 154.0495 | 186.8374 | 0.2066%
562 | 10-79.5 | -79.3398 | 9.8458 | 1317.5325 | 66.9082 | 88.3113 | 123.4416 | 154.5292 | 187.1874 | 0.2088%
563 | 10-79.5 | -79.6111 | 9.8458 | 1335.0161 | 67.7662 | 89.1067 | 124.0529 | 154.9983 | 187.5353 | 0.211%
564 | 10-80 | -79.8824 | 9.8458 | 1352.5202 | 68.5441 | 89.8486 | 124.6713 | 155.5105 | 187.9308 | 0.2133%
565 | 10-80 | -80.1537 | 9.8458 | 1370.044 | 69.1466 | 90.4482 | 125.2036 | 155.9719 | 188.3066 | 0.2154%
566 | 10-80.5 | -80.4251 | 9.8458 | 1387.5867 | 69.5106 | 90.8418 | 125.573 | 156.2878 | 188.5685 | 0.2168%
567 | 10-80.5 | -80.6964 | 9.8458 | 1405.1476 | 69.6129 | 91.0053 | 125.7392 | 156.3972 | 188.6424 | 0.2174%
568 | 10-81 | -80.9677 | 9.8458 | 1422.726 | 69.3703 | 90.8275 | 125.572 | 156.1543 | 188.4111 | 0.2164%
569 | 10-81 | -81.239 | 9.8458 | 1440.3213 | 68.8288 | 90.3544 | 125.1098 | 155.6088 | 187.923 | 0.2143%
570 | 10-81.5 | -81.5104 | 9.8458 | 1457.9328 | 68.0719 | 89.6598 | 124.4392 | 154.8668 | 187.2594 | 0.2113%
571 | 10-82 | -81.7817 | 9.8458 | 1475.5599 | 67.0593 | 88.6563 | 123.3686 | 153.7474 | 186.1998 | 0.2068%
572 | 10-82 | -82.053 | 9.8458 | 1493.2021 | 65.8288 | 87.3689 | 121.8585 | 152.1516 | 184.6151 | 0.2007%
573 | 10-82.5 | -82.3243 | 9.8458 | 1510.8587 | 64.427 | 85.8601 | 119.958 | 150.0606 | 182.4746 | 0.193%
574 | 10-82.5 | -82.5956 | 9.8458 | 1528.5294 | 62.9524 | 84.2287 | 117.8777 | 147.7516 | 180.1301 | 0.1849%
575 | 10-83 | -82.867 | 9.8458 | 1546.2135 | 61.5425 | 82.6171 | 115.8106 | 145.4568 | 177.844 | 0.1773%
576 | 10-83 | -83.1383 | 9.8458 | 1563.9106 | 60.2647 | 81.1055 | 113.8547 | 143.2918 | 175.7213 | 0.1704%
577 | 10-83.5 | -83.4096 | 9.8458 | 1581.6202 | 59.0359 | 79.5821 | 111.7939 | 140.9263 | 173.3441 | 0.1632%
578 | 10-83.5 | -83.6809 | 9.8458 | 1599.342 | 57.8703 | 78.0539 | 109.6382 | 138.381 | 170.7183 | 0.1556%
579 | 10-84 | -83.9522 | 9.8458 | 1617.0755 | 56.8075 | 76.57 | 107.4496 | 135.7294 | 167.8882 | 0.1478%
580 | 10-84 | -84.2236 | 9.8458 | 1634.8202 | 55.8807 | 75.1951 | 105.3449 | 133.1289 | 165.036 | 0.1404%
581 | 10-84.5 | -84.4949 | 9.8458 | 1652.5758 | 55.1323 | 74.0167 | 103.4508 | 130.7412 | 162.3245 | 0.1336%
582 | 10-85 | -84.7662 | 9.8458 | 1670.342 | 54.5576 | 73.0401 | 101.7976 | 128.6289 | 159.843 | 0.1276%
583 | 10-85 | -85.0375 | 9.8458 | 1688.1184 | 54.127 | 72.243 | 100.324 | 126.6998 | 157.5169 | 0.1221%
584 | 10-85.5 | -85.3089 | 9.8458 | 1705.9046 | 53.8899 | 71.7625 | 99.2551 | 125.1803 | 155.6298 | 0.1178%
585 | 10-85.5 | -85.5802 | 9.8458 | 1723.7003 | 53.8502 | 71.6147 | 98.6289 | 124.1593 | 154.2914 | 0.1148%
586 | 10-86 | -85.8515 | 9.8458 | 1741.5052 | 53.9998 | 71.7183 | 98.3781 | 123.6106 | 153.4611 | 0.1129%
587 | 10-86 | -86.1228 | 9.8458 | 1759.319 | 54.3024 | 71.9792 | 98.339 | 123.326 | 152.8637 | 0.1117%
588 | 10-86.5 | -86.3941 | 9.8458 | 1777.1415 | 54.7877 | 72.397 | 98.5031 | 123.2922 | 152.451 | 0.1108%
589 | 10-86.5 | -86.6655 | 9.8458 | 1794.9723 | 55.3974 | 72.9245 | 98.8025 | 123.4089 | 152.0918 | 0.1101%
590 | 10-87 | -86.9368 | 9.8458 | 1812.8111 | 56.2476 | 73.7259 | 99.5152 | 124.0409 | 152.2448 | 0.1107%
591 | 10-87 | -87.2081 | 9.8458 | 1830.6578 | 57.4478 | 74.9172 | 100.7613 | 125.2703 | 152.9932 | 0.1127%
592 | 10-87.5 | -87.4794 | 9.8458 | 1848.5121 | 58.9587 | 76.4562 | 102.4607 | 126.9757 | 154.248 | 0.1161%
593 | 10-88 | -87.7507 | 9.8458 | 1866.3736 | 60.6754 | 78.2069 | 104.3945 | 128.8983 | 155.7547 | 0.1202%
594 | 10-88 | -88.0221 | 9.8458 | 1884.2423 | 62.6255 | 80.1929 | 106.5819 | 131.0416 | 157.5214 | 0.1253%
595 | 10-88.5 | -88.2934 | 9.8458 | 1902.1179 | 64.8352 | 82.4457 | 109.0566 | 133.43 | 159.5677 | 0.1315%
596 | 10-88.5 | -88.5647 | 9.8458 | 1920.0001 | 67.2403 | 84.8938 | 111.7576 | 136.0515 | 161.8768 | 0.1389%
597 | 10-89 | -88.836 | 9.8458 | 1937.8887 | 69.8095 | 87.4654 | 114.6168 | 138.8416 | 164.3874 | 0.1477%
598 | 10-89 | -89.1074 | 9.8458 | 1955.7837 | 72.523 | 90.1556 | 117.6293 | 141.7882 | 167.0898 | 0.1579%
599 | 10-89.5 | -89.3787 | 9.8458 | 1973.6847 | 75.3628 | 93.0295 | 120.8268 | 144.9335 | 170.0524 | 0.1701%
600 | 10-89.5 | -89.65 | 9.8458 | 1991.5916 | 78.1413 | 95.9102 | 123.9831 | 148.0152 | 172.9761 | 0.1835%
601 | 10-90 | -89.9213 | 9.8458 | 2009.5042 | 80.8299 | 98.7984 | 127.0957 | 151.0192 | 175.8724 | 0.198%
602 | 10-90 | -90.1926 | 9.8458 | 2027.4223 | 83.5204 | 101.7655 | 130.2683 | 154.0874 | 178.9449 | 0.2147%
603 | 10-90.5 | -90.464 | 9.8458 | 2045.3458 | 86.1685 | 104.7417 | 133.4399 | 157.1872 | 182.1454 | 0.2334%
604 | 10-90.5 | -90.7353 | 9.8458 | 2063.2745 | 88.6815 | 107.6361 | 136.5281 | 160.2576 | 185.381 | 0.2537%
605 | 10-50 | -50.0371 | 10.1171 | 802.7497 | 78.7138 | 101.8804 | 139.7808 | 169.0466 | 199.1254 | 0.2802%
606 | 10-50.5 | -50.3084 | 10.1171 | 786.5398 | 78.5115 | 101.6684 | 139.5395 | 168.8786 | 199.066 | 0.2791%
607 | 10-50.5 | -50.5797 | 10.1171 | 770.4221 | 78.3013 | 101.4371 | 139.2806 | 168.6978 | 198.9884 | 0.2779%
608 | 10-51 | -50.851 | 10.1171 | 754.4023 | 78.0921 | 101.2009 | 139.0272 | 168.5269 | 198.9202 | 0.2768%
609 | 10-51 | -51.1224 | 10.1171 | 738.487 | 77.898 | 100.9786 | 138.803 | 168.3904 | 198.8944 | 0.2758%
610 | 10-51.5 | -51.3937 | 10.1171 | 722.6831 | 77.7141 | 100.7622 | 138.586 | 168.2503 | 198.8541 | 0.2749%
611 | 10-51.5 | -51.665 | 10.1171 | 706.9979 | 77.5598 | 100.5767 | 138.4047 | 168.1373 | 198.8328 | 0.2741%
612 | 10-52 | -51.9363 | 10.1171 | 691.4397 | 77.4522 | 100.4411 | 138.2822 | 168.0784 | 198.8606 | 0.2737%
613 | 10-52 | -52.2077 | 10.1171 | 676.0172 | 77.3747 | 100.3358 | 138.2003 | 168.062 | 198.9208 | 0.2734%
614 | 10-52.5 | -52.479 | 10.1171 | 660.74 | 77.3405 | 100.2726 | 138.1662 | 168.0963 | 199.0309 | 0.2735%
615 | 10-53 | -52.7503 | 10.1171 | 645.6183 | 77.3614 | 100.262 | 138.1875 | 168.1862 | 199.2002 | 0.2738%
616 | 10-53 | -53.0216 | 10.1171 | 630.6634 | 77.394 | 100.2564 | 138.201 | 168.2549 | 199.3366 | 0.2741%
617 | 10-53.5 | -53.2929 | 10.1171 | 615.8874 | 77.4669 | 100.285 | 138.2391 | 168.3387 | 199.4868 | 0.2746%
618 | 10-53.5 | -53.5643 | 10.1171 | 601.3036 | 77.6035 | 100.3696 | 138.321 | 168.4554 | 199.67 | 0.2753%
619 | 10-54 | -53.8356 | 10.1171 | 586.9262 | 77.7681 | 100.4763 | 138.4101 | 168.5637 | 199.8318 | 0.276%
620 | 10-54 | -54.1069 | 10.1171 | 572.7709 | 77.9967 | 100.6368 | 138.5278 | 168.6875 | 200.0055 | 0.277%
621 | 10-54.5 | -54.3782 | 10.1171 | 558.8545 | 78.3006 | 100.8649 | 138.6795 | 168.8297 | 200.1931 | 0.2781%
622 | 10-54.5 | -54.6495 | 10.1171 | 545.1954 | 78.6383 | 101.1071 | 138.7993 | 168.91 | 200.2863 | 0.2791%
623 | 10-55 | -54.9209 | 10.1171 | 531.8134 | 79.0221 | 101.3777 | 138.9119 | 168.9675 | 200.3417 | 0.28%
624 | 10-55 | -55.1922 | 10.1171 | 518.7299 | 79.4487 | 101.6747 | 139.0171 | 169.007 | 200.3707 | 0.281%
625 | 10-55.5 | -55.4635 | 10.1171 | 505.9682 | 79.8747 | 101.9579 | 139.0794 | 168.9935 | 200.3383 | 0.2817%
626 | 10-55.5 | -55.7348 | 10.1171 | 493.5531 | 80.3174 | 102.2496 | 139.121 | 168.9442 | 200.2654 | 0.2824%
627 | 10-56 | -56.0061 | 10.1171 | 481.5116 | 80.7709 | 102.5492 | 139.1436 | 168.8593 | 200.1509 | 0.2829%
628 | 10-56.5 | -56.2775 | 10.1171 | 469.8724 | 81.1872 | 102.8098 | 139.105 | 168.6957 | 199.9415 | 0.283%
629 | 10-56.5 | -56.5488 | 10.1171 | 458.666 | 81.6086 | 103.0802 | 139.0741 | 168.5358 | 199.7351 | 0.2831%
630 | 10-57 | -56.8201 | 10.1171 | 447.9251 | 82.0256 | 103.3559 | 139.0541 | 168.3867 | 199.5416 | 0.2833%
631 | 10-57 | -57.0914 | 10.1171 | 437.6838 | 82.3876 | 103.5976 | 139.0185 | 168.224 | 199.3308 | 0.2834%
632 | 10-57.5 | -57.3628 | 10.1171 | 427.9782 | 82.7318 | 103.8436 | 139.0119 | 168.098 | 199.1658 | 0.2836%
633 | 10-57.5 | -57.6341 | 10.1171 | 418.8453 | 83.0364 | 104.0773 | 139.0233 | 168.0001 | 199.0377 | 0.2838%
634 | 10-58 | -57.9054 | 10.1171 | 410.3235 | 83.2568 | 104.2506 | 139.0048 | 167.8796 | 198.8835 | 0.2838%
635 | 10-58 | -58.1767 | 10.1171 | 402.4516 | 83.4369 | 104.4206 | 139.029 | 167.8241 | 198.8152 | 0.2841%
636 | 10-58.5 | -58.448 | 10.1171 | 395.2685 | 83.5591 | 104.5689 | 139.0783 | 167.8127 | 198.8088 | 0.2844%
637 | 10-58.5 | -58.7194 | 10.1171 | 388.8123 | 83.5739 | 104.6503 | 139.0951 | 167.776 | 198.7809 | 0.2845%
638 | 10-59 | -58.9907 | 10.1171 | 383.1198 | 83.5188 | 104.7 | 139.1118 | 167.7504 | 198.7645 | 0.2845%
639 | 10-59.5 | -59.262 | 10.1171 | 378.2254 | 83.3741 | 104.6891 | 139.094 | 167.7009 | 198.7319 | 0.2842%
640 | 10-59.5 | -59.5333 | 10.1171 | 374.1606 | 83.1104 | 104.571 | 138.9798 | 167.5605 | 198.6293 | 0.2832%
641 | 10-60 | -59.8046 | 10.1171 | 370.9525 | 82.7702 | 104.3891 | 138.8114 | 167.3742 | 198.5094 | 0.282%
642 | 10-60 | -60.076 | 10.1171 | 368.6236 | 82.3315 | 104.1094 | 138.543 | 167.097 | 198.299 | 0.2801%
643 | 10-60.5 | -60.3473 | 10.1171 | 367.1906 | 81.766 | 103.6855 | 138.1055 | 166.6539 | 197.8938 | 0.2772%
644 | 10-60.5 | -60.6186 | 10.1171 | 366.6639 | 81.1117 | 103.1442 | 137.5191 | 166.0712 | 197.3302 | 0.2735%
645 | 10-61 | -60.8899 | 10.1171 | 367.0476 | 80.4235 | 102.5676 | 136.9178 | 165.4984 | 196.7692 | 0.2698%
646 | 10-61 | -61.1613 | 10.1171 | 368.3387 | 79.7857 | 102.0781 | 136.4992 | 165.1496 | 196.439 | 0.2672%
647 | 10-61.5 | -61.4326 | 10.1171 | 370.5278 | 79.2387 | 101.7212 | 136.3178 | 165.0638 | 196.4068 | 0.266%
648 | 10-61.5 | -61.7039 | 10.1171 | 373.599 | 78.7029 | 101.3757 | 136.173 | 165.024 | 196.4529 | 0.2651%
649 | 10-62 | -61.9752 | 10.1171 | 377.5309 | 78.1008 | 100.9282 | 135.8768 | 164.8245 | 196.3825 | 0.2634%
650 | 10-62 | -62.2465 | 10.1171 | 382.2969 | 77.4781 | 100.4249 | 135.4945 | 164.5405 | 196.2904 | 0.2614%
651 | 10-62.5 | -62.5179 | 10.1171 | 387.8662 | 76.8276 | 99.8695 | 135.0397 | 164.1645 | 196.121 | 0.2591%
652 | 10-63 | -62.7892 | 10.1171 | 394.2047 | 76.1633 | 99.286 | 134.55 | 163.7333 | 195.8509 | 0.2565%
653 | 10-63 | -63.0605 | 10.1171 | 401.2761 | 75.5141 | 98.7153 | 134.0867 | 163.3187 | 195.5432 | 0.254%
654 | 10-63.5 | -63.3318 | 10.1171 | 409.0423 | 74.8784 | 98.1513 | 133.6433 | 162.9172 | 195.211 | 0.2516%
655 | 10-63.5 | -63.6031 | 10.1171 | 417.4646 | 74.2729 | 97.6228 | 133.2552 | 162.5667 | 194.9272 | 0.2494%
656 | 10-64 | -63.8745 | 10.1171 | 426.5039 | 73.7274 | 97.1771 | 132.9906 | 162.343 | 194.8006 | 0.248%
657 | 10-64 | -64.1458 | 10.1171 | 436.1221 | 73.1578 | 96.6911 | 132.6468 | 162.0354 | 194.5871 | 0.2462%
658 | 10-64.5 | -64.4171 | 10.1171 | 446.2816 | 72.4612 | 96.0125 | 131.976 | 161.3471 | 193.9892 | 0.2428%
659 | 10-64.5 | -64.6884 | 10.1171 | 456.9463 | 71.554 | 95.0322 | 130.8046 | 160.0443 | 192.7994 | 0.237%
660 | 10-65 | -64.9598 | 10.1171 | 468.0817 | 70.5846 | 93.9542 | 129.466 | 158.5722 | 191.3893 | 0.2305%
661 | 10-65 | -65.2311 | 10.1171 | 479.655 | 69.6942 | 92.9901 | 128.3185 | 157.3284 | 190.1375 | 0.2251%
662 | 10-65.5 | -65.5024 | 10.1171 | 491.6352 | 68.9717 | 92.2729 | 127.588 | 156.5042 | 189.269 | 0.2215%
663 | 10-66 | -65.7737 | 10.1171 | 503.9934 | 68.3107 | 91.6416 | 127.0073 | 155.8311 | 188.4905 | 0.2186%
664 | 10-66 | -66.045 | 10.1171 | 516.7024 | 67.6736 | 91.0317 | 126.4652 | 155.2261 | 187.7642 | 0.2158%
665 | 10-66.5 | -66.3164 | 10.1171 | 529.7369 | 67.055 | 90.4375 | 125.9509 | 154.6852 | 187.1435 | 0.2134%
666 | 10-66.5 | -66.5877 | 10.1171 | 543.0734 | 66.3494 | 89.7047 | 125.2432 | 153.9652 | 186.3399 | 0.2103%
667 | 10-67 | -66.859 | 10.1171 | 556.6903 | 65.53 | 88.8021 | 124.2709 | 152.996 | 185.2726 | 0.2063%
668 | 10-67 | -67.1303 | 10.1171 | 570.5675 | 64.5994 | 87.7343 | 123.0287 | 151.7733 | 183.9295 | 0.2013%
669 | 10-67.5 | -67.4016 | 10.1171 | 584.6864 | 63.6285 | 86.6001 | 121.6663 | 150.4079 | 182.4657 | 0.196%
670 | 10-67.5 | -67.673 | 10.1171 | 599.03 | 62.7075 | 85.5406 | 120.4157 | 149.1198 | 181.1515 | 0.1913%
671 | 10-68 | -67.9443 | 10.1171 | 613.5823 | 61.8722 | 84.6186 | 119.3834 | 148.0489 | 180.0954 | 0.1876%
672 | 10-68 | -68.2156 | 10.1171 | 628.329 | 61.2365 | 83.9456 | 118.7741 | 147.4699 | 179.4591 | 0.1854%
673 | 10-68.5 | -68.4869 | 10.1171 | 643.2566 | 60.6626 | 83.327 | 118.2561 | 146.9755 | 178.869 | 0.1836%
674 | 10-69 | -68.7583 | 10.1171 | 658.3529 | 60.0771 | 82.6667 | 117.6581 | 146.3636 | 178.1575 | 0.1814%
675 | 10-69 | -69.0296 | 10.1171 | 673.6064 | 59.4618 | 81.951 | 116.9738 | 145.7553 | 177.4417 | 0.1792%
676 | 10-69.5 | -69.3009 | 10.1171 | 689.0067 | 58.9137 | 81.3369 | 116.4619 | 145.4272 | 177.0145 | 0.1778%
677 | 10-69.5 | -69.5722 | 10.1171 | 704.5442 | 58.469 | 80.8809 | 116.2156 | 145.4479 | 176.9522 | 0.1775%
678 | 10-70 | -69.8435 | 10.1171 | 720.2099 | 58.0082 | 80.3927 | 115.9272 | 145.4475 | 176.8706 | 0.1771%
679 | 10-70 | -70.1149 | 10.1171 | 735.9957 | 57.6328 | 80.0291 | 115.7841 | 145.6617 | 177.0515 | 0.1774%
680 | 10-70.5 | -70.3862 | 10.1171 | 751.894 | 57.3651 | 79.8237 | 115.8454 | 146.145 | 177.5501 | 0.1786%
681 | 10-70.5 | -70.6575 | 10.1171 | 767.8978 | 57.1886 | 79.7481 | 116.0834 | 146.6882 | 178.1615 | 0.1801%
682 | 10-71 | -70.9288 | 10.1171 | 784.0005 | 57.0244 | 79.7018 | 116.3316 | 147.1804 | 178.7104 | 0.1815%
683 | 10-71 | -71.2001 | 10.1171 | 800.1963 | 56.8678 | 79.6764 | 116.5782 | 147.6266 | 179.1912 | 0.1828%
684 | 10-71.5 | -71.4715 | 10.1171 | 816.4795 | 56.7732 | 79.7602 | 116.96 | 148.2079 | 179.8885 | 0.1846%
685 | 10-71.5 | -71.7428 | 10.1171 | 832.845 | 56.626 | 79.8362 | 117.2408 | 148.6852 | 180.6376 | 0.1862%
686 | 10-72 | -72.0141 | 10.1171 | 849.2881 | 56.4194 | 79.8775 | 117.4111 | 149.0363 | 181.3684 | 0.1876%
687 | 10-72.5 | -72.2854 | 10.1171 | 865.8042 | 56.1751 | 79.8325 | 117.465 | 149.2533 | 181.9439 | 0.1885%
688 | 10-72.5 | -72.5568 | 10.1171 | 882.3893 | 55.912 | 79.7067 | 117.3891 | 149.2583 | 182.2007 | 0.1888%
689 | 10-73 | -72.8281 | 10.1171 | 899.0396 | 55.6267 | 79.4908 | 117.1593 | 149.0031 | 182.1215 | 0.1882%
690 | 10-73 | -73.0994 | 10.1171 | 915.7514 | 55.2833 | 79.1398 | 116.6646 | 148.3835 | 181.6714 | 0.1866%
691 | 10-73.5 | -73.3707 | 10.1171 | 932.5215 | 55.0109 | 78.8493 | 116.2128 | 147.7667 | 181.2276 | 0.185%
692 | 10-73.5 | -73.642 | 10.1171 | 949.3467 | 54.8465 | 78.6642 | 115.9032 | 147.2416 | 180.8754 | 0.1838%
693 | 10-74 | -73.9134 | 10.1171 | 966.2241 | 54.886 | 78.7052 | 115.9533 | 147.084 | 180.8481 | 0.1837%
694 | 10-74 | -74.1847 | 10.1171 | 983.1511 | 55.1589 | 79.0128 | 116.4157 | 147.4946 | 181.3534 | 0.1851%
695 | 10-74.5 | -74.456 | 10.1171 | 1000.125 | 55.648 | 79.559 | 117.2387 | 148.3713 | 182.3278 | 0.1879%
696 | 10-74.5 | -74.7273 | 10.1171 | 1017.1436 | 56.2727 | 80.2433 | 118.2407 | 149.5391 | 183.6064 | 0.1915%
697 | 10-75 | -74.9986 | 10.1171 | 1034.2046 | 56.9925 | 80.9831 | 119.2923 | 150.8219 | 184.9204 | 0.1953%
698 | 10-75.5 | -75.27 | 10.1171 | 1051.3058 | 57.7966 | 81.7484 | 120.3691 | 152.1491 | 186.1667 | 0.1993%
699 | 10-75.5 | -75.5413 | 10.1171 | 1068.4455 | 58.6448 | 82.4995 | 121.3975 | 153.4041 | 187.2674 | 0.203%
700 | 10-76 | -75.8126 | 10.1171 | 1085.6217 | 59.5296 | 83.2953 | 122.3947 | 154.6111 | 188.363 | 0.2068%
701 | 10-76 | -76.0839 | 10.1171 | 1102.8326 | 60.4277 | 84.1074 | 123.3121 | 155.7009 | 189.4293 | 0.2104%
702 | 10-76.5 | -76.3553 | 10.1171 | 1120.0768 | 61.3255 | 84.9079 | 124.1151 | 156.6297 | 190.3791 | 0.2137%
703 | 10-76.5 | -76.6266 | 10.1171 | 1137.3526 | 62.2806 | 85.7616 | 124.9324 | 157.5336 | 191.2672 | 0.2171%
704 | 10-77 | -76.8979 | 10.1171 | 1154.6586 | 63.3087 | 86.6962 | 125.8088 | 158.4781 | 192.1694 | 0.2207%
705 | 10-77 | -77.1692 | 10.1171 | 1171.9935 | 64.4024 | 87.7003 | 126.7275 | 159.4502 | 193.0795 | 0.2246%
706 | 10-77.5 | -77.4405 | 10.1171 | 1189.3559 | 65.4971 | 88.6756 | 127.5061 | 160.2052 | 193.7737 | 0.228%
707 | 10-77.5 | -77.7119 | 10.1171 | 1206.7447 | 66.5192 | 89.5437 | 128.0628 | 160.665 | 194.1596 | 0.2304%
708 | 10-78 | -77.9832 | 10.1171 | 1224.1587 | 67.4354 | 90.281 | 128.4007 | 160.842 | 194.23 | 0.2318%
709 | 10-78.5 | -78.2545 | 10.1171 | 1241.5968 | 68.3373 | 90.9949 | 128.7003 | 160.9068 | 194.1265 | 0.2329%
710 | 10-78.5 | -78.5258 | 10.1171 | 1259.0581 | 69.2318 | 91.7001 | 129.0098 | 160.9442 | 193.9681 | 0.2339%
711 | 10-79 | -78.7971 | 10.1171 | 1276.5415 | 70.1513 | 92.439 | 129.409 | 161.0872 | 193.9373 | 0.2353%
712 | 10-79 | -79.0685 | 10.1171 | 1294.0462 | 71.1273 | 93.27 | 129.9783 | 161.4579 | 194.178 | 0.2377%
713 | 10-79.5 | -79.3398 | 10.1171 | 1311.5712 | 72.0406 | 94.0645 | 130.5603 | 161.8759 | 194.4842 | 0.2403%
714 | 10-79.5 | -79.6111 | 10.1171 | 1329.1157 | 72.8496 | 94.7813 | 131.1093 | 162.2913 | 194.7963 | 0.2428%
715 | 10-80 | -79.8824 | 10.1171 | 1346.679 | 73.5911 | 95.4671 | 131.6908 | 162.7868 | 195.2095 | 0.2456%
716 | 10-80 | -80.1537 | 10.1171 | 1364.2602 | 74.1652 | 96.0257 | 132.2042 | 163.2554 | 195.6346 | 0.2482%
717 | 10-80.5 | -80.4251 | 10.1171 | 1381.8588 | 74.5079 | 96.3895 | 132.5653 | 163.5879 | 195.9529 | 0.25%
718 | 10-80.5 | -80.6964 | 10.1171 | 1399.474 | 74.5983 | 96.5337 | 132.7299 | 163.7156 | 196.0751 | 0.2508%
719 | 10-81 | -80.9677 | 10.1171 | 1417.1052 | 74.3561 | 96.3598 | 132.5798 | 163.5094 | 195.9078 | 0.2498%
720 | 10-81 | -81.239 | 10.1171 | 1434.7518 | 73.8279 | 95.9154 | 132.1543 | 163.0215 | 195.5039 | 0.2474%
721 | 10-81.5 | -81.5104 | 10.1171 | 1452.4132 | 73.0967 | 95.2718 | 131.5371 | 162.3542 | 194.9407 | 0.2442%
722 | 10-82 | -81.7817 | 10.1171 | 1470.0888 | 72.1022 | 94.311 | 130.4986 | 161.2826 | 193.9405 | 0.239%
723 | 10-82 | -82.053 | 10.1171 | 1487.7781 | 70.8763 | 93.0411 | 128.961 | 159.6805 | 192.3388 | 0.2317%
724 | 10-82.5 | -82.3243 | 10.1171 | 1505.4807 | 69.4661 | 91.5197 | 126.9727 | 157.5188 | 190.0908 | 0.2224%
725 | 10-82.5 | -82.5956 | 10.1171 | 1523.1959 | 67.9765 | 89.8621 | 124.7799 | 155.1097 | 187.5949 | 0.2126%
726 | 10-83 | -82.867 | 10.1171 | 1540.9235 | 66.5475 | 88.218 | 122.5895 | 152.7033 | 185.1404 | 0.2032%
727 | 10-83 | -83.1383 | 10.1171 | 1558.6628 | 65.2444 | 86.6674 | 120.5036 | 150.4214 | 182.8423 | 0.1947%
728 | 10-83.5 | -83.4096 | 10.1171 | 1576.4136 | 63.9825 | 85.1004 | 118.318 | 147.9474 | 180.3049 | 0.1859%
729 | 10-83.5 | -83.6809 | 10.1171 | 1594.1754 | 62.7751 | 83.5276 | 116.0526 | 145.3186 | 177.5608 | 0.1769%
730 | 10-84 | -83.9522 | 10.1171 | 1611.9478 | 61.6639 | 82.0003 | 113.7701 | 142.6114 | 174.6632 | 0.168%
731 | 10-84 | -84.2236 | 10.1171 | 1629.7305 | 60.6775 | 80.5722 | 111.5614 | 139.9573 | 171.7637 | 0.1594%
732 | 10-84.5 | -84.4949 | 10.1171 | 1647.523 | 59.8542 | 79.3169 | 109.5379 | 137.493 | 168.9955 | 0.1516%
733 | 10-85 | -84.7662 | 10.1171 | 1665.3252 | 59.1869 | 78.2348 | 107.7257 | 135.2744 | 166.4381 | 0.1446%
734 | 10-85 | -85.0375 | 10.1171 | 1683.1366 | 58.6461 | 77.3008 | 106.0658 | 133.2174 | 164.0219 | 0.1382%
735 | 10-85.5 | -85.3089 | 10.1171 | 1700.9569 | 58.2956 | 76.6679 | 104.8159 | 131.5878 | 162.0822 | 0.1332%
736 | 10-85.5 | -85.5802 | 10.1171 | 1718.7858 | 58.1424 | 76.3602 | 104.0542 | 130.4978 | 160.7532 | 0.1298%
737 | 10-86 | -85.8515 | 10.1171 | 1736.6231 | 58.1704 | 76.2917 | 103.6974 | 129.9081 | 159.9729 | 0.1279%
738 | 10-86 | -86.1228 | 10.1171 | 1754.4684 | 58.3362 | 76.3687 | 103.5516 | 129.579 | 159.422 | 0.1267%
739 | 10-86.5 | -86.3941 | 10.1171 | 1772.3215 | 58.669 | 76.5948 | 103.6071 | 129.4951 | 159.0472 | 0.1259%
740 | 10-86.5 | -86.6655 | 10.1171 | 1790.1822 | 59.1277 | 76.9411 | 103.8132 | 129.5719 | 158.733 | 0.1254%
741 | 10-87 | -86.9368 | 10.1171 | 1808.0502 | 59.8285 | 77.5756 | 104.4457 | 130.165 | 158.9204 | 0.1263%
742 | 10-87 | -87.2081 | 10.1171 | 1825.9253 | 60.8831 | 78.6247 | 105.6316 | 131.3566 | 159.6908 | 0.1288%
743 | 10-87.5 | -87.4794 | 10.1171 | 1843.8072 | 62.2579 | 80.0494 | 107.2937 | 133.0263 | 160.953 | 0.1329%
744 | 10-88 | -87.7507 | 10.1171 | 1861.6957 | 63.8702 | 81.7253 | 109.2338 | 134.9374 | 162.4795 | 0.1379%
745 | 10-88 | -88.0221 | 10.1171 | 1879.5906 | 65.7492 | 83.6805 | 111.4809 | 137.1043 | 164.2868 | 0.1441%
746 | 10-88.5 | -88.2934 | 10.1171 | 1897.4918 | 67.9252 | 85.9516 | 114.0561 | 139.5542 | 166.3981 | 0.1517%
747 | 10-88.5 | -88.5647 | 10.1171 | 1915.3989 | 70.3315 | 88.4703 | 116.8978 | 142.2711 | 168.7984 | 0.1609%
748 | 10-89 | -88.836 | 10.1171 | 1933.3119 | 72.9448 | 91.1875 | 119.9477 | 145.201 | 171.4393 | 0.1719%
749 | 10-89 | -89.1074 | 10.1171 | 1951.2305 | 75.7545 | 94.1137 | 123.1946 | 148.329 | 174.3121 | 0.1849%
750 | 10-89.5 | -89.3787 | 10.1171 | 1969.1546 | 78.7636 | 97.3191 | 126.6878 | 151.7196 | 177.5165 | 0.2006%
751 | 10-89.5 | -89.65 | 10.1171 | 1987.084 | 81.7531 | 100.5545 | 130.1589 | 155.0612 | 180.6951 | 0.218%
752 | 10-90 | -89.9213 | 10.1171 | 2005.0185 | 84.7028 | 103.8172 | 133.601 | 158.337 | 183.8569 | 0.2372%
753 | 10-90 | -90.1926 | 10.1171 | 2022.9579 | 87.7031 | 107.1669 | 137.1034 | 161.6769 | 187.1935 | 0.2593%
754 | 10-90.5 | -90.464 | 10.1171 | 2040.9022 | 90.7004 | 110.5177 | 140.5818 | 165.0255 | 190.628 | 0.2841%
755 | 10-90.5 | -90.7353 | 10.1171 | 2058.8512 | 93.5658 | 113.7513 | 143.9164 | 168.2825 | 194.019 | 0.3109%
756 | 10-50 | -50.0371 | 10.3884 | 794.0407 | 83.4478 | 107.5761 | 146.8155 | 176.335 | 206.4849 | 0.3243%
757 | 10-50.5 | -50.3084 | 10.3884 | 777.6659 | 83.255 | 107.3835 | 146.6032 | 176.2027 | 206.467 | 0.3232%
758 | 10-50.5 | -50.5797 | 10.3884 | 761.3769 | 83.0492 | 107.1649 | 146.3654 | 176.0457 | 206.4141 | 0.3219%
759 | 10-51 | -50.851 | 10.3884 | 745.1792 | 82.8396 | 106.9344 | 146.1249 | 175.8873 | 206.3553 | 0.3205%
760 | 10-51 | -51.1224 | 10.3884 | 729.0789 | 82.6407 | 106.7105 | 145.905 | 175.7522 | 206.3247 | 0.3194%
761 | 10-51.5 | -51.3937 | 10.3884 | 713.0827 | 82.4461 | 106.4832 | 145.6832 | 175.6035 | 206.2687 | 0.3181%
762 | 10-51.5 | -51.665 | 10.3884 | 697.1977 | 82.2747 | 106.2783 | 145.4884 | 175.4728 | 206.2234 | 0.317%
763 | 10-52 | -51.9363 | 10.3884 | 681.4318 | 82.1418 | 106.1148 | 145.3433 | 175.3879 | 206.2208 | 0.3163%
764 | 10-52 | -52.2077 | 10.3884 | 665.7934 | 82.0298 | 105.9735 | 145.2296 | 175.3359 | 206.2412 | 0.3157%
765 | 10-52.5 | -52.479 | 10.3884 | 650.2917 | 81.9526 | 105.8696 | 145.1579 | 175.3304 | 206.31 | 0.3154%
766 | 10-53 | -52.7503 | 10.3884 | 634.9368 | 81.9222 | 105.8159 | 145.1381 | 175.3795 | 206.441 | 0.3155%
767 | 10-53 | -53.0216 | 10.3884 | 619.7396 | 81.9015 | 105.7673 | 145.11 | 175.4087 | 206.5432 | 0.3155%
768 | 10-53.5 | -53.2929 | 10.3884 | 604.712 | 81.9186 | 105.7539 | 145.1068 | 175.4569 | 206.6684 | 0.3158%
769 | 10-53.5 | -53.5643 | 10.3884 | 589.867 | 81.9951 | 105.7968 | 145.1471 | 175.5422 | 206.8373 | 0.3163%
770 | 10-54 | -53.8356 | 10.3884 | 575.2187 | 82.0975 | 105.8625 | 145.1971 | 175.6267 | 206.9997 | 0.317%
771 | 10-54 | -54.1069 | 10.3884 | 560.7826 | 82.2596 | 105.9835 | 145.2778 | 175.7345 | 207.1896 | 0.3179%
772 | 10-54.5 | -54.3782 | 10.3884 | 546.5755 | 82.4986 | 106.1738 | 145.3945 | 175.8676 | 207.4078 | 0.3192%
773 | 10-54.5 | -54.6495 | 10.3884 | 532.6157 | 82.7732 | 106.3799 | 145.4812 | 175.9434 | 207.5395 | 0.3203%
774 | 10-55 | -54.9209 | 10.3884 | 518.9233 | 83.0988 | 106.6189 | 145.5634 | 175.9996 | 207.638 | 0.3214%
775 | 10-55 | -55.1922 | 10.3884 | 505.5199 | 83.4764 | 106.8922 | 145.6434 | 176.0435 | 207.715 | 0.3226%
776 | 10-55.5 | -55.4635 | 10.3884 | 492.4292 | 83.867 | 107.1635 | 145.69 | 176.0418 | 207.7347 | 0.3237%
777 | 10-55.5 | -55.7348 | 10.3884 | 479.6768 | 84.2898 | 107.4557 | 145.7265 | 176.0141 | 207.7221 | 0.3248%
778 | 10-56 | -56.0061 | 10.3884 | 467.2904 | 84.7408 | 107.7688 | 145.7554 | 175.9613 | 207.6764 | 0.3258%
779 | 10-56.5 | -56.2775 | 10.3884 | 455.2999 | 85.1708 | 108.0531 | 145.7324 | 175.8364 | 207.5383 | 0.3265%
780 | 10-56.5 | -56.5488 | 10.3884 | 443.7374 | 85.6169 | 108.3562 | 145.7241 | 175.7201 | 207.4048 | 0.3273%
781 | 10-57 | -56.8201 | 10.3884 | 432.6372 | 86.0697 | 108.6736 | 145.7338 | 175.6188 | 207.2838 | 0.3282%
782 | 10-57 | -57.0914 | 10.3884 | 422.0359 | 86.4829 | 108.9622 | 145.7311 | 175.5007 | 207.1335 | 0.3289%
783 | 10-57.5 | -57.3628 | 10.3884 | 411.9719 | 86.8917 | 109.2609 | 145.7583 | 175.413 | 207.0123 | 0.3298%
784 | 10-57.5 | -57.6341 | 10.3884 | 402.4856 | 87.2792 | 109.5557 | 145.8084 | 175.352 | 206.9176 | 0.3307%
785 | 10-58 | -57.9054 | 10.3884 | 393.6187 | 87.602 | 109.8017 | 145.8423 | 175.2809 | 206.8067 | 0.3314%
786 | 10-58 | -58.1767 | 10.3884 | 385.4141 | 87.9036 | 110.0574 | 145.9339 | 175.2903 | 206.7979 | 0.3325%
787 | 10-58.5 | -58.448 | 10.3884 | 377.9148 | 88.1629 | 110.303 | 146.0652 | 175.3598 | 206.8679 | 0.3338%
788 | 10-58.5 | -58.7194 | 10.3884 | 371.1637 | 88.3256 | 110.4881 | 146.1761 | 175.4184 | 206.9335 | 0.3347%
789 | 10-59 | -58.9907 | 10.3884 | 365.2022 | 88.4275 | 110.6472 | 146.2978 | 175.5027 | 207.0302 | 0.3357%
790 | 10-59.5 | -59.262 | 10.3884 | 360.0695 | 88.4446 | 110.7482 | 146.3916 | 175.5719 | 207.1217 | 0.3363%
791 | 10-59.5 | -59.5333 | 10.3884 | 355.8016 | 88.3404 | 110.7382 | 146.3878 | 175.5482 | 207.1404 | 0.3361%
792 | 10-60 | -59.8046 | 10.3884 | 352.4299 | 88.1597 | 110.6633 | 146.3314 | 175.4815 | 207.146 | 0.3354%
793 | 10-60 | -60.076 | 10.3884 | 349.9802 | 87.8779 | 110.4877 | 146.1753 | 175.3251 | 207.0639 | 0.334%
794 | 10-60.5 | -60.3473 | 10.3884 | 348.472 | 87.464 | 110.1637 | 145.8488 | 175.0033 | 206.7896 | 0.3314%
795 | 10-60.5 | -60.6186 | 10.3884 | 347.9176 | 86.9539 | 109.7272 | 145.3781 | 174.5512 | 206.3727 | 0.3277%
796 | 10-61 | -60.8899 | 10.3884 | 348.3215 | 86.4016 | 109.2575 | 144.8955 | 174.1167 | 205.9723 | 0.3241%
797 | 10-61 | -61.1613 | 10.3884 | 349.6804 | 85.8882 | 108.873 | 144.5944 | 173.9082 | 205.8087 | 0.3217%
798 | 10-61.5 | -61.4326 | 10.3884 | 351.9832 | 85.448 | 108.6172 | 144.5221 | 173.9524 | 205.9303 | 0.3208%
799 | 10-61.5 | -61.7039 | 10.3884 | 355.2116 | 84.9999 | 108.3626 | 144.4733 | 174.0262 | 206.1094 | 0.32%
800 | 10-62 | -61.9752 | 10.3884 | 359.3407 | 84.4654 | 107.9919 | 144.2559 | 173.918 | 206.1419 | 0.3182%
801 | 10-62 | -62.2465 | 10.3884 | 364.3397 | 83.8938 | 107.5552 | 143.9374 | 173.7035 | 206.1219 | 0.3159%
802 | 10-62.5 | -62.5179 | 10.3884 | 370.1735 | 83.282 | 107.0632 | 143.5374 | 173.3847 | 206.0073 | 0.3131%
803 | 10-63 | -62.7892 | 10.3884 | 376.8032 | 82.6505 | 106.5486 | 143.1028 | 173.0112 | 205.7936 | 0.3101%
804 | 10-63 | -63.0605 | 10.3884 | 384.1877 | 82.0352 | 106.0574 | 142.7022 | 172.6655 | 205.5583 | 0.3072%
805 | 10-63.5 | -63.3318 | 10.3884 | 392.2843 | 81.431 | 105.5763 | 142.3218 | 172.3325 | 205.2972 | 0.3044%
806 | 10-63.5 | -63.6031 | 10.3884 | 401.05 | 80.8542 | 105.131 | 141.9931 | 172.0437 | 205.0734 | 0.3019%
807 | 10-64 | -63.8745 | 10.3884 | 410.4417 | 80.3373 | 104.7702 | 141.7867 | 171.8781 | 204.9993 | 0.3002%
808 | 10-64 | -64.1458 | 10.3884 | 420.4176 | 79.7951 | 104.365 | 141.4998 | 171.6269 | 204.8359 | 0.2981%
809 | 10-64.5 | -64.4171 | 10.3884 | 430.9371 | 79.1249 | 103.7641 | 140.8859 | 170.996 | 204.2907 | 0.2941%
810 | 10-64.5 | -64.6884 | 10.3884 | 441.9614 | 78.2446 | 102.8609 | 139.7733 | 169.754 | 203.1588 | 0.2873%
811 | 10-65 | -64.9598 | 10.3884 | 453.4535 | 77.2994 | 101.8545 | 138.4896 | 168.338 | 201.8012 | 0.2797%
812 | 10-65 | -65.2311 | 10.3884 | 465.379 | 76.4321 | 100.9592 | 137.3948 | 167.1479 | 200.5994 | 0.2733%
813 | 10-65.5 | -65.5024 | 10.3884 | 477.7052 | 75.7343 | 100.3131 | 136.7191 | 166.3808 | 199.7866 | 0.2691%
814 | 10-66 | -65.7737 | 10.3884 | 490.402 | 75.0962 | 99.7497 | 136.1895 | 165.7591 | 199.0564 | 0.2656%
815 | 10-66 | -66.045 | 10.3884 | 503.4412 | 74.4759 | 99.1948 | 135.6862 | 165.1881 | 198.354 | 0.2623%
816 | 10-66.5 | -66.3164 | 10.3884 | 516.7971 | 73.8654 | 98.6369 | 135.1935 | 164.6567 | 197.7227 | 0.2592%
817 | 10-66.5 | -66.5877 | 10.3884 | 530.4456 | 73.1554 | 97.9167 | 134.4859 | 163.917 | 196.8688 | 0.2552%
818 | 10-67 | -66.859 | 10.3884 | 544.3647 | 72.3217 | 97.0081 | 133.4983 | 162.9086 | 195.727 | 0.2499%
819 | 10-67 | -67.1303 | 10.3884 | 558.5342 | 71.3687 | 95.92 | 132.23 | 161.635 | 194.2969 | 0.2435%
820 | 10-67.5 | -67.4016 | 10.3884 | 572.9355 | 70.3697 | 94.756 | 130.8352 | 160.2132 | 192.7422 | 0.2367%
821 | 10-67.5 | -67.673 | 10.3884 | 587.5515 | 69.4165 | 93.6597 | 129.5467 | 158.8622 | 191.3302 | 0.2306%
822 | 10-68 | -67.9443 | 10.3884 | 602.3665 | 68.5455 | 92.6945 | 128.4708 | 157.7211 | 190.1672 | 0.2256%
823 | 10-68 | -68.2156 | 10.3884 | 617.3663 | 67.8767 | 91.9847 | 127.8253 | 157.0831 | 189.4415 | 0.2225%
824 | 10-68.5 | -68.4869 | 10.3884 | 632.5377 | 67.2759 | 91.3415 | 127.2848 | 156.5504 | 188.793 | 0.22%
825 | 10-69 | -68.7583 | 10.3884 | 647.8686 | 66.6752 | 90.671 | 126.6804 | 155.9243 | 188.0587 | 0.2171%
826 | 10-69 | -69.0296 | 10.3884 | 663.3479 | 66.0177 | 89.9022 | 125.9538 | 155.254 | 187.2573 | 0.214%
827 | 10-69.5 | -69.3009 | 10.3884 | 678.9654 | 65.4018 | 89.1956 | 125.3672 | 154.8221 | 186.6907 | 0.2117%
828 | 10-69.5 | -69.5722 | 10.3884 | 694.7119 | 64.8657 | 88.6113 | 125.0164 | 154.7005 | 186.4395 | 0.2105%
829 | 10-70 | -69.8435 | 10.3884 | 710.5786 | 64.308 | 87.9817 | 124.6086 | 154.5358 | 186.1366 | 0.2091%
830 | 10-70 | -70.1149 | 10.3884 | 726.5579 | 63.8342 | 87.4689 | 124.3349 | 154.5673 | 186.0671 | 0.2085%
831 | 10-70.5 | -70.3862 | 10.3884 | 742.6422 | 63.4688 | 87.1106 | 124.2579 | 154.8547 | 186.292 | 0.2088%
832 | 10-70.5 | -70.6575 | 10.3884 | 758.825 | 63.2256 | 86.9362 | 124.4094 | 155.2754 | 186.7327 | 0.2099%
833 | 10-71 | -70.9288 | 10.3884 | 775.1001 | 63.0235 | 86.8407 | 124.6178 | 155.7119 | 187.2045 | 0.2111%
834 | 10-71 | -71.2001 | 10.3884 | 791.4618 | 62.8555 | 86.8106 | 124.8653 | 156.1609 | 187.6903 | 0.2124%
835 | 10-71.5 | -71.4715 | 10.3884 | 807.9047 | 62.7503 | 86.8899 | 125.2473 | 156.744 | 188.3905 | 0.2143%
836 | 10-71.5 | -71.7428 | 10.3884 | 824.424 | 62.5876 | 86.9489 | 125.5143 | 157.203 | 189.1123 | 0.216%
837 | 10-72 | -72.0141 | 10.3884 | 841.0152 | 62.3594 | 86.9595 | 125.6559 | 157.5141 | 189.7838 | 0.2172%
838 | 10-72.5 | -72.2854 | 10.3884 | 857.674 | 62.0814 | 86.8711 | 125.6699 | 157.6765 | 190.2811 | 0.2179%
839 | 10-72.5 | -72.5568 | 10.3884 | 874.3967 | 61.8125 | 86.7462 | 125.595 | 157.6843 | 190.5395 | 0.218%
840 | 10-73 | -72.8281 | 10.3884 | 891.1795 | 61.5495 | 86.5743 | 125.4067 | 157.4892 | 190.5414 | 0.2175%
841 | 10-73 | -73.0994 | 10.3884 | 908.0192 | 61.2486 | 86.2998 | 124.9835 | 156.9719 | 190.2309 | 0.216%
842 | 10-73.5 | -73.3707 | 10.3884 | 924.9126 | 61.0209 | 86.0954 | 124.6182 | 156.4826 | 189.9673 | 0.2146%
843 | 10-73.5 | -73.642 | 10.3884 | 941.8568 | 60.9052 | 86.007 | 124.4107 | 156.1116 | 189.8378 | 0.2138%
844 | 10-74 | -73.9134 | 10.3884 | 958.8491 | 60.9966 | 86.1546 | 124.5771 | 156.1314 | 190.0709 | 0.2144%
845 | 10-74 | -74.1847 | 10.3884 | 975.887 | 61.2952 | 86.5212 | 125.1105 | 156.6554 | 190.7471 | 0.2165%
846 | 10-74.5 | -74.456 | 10.3884 | 992.968 | 61.7814 | 87.0731 | 125.9528 | 157.5709 | 191.7859 | 0.2199%
847 | 10-74.5 | -74.7273 | 10.3884 | 1010.09 | 62.3703 | 87.7026 | 126.9126 | 158.6856 | 192.9943 | 0.2239%
848 | 10-75 | -74.9986 | 10.3884 | 1027.251 | 63.0478 | 88.3712 | 127.9009 | 159.8811 | 194.1851 | 0.2281%
849 | 10-75.5 | -75.27 | 10.3884 | 1044.4489 | 63.8052 | 89.0549 | 128.9019 | 161.1026 | 195.2816 | 0.2324%
850 | 10-75.5 | -75.5413 | 10.3884 | 1061.6819 | 64.6061 | 89.7246 | 129.858 | 162.261 | 196.2518 | 0.2365%
851 | 10-76 | -75.8126 | 10.3884 | 1078.9485 | 65.4447 | 90.4379 | 130.7817 | 163.3728 | 197.2221 | 0.2407%
852 | 10-76 | -76.0839 | 10.3884 | 1096.2469 | 66.2936 | 91.162 | 131.6195 | 164.3607 | 198.1561 | 0.2447%
853 | 10-76.5 | -76.3553 | 10.3884 | 1113.5756 | 67.1362 | 91.8648 | 132.3315 | 165.173 | 198.9541 | 0.2482%
854 | 10-76.5 | -76.6266 | 10.3884 | 1130.9333 | 68.0371 | 92.6199 | 133.0553 | 165.9582 | 199.6893 | 0.2518%
855 | 10-77 | -76.8979 | 10.3884 | 1148.3185 | 69.0077 | 93.4487 | 133.8297 | 166.7742 | 200.4275 | 0.2558%
856 | 10-77 | -77.1692 | 10.3884 | 1165.7302 | 70.0337 | 94.3313 | 134.6316 | 167.5992 | 201.151 | 0.2599%
857 | 10-77.5 | -77.4405 | 10.3884 | 1183.167 | 71.0499 | 95.1668 | 135.2759 | 168.1869 | 201.636 | 0.2634%
858 | 10-77.5 | -77.7119 | 10.3884 | 1200.6278 | 71.9878 | 95.8907 | 135.6921 | 168.4745 | 201.811 | 0.2657%
859 | 10-78 | -77.9832 | 10.3884 | 1218.1117 | 72.8223 | 96.4909 | 135.9001 | 168.4992 | 201.7047 | 0.267%
860 | 10-78.5 | -78.2545 | 10.3884 | 1235.6175 | 73.6517 | 97.0871 | 136.0947 | 168.4552 | 201.4957 | 0.2682%
861 | 10-78.5 | -78.5258 | 10.3884 | 1253.1444 | 74.4788 | 97.6902 | 136.3206 | 168.421 | 201.2929 | 0.2693%
862 | 10-79 | -78.7971 | 10.3884 | 1270.6915 | 75.3306 | 98.3337 | 136.6454 | 168.5088 | 201.2451 | 0.2711%
863 | 10-79 | -79.0685 | 10.3884 | 1288.2578 | 76.2355 | 99.0662 | 137.1335 | 168.8133 | 201.4506 | 0.2739%
864 | 10-79.5 | -79.3398 | 10.3884 | 1305.8428 | 77.0769 | 99.7611 | 137.6329 | 169.1595 | 201.7092 | 0.2768%
865 | 10-79.5 | -79.6111 | 10.3884 | 1323.4454 | 77.8183 | 100.3833 | 138.1056 | 169.5084 | 201.9762 | 0.2796%
866 | 10-80 | -79.8824 | 10.3884 | 1341.0651 | 78.5014 | 100.9865 | 138.6245 | 169.9544 | 202.3654 | 0.2827%
867 | 10-80 | -80.1537 | 10.3884 | 1358.7012 | 79.0266 | 101.4747 | 139.0903 | 170.3902 | 202.7845 | 0.2856%
868 | 10-80.5 | -80.4251 | 10.3884 | 1376.353 | 79.3346 | 101.7863 | 139.4242 | 170.7133 | 203.1223 | 0.2877%
869 | 10-80.5 | -80.6964 | 10.3884 | 1394.0199 | 79.41 | 101.9046 | 139.5885 | 170.8633 | 203.3008 | 0.2886%
870 | 10-81 | -80.9677 | 10.3884 | 1411.7013 | 79.1716 | 101.7386 | 139.4656 | 170.7113 | 203.225 | 0.2876%
871 | 10-81 | -81.239 | 10.3884 | 1429.3966 | 78.6605 | 101.3219 | 139.0841 | 170.2936 | 202.9258 | 0.2851%
872 | 10-81.5 | -81.5104 | 10.3884 | 1447.1053 | 77.955 | 100.7194 | 138.517 | 169.6981 | 202.4608 | 0.2816%
873 | 10-82 | -81.7817 | 10.3884 | 1464.827 | 76.9725 | 99.7764 | 137.497 | 168.6496 | 201.4862 | 0.2756%
874 | 10-82 | -82.053 | 10.3884 | 1482.5611 | 75.746 | 98.498 | 135.927 | 167.0158 | 199.8313 | 0.2669%
875 | 10-82.5 | -82.3243 | 10.3884 | 1500.3071 | 74.3292 | 96.9485 | 133.8549 | 164.7743 | 197.461 | 0.2557%
876 | 10-82.5 | -82.5956 | 10.3884 | 1518.0646 | 72.8358 | 95.2647 | 131.5681 | 162.2788 | 194.831 | 0.2439%
877 | 10-83 | -82.867 | 10.3884 | 1535.8333 | 71.4024 | 93.5964 | 129.2774 | 159.7825 | 192.2365 | 0.2327%
878 | 10-83 | -83.1383 | 10.3884 | 1553.6127 | 70.0891 | 92.0186 | 127.0821 | 157.4036 | 189.7892 | 0.2225%
879 | 10-83.5 | -83.4096 | 10.3884 | 1571.4023 | 68.8141 | 90.4307 | 124.8023 | 154.8518 | 187.1332 | 0.2121%
880 | 10-83.5 | -83.6809 | 10.3884 | 1589.202 | 67.587 | 88.8411 | 122.4607 | 152.1698 | 184.312 | 0.2016%
881 | 10-84 | -83.9522 | 10.3884 | 1607.0112 | 66.4488 | 87.2993 | 120.1165 | 149.4317 | 181.3791 | 0.1913%
882 | 10-84 | -84.2236 | 10.3884 | 1624.8296 | 65.4127 | 85.8302 | 117.8093 | 146.7168 | 178.4192 | 0.1815%
883 | 10-84.5 | -84.4949 | 10.3884 | 1642.657 | 64.5177 | 84.4988 | 115.6467 | 144.156 | 175.5595 | 0.1724%
884 | 10-85 | -84.7662 | 10.3884 | 1660.4931 | 63.7574 | 83.3057 | 113.6572 | 141.8021 | 172.8795 | 0.1641%
885 | 10-85 | -85.0375 | 10.3884 | 1678.3374 | 63.1112 | 82.2389 | 111.8106 | 139.6098 | 170.3496 | 0.1566%
886 | 10-85.5 | -85.3089 | 10.3884 | 1696.1899 | 62.6608 | 81.4749 | 110.3976 | 137.8861 | 168.3665 | 0.1508%
887 | 10-85.5 | -85.5802 | 10.3884 | 1714.05 | 62.4135 | 81.0405 | 109.5255 | 136.7603 | 167.0831 | 0.1471%
888 | 10-86 | -85.8515 | 10.3884 | 1731.9177 | 62.3397 | 80.8408 | 109.0925 | 136.1658 | 166.3958 | 0.1451%
889 | 10-86 | -86.1228 | 10.3884 | 1749.7927 | 62.385 | 80.7726 | 108.8678 | 135.8242 | 165.9297 | 0.1439%
890 | 10-86.5 | -86.3941 | 10.3884 | 1767.6747 | 62.577 | 80.8419 | 108.8397 | 135.7164 | 165.6244 | 0.1432%
891 | 10-86.5 | -86.6655 | 10.3884 | 1785.5634 | 62.8928 | 81.0376 | 108.974 | 135.7747 | 165.3829 | 0.1429%
892 | 10-87 | -86.9368 | 10.3884 | 1803.4587 | 63.4449 | 81.5258 | 109.5341 | 136.3358 | 165.6137 | 0.1441%
893 | 10-87 | -87.2081 | 10.3884 | 1821.3604 | 64.3446 | 82.4409 | 110.6538 | 137.4819 | 166.3953 | 0.1472%
894 | 10-87.5 | -87.4794 | 10.3884 | 1839.2682 | 65.5783 | 83.7477 | 112.2582 | 139.0907 | 167.6298 | 0.1518%
895 | 10-88 | -87.7507 | 10.3884 | 1857.1819 | 67.0859 | 85.3503 | 114.1967 | 140.9747 | 169.1534 | 0.1577%
896 | 10-88 | -88.0221 | 10.3884 | 1875.1014 | 68.8984 | 87.2832 | 116.4963 | 143.1577 | 170.9936 | 0.165%
897 | 10-88.5 | -88.2934 | 10.3884 | 1893.0265 | 71.0488 | 89.5906 | 119.1765 | 145.6729 | 173.1746 | 0.1743%
898 | 10-88.5 | -88.5647 | 10.3884 | 1910.9569 | 73.4621 | 92.196 | 122.1489 | 148.4701 | 175.6497 | 0.1854%
899 | 10-89 | -88.836 | 10.3884 | 1928.8925 | 76.1262 | 95.0766 | 125.3656 | 151.5128 | 178.387 | 0.1988%
900 | 10-89 | -89.1074 | 10.3884 | 1946.8332 | 79.0507 | 98.2597 | 128.8206 | 154.7945 | 181.391 | 0.2148%
901 | 10-89.5 | -89.3787 | 10.3884 | 1964.7788 | 82.2801 | 101.7964 | 132.5961 | 158.4179 | 184.8148 | 0.2347%
902 | 10-89.5 | -89.65 | 10.3884 | 1982.7291 | 85.5523 | 105.3927 | 136.377 | 162.0167 | 188.2365 | 0.2571%
903 | 10-90 | -89.9213 | 10.3884 | 2000.6839 | 88.8559 | 109.0415 | 140.1509 | 165.5708 | 191.662 | 0.2822%
904 | 10-90 | -90.1926 | 10.3884 | 2018.6432 | 92.2343 | 112.79 | 143.9933 | 169.197 | 195.2688 | 0.3114%
905 | 10-90.5 | -90.464 | 10.3884 | 2036.6068 | 95.6248 | 116.5333 | 147.7925 | 172.8131 | 198.9479 | 0.3445%
906 | 10-90.5 | -90.7353 | 10.3884 | 2054.5746 | 98.8823 | 120.122 | 151.3857 | 176.2734 | 202.5025 | 0.3803%
907 | 11-50 | -50.0371 | 10.6598 | 785.6777 | 87.8663 | 113.1754 | 153.4732 | 183.0926 | 213.1111 | 0.372%
908 | 11-50.5 | -50.3084 | 10.6598 | 769.142 | 87.6902 | 113.007 | 153.2948 | 183.0034 | 213.1461 | 0.3709%
909 | 11-50.5 | -50.5797 | 10.6598 | 752.6855 | 87.4967 | 112.8069 | 153.0842 | 182.8798 | 213.1322 | 0.3695%
910 | 11-51 | -50.851 | 10.6598 | 736.3135 | 87.2949 | 112.5889 | 152.8644 | 182.7459 | 213.1003 | 0.3681%
911 | 11-51 | -51.1224 | 10.6598 | 720.0318 | 87.0991 | 112.3716 | 152.6584 | 182.6267 | 213.0857 | 0.3667%
912 | 11-51.5 | -51.3937 | 10.6598 | 703.8467 | 86.9015 | 112.1431 | 152.4439 | 182.4863 | 213.0379 | 0.3652%
913 | 11-51.5 | -51.665 | 10.6598 | 687.765 | 86.7202 | 111.9296 | 152.2489 | 182.3563 | 212.9933 | 0.3639%
914 | 11-52 | -51.9363 | 10.6598 | 671.7942 | 86.5687 | 111.7502 | 152.0954 | 182.2638 | 212.9839 | 0.3628%
915 | 11-52 | -52.2077 | 10.6598 | 655.9424 | 86.4297 | 111.5857 | 151.9647 | 182.1941 | 212.9859 | 0.3619%
916 | 11-52.5 | -52.479 | 10.6598 | 640.2185 | 86.3175 | 111.4551 | 151.871 | 182.1667 | 213.0337 | 0.3613%
917 | 11-53 | -52.7503 | 10.6598 | 624.6321 | 86.2456 | 111.3729 | 151.8261 | 182.1929 | 213.1458 | 0.3612%
918 | 11-53 | -53.0216 | 10.6598 | 609.1938 | 86.1848 | 111.2954 | 151.7721 | 182.2 | 213.2326 | 0.3609%
919 | 11-53.5 | -53.2929 | 10.6598 | 593.9152 | 86.1616 | 111.2525 | 151.7423 | 182.2293 | 213.3512 | 0.361%
920 | 11-53.5 | -53.5643 | 10.6598 | 578.8089 | 86.1973 | 111.2647 | 151.7548 | 182.2992 | 213.5242 | 0.3614%
921 | 11-54 | -53.8356 | 10.6598 | 563.8888 | 86.2583 | 111.2994 | 151.7788 | 182.3747 | 213.7035 | 0.362%
922 | 11-54 | -54.1069 | 10.6598 | 549.1701 | 86.3783 | 111.3893 | 151.8346 | 182.4796 | 213.9238 | 0.3629%
923 | 11-54.5 | -54.3782 | 10.6598 | 534.6695 | 86.5753 | 111.5486 | 151.9268 | 182.6152 | 214.1845 | 0.3643%
924 | 11-54.5 | -54.6495 | 10.6598 | 520.4051 | 86.8083 | 111.7241 | 151.9898 | 182.696 | 214.3646 | 0.3656%
925 | 11-55 | -54.9209 | 10.6598 | 506.3971 | 87.0964 | 111.9354 | 152.0489 | 182.7587 | 214.5137 | 0.3669%
926 | 11-55 | -55.1922 | 10.6598 | 492.6672 | 87.4451 | 112.1873 | 152.1094 | 182.8121 | 214.6436 | 0.3685%
927 | 11-55.5 | -55.4635 | 10.6598 | 479.2393 | 87.8196 | 112.4472 | 152.144 | 182.8257 | 214.7188 | 0.37%
928 | 11-55.5 | -55.7348 | 10.6598 | 466.1397 | 88.2413 | 112.739 | 152.1776 | 182.822 | 214.7693 | 0.3715%
929 | 11-56 | -56.0061 | 10.6598 | 453.3968 | 88.7081 | 113.0633 | 152.2141 | 182.8029 | 214.795 | 0.3733%
930 | 11-56.5 | -56.2775 | 10.6598 | 441.0414 | 89.1686 | 113.3692 | 152.2085 | 182.7201 | 214.7341 | 0.3747%
931 | 11-56.5 | -56.5488 | 10.6598 | 429.1072 | 89.6538 | 113.7045 | 152.2265 | 182.6535 | 214.6832 | 0.3763%
932 | 11-57 | -56.8201 | 10.6598 | 417.6302 | 90.1541 | 114.065 | 152.2714 | 182.6084 | 214.6477 | 0.3781%
933 | 11-57 | -57.0914 | 10.6598 | 406.6491 | 90.6195 | 114.4031 | 152.3074 | 182.544 | 214.571 | 0.3797%
934 | 11-57.5 | -57.3628 | 10.6598 | 396.2052 | 91.0863 | 114.7579 | 152.3745 | 182.5044 | 214.5089 | 0.3815%
935 | 11-57.5 | -57.6341 | 10.6598 | 386.3421 | 91.5386 | 115.117 | 152.4676 | 182.488 | 214.4604 | 0.3834%
936 | 11-58 | -57.9054 | 10.6598 | 377.1053 | 91.9315 | 115.4346 | 152.5507 | 182.4635 | 214.3913 | 0.385%
937 | 11-58 | -58.1767 | 10.6598 | 368.542 | 92.3099 | 115.7706 | 152.6988 | 182.5246 | 214.4257 | 0.3871%
938 | 11-58.5 | -58.448 | 10.6598 | 360.7002 | 92.6534 | 116.1052 | 152.8967 | 182.6559 | 214.5486 | 0.3894%
939 | 11-58.5 | -58.7194 | 10.6598 | 353.6278 | 92.9208 | 116.3883 | 153.0919 | 182.7995 | 214.6975 | 0.3915%
940 | 11-59 | -58.9907 | 10.6598 | 347.3718 | 93.1456 | 116.6535 | 153.3138 | 182.9911 | 214.9079 | 0.3937%
941 | 11-59.5 | -59.262 | 10.6598 | 341.9772 | 93.2962 | 116.864 | 153.5162 | 183.1788 | 215.1277 | 0.3956%
942 | 11-59.5 | -59.5333 | 10.6598 | 337.4852 | 93.3232 | 116.9565 | 153.6147 | 183.2632 | 215.259 | 0.3964%
943 | 11-60 | -59.8046 | 10.6598 | 333.9321 | 93.2731 | 116.9795 | 153.6553 | 183.2964 | 215.3645 | 0.3966%
944 | 11-60 | -60.076 | 10.6598 | 331.3484 | 93.1197 | 116.8964 | 153.5918 | 183.2335 | 215.3732 | 0.3958%
945 | 11-60.5 | -60.3473 | 10.6598 | 329.7566 | 92.831 | 116.6593 | 153.3561 | 183.0043 | 215.1899 | 0.3934%
946 | 11-60.5 | -60.6186 | 10.6598 | 329.1713 | 92.4467 | 116.3103 | 152.981 | 182.6539 | 214.8791 | 0.39%
947 | 11-61 | -60.8899 | 10.6598 | 329.5977 | 92.0192 | 115.9268 | 152.5981 | 182.33 | 214.5996 | 0.3864%
948 | 11-61 | -61.1613 | 10.6598 | 331.032 | 91.6284 | 115.6256 | 152.3993 | 182.2386 | 214.5691 | 0.3843%
949 | 11-61.5 | -61.4326 | 10.6598 | 333.4612 | 91.3101 | 115.4518 | 152.4297 | 182.4025 | 214.8289 | 0.3839%
950 | 11-61.5 | -61.7039 | 10.6598 | 336.8637 | 90.9777 | 115.2726 | 152.476 | 182.5867 | 215.134 | 0.3835%
951 | 11-62 | -61.9752 | 10.6598 | 341.2105 | 90.5453 | 114.9644 | 152.3345 | 182.5614 | 215.2534 | 0.3817%
952 | 11-62 | -62.2465 | 10.6598 | 346.4659 | 90.0474 | 114.576 | 152.0645 | 182.3888 | 215.2599 | 0.379%
953 | 11-62.5 | -62.5179 | 10.6598 | 352.5893 | 89.4898 | 114.1248 | 151.7003 | 182.0934 | 215.1458 | 0.3756%
954 | 11-63 | -62.7892 | 10.6598 | 359.5365 | 88.9067 | 113.6537 | 151.3083 | 181.755 | 214.9513 | 0.3719%
955 | 11-63 | -63.0605 | 10.6598 | 367.2606 | 88.3461 | 113.2232 | 150.9718 | 181.4768 | 214.783 | 0.3686%
956 | 11-63.5 | -63.3318 | 10.6598 | 375.7137 | 87.7973 | 112.8144 | 150.6647 | 181.2253 | 214.6097 | 0.3656%
957 | 11-63.5 | -63.6031 | 10.6598 | 384.8477 | 87.2734 | 112.4448 | 150.4096 | 181.018 | 214.4729 | 0.3629%
958 | 11-64 | -63.8745 | 10.6598 | 394.6155 | 86.808 | 112.1631 | 150.2754 | 180.9306 | 214.4795 | 0.3611%
959 | 11-64 | -64.1458 | 10.6598 | 404.971 | 86.3149 | 111.8384 | 150.0593 | 180.7556 | 214.3942 | 0.3588%
960 | 11-64.5 | -64.4171 | 10.6598 | 415.8705 | 85.6916 | 111.3197 | 149.5157 | 180.2009 | 213.9276 | 0.3543%
961 | 11-64.5 | -64.6884 | 10.6598 | 427.2722 | 84.8572 | 110.5016 | 148.4737 | 179.0361 | 212.8762 | 0.3465%
962 | 11-65 | -64.9598 | 10.6598 | 439.1371 | 83.9541 | 109.5777 | 147.256 | 177.6912 | 211.5912 | 0.3378%
963 | 11-65 | -65.2311 | 10.6598 | 451.4285 | 83.1287 | 108.7649 | 146.2278 | 176.5741 | 210.466 | 0.3305%
964 | 11-65.5 | -65.5024 | 10.6598 | 464.1127 | 82.4774 | 108.2062 | 145.6278 | 175.8944 | 209.752 | 0.3258%
965 | 11-66 | -65.7737 | 10.6598 | 477.1582 | 81.8872 | 107.7295 | 145.1776 | 175.3671 | 209.1328 | 0.322%
966 | 11-66 | -66.045 | 10.6598 | 490.5362 | 81.3071 | 107.2511 | 144.741 | 174.8726 | 208.5165 | 0.3183%
967 | 11-66.5 | -66.3164 | 10.6598 | 504.2203 | 80.7231 | 106.7529 | 144.2896 | 174.3808 | 207.9181 | 0.3146%
968 | 11-66.5 | -66.5877 | 10.6598 | 518.1861 | 80.0252 | 106.0704 | 143.5971 | 173.6425 | 207.0425 | 0.3096%
969 | 11-67 | -66.859 | 10.6598 | 532.4116 | 79.1947 | 105.1813 | 142.6094 | 172.6148 | 205.8507 | 0.3029%
970 | 11-67 | -67.1303 | 10.6598 | 546.8763 | 78.2398 | 104.1023 | 141.3335 | 171.3132 | 204.3605 | 0.2949%
971 | 11-67.5 | -67.4016 | 10.6598 | 561.5619 | 77.2327 | 102.937 | 139.9245 | 169.8568 | 202.7399 | 0.2864%
972 | 11-67.5 | -67.673 | 10.6598 | 576.4513 | 76.2661 | 101.8302 | 138.6151 | 168.4636 | 201.2537 | 0.2786%
973 | 11-68 | -67.9443 | 10.6598 | 591.5293 | 75.377 | 100.8464 | 137.5117 | 167.2718 | 200.0061 | 0.2721%
974 | 11-68 | -68.2156 | 10.6598 | 606.7817 | 74.6917 | 100.1252 | 136.8488 | 166.6004 | 199.225 | 0.268%
975 | 11-68.5 | -68.4869 | 10.6598 | 622.1957 | 74.0793 | 99.484 | 136.3074 | 166.0608 | 198.5626 | 0.2647%
976 | 11-69 | -68.7583 | 10.6598 | 637.7596 | 73.4731 | 98.8305 | 135.7209 | 165.4572 | 197.8596 | 0.2612%
977 | 11-69 | -69.0296 | 10.6598 | 653.4626 | 72.7811 | 98.0287 | 134.9687 | 164.7496 | 197.0081 | 0.2571%
978 | 11-69.5 | -69.3009 | 10.6598 | 669.2949 | 72.1038 | 97.2422 | 134.3152 | 164.2232 | 196.3133 | 0.2536%
979 | 11-69.5 | -69.5722 | 10.6598 | 685.2475 | 71.4811 | 96.534 | 133.8584 | 163.9525 | 195.8585 | 0.2511%
980 | 11-70 | -69.8435 | 10.6598 | 701.3123 | 70.8352 | 95.7759 | 133.3399 | 163.6318 | 195.3419 | 0.2484%
981 | 11-70 | -70.1149 | 10.6598 | 717.4816 | 70.2725 | 95.131 | 132.9521 | 163.5023 | 195.0508 | 0.2466%
982 | 11-70.5 | -70.3862 | 10.6598 | 733.7485 | 69.8192 | 94.6395 | 132.7599 | 163.6268 | 195.051 | 0.2459%
983 | 11-70.5 | -70.6575 | 10.6598 | 750.1067 | 69.5134 | 94.3758 | 132.8357 | 163.9404 | 195.3444 | 0.2464%
984 | 11-71 | -70.9288 | 10.6598 | 766.5503 | 69.2754 | 94.2359 | 133.0072 | 164.3239 | 195.7428 | 0.2474%
985 | 11-71 | -71.2001 | 10.6598 | 783.0739 | 69.0956 | 94.2009 | 133.2514 | 164.7664 | 196.2182 | 0.2487%
986 | 11-71.5 | -71.4715 | 10.6598 | 799.6725 | 68.9739 | 94.2621 | 133.6159 | 165.321 | 196.8736 | 0.2506%
987 | 11-71.5 | -71.7428 | 10.6598 | 816.3416 | 68.7835 | 94.2738 | 133.8341 | 165.7025 | 197.474 | 0.2519%
988 | 11-72 | -72.0141 | 10.6598 | 833.0768 | 68.5169 | 94.2105 | 133.8981 | 165.8914 | 197.9549 | 0.2526%
989 | 11-72.5 | -72.2854 | 10.6598 | 849.8743 | 68.1965 | 94.0436 | 133.8313 | 165.9302 | 198.2637 | 0.2527%
990 | 11-72.5 | -72.5568 | 10.6598 | 866.7304 | 67.9159 | 93.8997 | 133.7345 | 165.9018 | 198.4613 | 0.2525%
991 | 11-73 | -72.8281 | 10.6598 | 883.6417 | 67.6707 | 93.7656 | 133.581 | 165.7549 | 198.5255 | 0.252%
992 | 11-73 | -73.0994 | 10.6598 | 900.6052 | 67.4096 | 93.5686 | 133.2319 | 165.3438 | 198.3603 | 0.2506%
993 | 11-73.5 | -73.3707 | 10.6598 | 917.6178 | 67.2199 | 93.4423 | 132.9452 | 164.97 | 198.2591 | 0.2495%
994 | 11-73.5 | -73.642 | 10.6598 | 934.677 | 67.1404 | 93.4329 | 132.8209 | 164.7241 | 198.3086 | 0.2491%
995 | 11-74 | -73.9134 | 10.6598 | 951.7801 | 67.2654 | 93.6589 | 133.0732 | 164.875 | 198.732 | 0.2503%
996 | 11-74 | -74.1847 | 10.6598 | 968.9248 | 67.5711 | 94.0593 | 133.6544 | 165.4781 | 199.5278 | 0.2531%
997 | 11-74.5 | -74.456 | 10.6598 | 986.109 | 68.0349 | 94.5939 | 134.499 | 166.4084 | 200.5966 | 0.2571%
998 | 11-74.5 | -74.7273 | 10.6598 | 1003.3306 | 68.5684 | 95.1467 | 135.4043 | 167.4545 | 201.715 | 0.2615%
999 | 11-75 | -74.9986 | 10.6598 | 1020.5876 | 69.1862 | 95.7312 | 136.3269 | 168.5646 | 202.7911 | 0.2661%
1000 | 11-75.5 | -75.27 | 10.6598 | 1037.8784 | 69.8825 | 96.3297 | 137.2597 | 169.6988 | 203.7731 | 0.2707%
1001 | 11-75.5 | -75.5413 | 10.6598 | 1055.2011 | 70.6239 | 96.9201 | 138.1556 | 170.7865 | 204.6598 | 0.2753%
1002 | 11-76 | -75.8126 | 10.6598 | 1072.5543 | 71.3981 | 97.5377 | 139.0012 | 171.8011 | 205.5076 | 0.2798%
1003 | 11-76 | -76.0839 | 10.6598 | 1089.9364 | 72.1782 | 98.1525 | 139.7463 | 172.6714 | 206.2903 | 0.284%
1004 | 11-76.5 | -76.3553 | 10.6598 | 1107.3462 | 72.9497 | 98.7399 | 140.3598 | 173.3599 | 206.931 | 0.2877%
1005 | 11-76.5 | -76.6266 | 10.6598 | 1124.7822 | 73.7842 | 99.3885 | 140.9953 | 174.0401 | 207.5406 | 0.2916%
1006 | 11-77 | -76.8979 | 10.6598 | 1142.2433 | 74.6851 | 100.106 | 141.6766 | 174.7472 | 208.1516 | 0.2958%
1007 | 11-77 | -77.1692 | 10.6598 | 1159.7282 | 75.6282 | 100.8613 | 142.3627 | 175.4338 | 208.71 | 0.3002%
1008 | 11-77.5 | -77.4405 | 10.6598 | 1177.236 | 76.5469 | 101.5557 | 142.8672 | 175.8529 | 208.9928 | 0.3037%
1009 | 11-77.5 | -77.7119 | 10.6598 | 1194.7656 | 77.3828 | 102.1366 | 143.1396 | 175.9708 | 208.9696 | 0.3059%
1010 | 11-78 | -77.9832 | 10.6598 | 1212.3161 | 78.125 | 102.6092 | 143.2265 | 175.8626 | 208.7229 | 0.307%
1011 | 11-78.5 | -78.2545 | 10.6598 | 1229.8864 | 78.8791 | 103.107 | 143.3384 | 175.7478 | 208.47 | 0.3083%
1012 | 11-78.5 | -78.5258 | 10.6598 | 1247.4758 | 79.6341 | 103.6276 | 143.5005 | 175.6762 | 208.2787 | 0.3098%
1013 | 11-79 | -78.7971 | 10.6598 | 1265.0835 | 80.4025 | 104.1879 | 143.7566 | 175.7237 | 208.2432 | 0.3119%
1014 | 11-79 | -79.0685 | 10.6598 | 1282.7086 | 81.2061 | 104.8261 | 144.1563 | 175.9601 | 208.4215 | 0.315%
1015 | 11-79.5 | -79.3398 | 10.6598 | 1300.3504 | 81.9441 | 105.4271 | 144.5651 | 176.2321 | 208.6416 | 0.3182%
1016 | 11-79.5 | -79.6111 | 10.6598 | 1318.0083 | 82.5895 | 105.9604 | 144.952 | 176.5082 | 208.8638 | 0.3211%
1017 | 11-80 | -79.8824 | 10.6598 | 1335.6816 | 83.1834 | 106.4772 | 145.3858 | 176.8764 | 209.1933 | 0.3244%
1018 | 11-80 | -80.1537 | 10.6598 | 1353.3696 | 83.6338 | 106.8873 | 145.7773 | 177.2422 | 209.5543 | 0.3273%
1019 | 11-80.5 | -80.4251 | 10.6598 | 1371.0718 | 83.8917 | 107.1455 | 146.0671 | 177.5313 | 209.8762 | 0.3294%
1020 | 11-80.5 | -80.6964 | 10.6598 | 1388.7877 | 83.9499 | 107.2455 | 146.2345 | 177.7089 | 210.1183 | 0.3304%
1021 | 11-81 | -80.9677 | 10.6598 | 1406.5166 | 83.7212 | 107.0855 | 146.1528 | 177.6311 | 210.1627 | 0.3297%
1022 | 11-81 | -81.239 | 10.6598 | 1424.258 | 83.234 | 106.6843 | 145.8261 | 177.2994 | 209.9909 | 0.3271%
1023 | 11-81.5 | -81.5104 | 10.6598 | 1442.0115 | 82.5552 | 106.1032 | 145.308 | 176.7747 | 209.6235 | 0.3232%
1024 | 11-82 | -81.7817 | 10.6598 | 1459.7767 | 81.5771 | 105.1464 | 144.2905 | 175.727 | 208.6436 | 0.3161%
1025 | 11-82 | -82.053 | 10.6598 | 1477.553 | 80.3427 | 103.8246 | 142.6856 | 174.0383 | 206.9017 | 0.3057%
1026 | 11-82.5 | -82.3243 | 10.6598 | 1495.3401 | 78.9219 | 102.2164 | 140.5347 | 171.7092 | 204.3954 | 0.2925%
1027 | 11-82.5 | -82.5956 | 10.6598 | 1513.1376 | 77.4439 | 100.4887 | 138.1746 | 169.1435 | 201.6504 | 0.2786%
1028 | 11-83 | -82.867 | 10.6598 | 1530.945 | 76.0312 | 98.7842 | 135.8093 | 166.583 | 198.948 | 0.2655%
1029 | 11-83 | -83.1383 | 10.6598 | 1548.762 | 74.7313 | 97.1686 | 133.5284 | 164.1319 | 196.3847 | 0.2535%
1030 | 11-83.5 | -83.4096 | 10.6598 | 1566.5883 | 73.4678 | 95.5526 | 131.1788 | 161.5278 | 193.6457 | 0.2414%
1031 | 11-83.5 | -83.6809 | 10.6598 | 1584.4235 | 72.2403 | 93.9392 | 128.7788 | 158.8084 | 190.7687 | 0.2294%
1032 | 11-84 | -83.9522 | 10.6598 | 1602.2673 | 71.0871 | 92.3723 | 126.3807 | 156.0394 | 187.7987 | 0.2177%
1033 | 11-84 | -84.2236 | 10.6598 | 1620.1194 | 70.0049 | 90.844 | 123.9683 | 153.2459 | 184.7504 | 0.2062%
1034 | 11-84.5 | -84.4949 | 10.6598 | 1637.9795 | 69.0394 | 89.425 | 121.6569 | 150.5689 | 181.7665 | 0.1956%
1035 | 11-85 | -84.7662 | 10.6598 | 1655.8473 | 68.1875 | 88.1197 | 119.4826 | 148.0681 | 178.9351 | 0.1858%
1036 | 11-85 | -85.0375 | 10.6598 | 1673.7226 | 67.4394 | 86.9231 | 117.4493 | 145.732 | 176.269 | 0.1769%
1037 | 11-85.5 | -85.3089 | 10.6598 | 1691.6051 | 66.8981 | 86.0416 | 115.8846 | 143.9182 | 174.2346 | 0.1702%
1038 | 11-85.5 | -85.5802 | 10.6598 | 1709.4946 | 66.57 | 85.5016 | 114.9064 | 142.7685 | 173.0008 | 0.166%
1039 | 11-86 | -85.8515 | 10.6598 | 1727.3907 | 66.4109 | 85.2096 | 114.415 | 142.1929 | 172.4285 | 0.164%
1040 | 11-86 | -86.1228 | 10.6598 | 1745.2933 | 66.3491 | 85.0351 | 114.1341 | 141.8645 | 172.0732 | 0.1629%
1041 | 11-86.5 | -86.3941 | 10.6598 | 1763.2022 | 66.4079 | 84.9849 | 114.0471 | 141.7581 | 171.8638 | 0.1623%
1042 | 11-86.5 | -86.6655 | 10.6598 | 1781.1172 | 66.583 | 85.063 | 114.1329 | 141.8205 | 171.7184 | 0.1622%
1043 | 11-87 | -86.9368 | 10.6598 | 1799.038 | 66.9809 | 85.4301 | 114.6376 | 142.3651 | 172.0081 | 0.1637%
1044 | 11-87 | -87.2081 | 10.6598 | 1816.9644 | 67.7265 | 86.2248 | 115.6974 | 143.4707 | 172.8058 | 0.1672%
1045 | 11-87.5 | -87.4794 | 10.6598 | 1834.8963 | 68.8166 | 87.4159 | 117.2387 | 145.0122 | 174.0051 | 0.1724%
1046 | 11-88 | -87.7507 | 10.6598 | 1852.8335 | 70.2118 | 88.9419 | 119.1619 | 146.8552 | 175.5109 | 0.1791%
1047 | 11-88 | -88.0221 | 10.6598 | 1870.7758 | 71.9452 | 90.8434 | 121.4909 | 149.032 | 177.3616 | 0.1876%
1048 | 11-88.5 | -88.2934 | 10.6598 | 1888.723 | 74.0525 | 93.1716 | 124.2464 | 151.5776 | 179.5821 | 0.1984%
1049 | 11-88.5 | -88.5647 | 10.6598 | 1906.6751 | 76.4514 | 95.8422 | 127.3108 | 154.4156 | 182.0938 | 0.2115%
1050 | 11-89 | -88.836 | 10.6598 | 1924.6317 | 79.1412 | 98.8577 | 130.6462 | 157.5224 | 184.88 | 0.2273%
1051 | 11-89 | -89.1074 | 10.6598 | 1942.5928 | 82.1524 | 102.2656 | 134.2561 | 160.9046 | 187.962 | 0.2465%
1052 | 11-89.5 | -89.3787 | 10.6598 | 1960.5583 | 85.5677 | 106.0872 | 138.2517 | 164.6974 | 191.5385 | 0.2707%
1053 | 11-89.5 | -89.65 | 10.6598 | 1978.5279 | 89.0918 | 109.9988 | 142.2802 | 168.4915 | 195.1371 | 0.2984%
1054 | 11-90 | -89.9213 | 10.6598 | 1996.5016 | 92.7288 | 113.9897 | 146.325 | 172.2649 | 198.7625 | 0.3302%
1055 | 11-90 | -90.1926 | 10.6598 | 2014.4792 | 96.4707 | 118.0961 | 150.4508 | 176.1243 | 202.5821 | 0.3677%
1056 | 11-90.5 | -90.464 | 10.6598 | 2032.4605 | 100.2457 | 122.1963 | 154.5217 | 179.9634 | 206.4574 | 0.4105%
1057 | 11-90.5 | -90.7353 | 10.6598 | 2050.4456 | 103.8781 | 126.1123 | 158.335 | 183.5933 | 210.1464 | 0.4572%
1058 | 11-50 | -50.0371 | 10.9311 | 777.672 | 92.0136 | 118.6131 | 159.6949 | 189.2466 | 219.1445 | 0.4229%
1059 | 11-50.5 | -50.3084 | 10.9311 | 760.9798 | 91.8458 | 118.4758 | 159.5574 | 189.2115 | 219.243 | 0.4219%
1060 | 11-50.5 | -50.5797 | 10.9311 | 744.3603 | 91.6572 | 118.3016 | 159.382 | 189.1336 | 219.2831 | 0.4206%
1061 | 11-51 | -50.851 | 10.9311 | 727.8184 | 91.4577 | 118.1047 | 159.1917 | 189.0372 | 219.2961 | 0.4191%
1062 | 11-51 | -51.1224 | 10.9311 | 711.3595 | 91.262 | 117.904 | 159.0095 | 188.9475 | 219.3178 | 0.4176%
1063 | 11-51.5 | -51.3937 | 10.9311 | 694.9896 | 91.0612 | 117.6865 | 158.8141 | 188.8314 | 219.2991 | 0.416%
1064 | 11-51.5 | -51.665 | 10.9311 | 678.7152 | 90.8736 | 117.4782 | 158.6328 | 188.7198 | 219.2778 | 0.4144%
1065 | 11-52 | -51.9363 | 10.9311 | 662.5432 | 90.7127 | 117.298 | 158.4863 | 188.6387 | 219.2861 | 0.4132%
1066 | 11-52 | -52.2077 | 10.9311 | 646.4815 | 90.5616 | 117.1268 | 158.355 | 188.571 | 219.2968 | 0.4121%
1067 | 11-52.5 | -52.479 | 10.9311 | 630.5383 | 90.4365 | 116.9868 | 158.2565 | 188.5416 | 219.351 | 0.4113%
1068 | 11-53 | -52.7503 | 10.9311 | 614.7231 | 90.3521 | 116.8942 | 158.2043 | 188.5647 | 219.4715 | 0.4109%
1069 | 11-53 | -53.0216 | 10.9311 | 599.0459 | 90.2789 | 116.804 | 158.1407 | 188.5674 | 219.5657 | 0.4105%
1070 | 11-53.5 | -53.2929 | 10.9311 | 583.5179 | 90.2425 | 116.7453 | 158.0991 | 188.5931 | 219.6965 | 0.4104%
1071 | 11-53.5 | -53.5643 | 10.9311 | 568.1513 | 90.2638 | 116.7378 | 158.0966 | 188.6604 | 219.8885 | 0.4108%
1072 | 11-54 | -53.8356 | 10.9311 | 552.9596 | 90.3095 | 116.7508 | 158.106 | 188.738 | 220.0931 | 0.4114%
1073 | 11-54 | -54.1069 | 10.9311 | 537.9577 | 90.4139 | 116.818 | 158.148 | 188.8506 | 220.3485 | 0.4124%
1074 | 11-54.5 | -54.3782 | 10.9311 | 523.1619 | 90.5954 | 116.9541 | 158.2272 | 188.9995 | 220.6545 | 0.414%
1075 | 11-54.5 | -54.6495 | 10.9311 | 508.5901 | 90.8124 | 117.1052 | 158.2765 | 189.0955 | 220.8814 | 0.4155%
1076 | 11-55 | -54.9209 | 10.9311 | 494.2623 | 91.0866 | 117.2934 | 158.3209 | 189.1722 | 221.0763 | 0.4171%
1077 | 11-55 | -55.1922 | 10.9311 | 480.2003 | 91.4268 | 117.526 | 158.3671 | 189.239 | 221.2507 | 0.4191%
1078 | 11-55.5 | -55.4635 | 10.9311 | 466.4282 | 91.8004 | 117.774 | 158.3923 | 189.2693 | 221.3709 | 0.421%
1079 | 11-55.5 | -55.7348 | 10.9311 | 452.9723 | 92.2301 | 118.0627 | 158.4239 | 189.2892 | 221.4709 | 0.4231%
1080 | 11-56 | -56.0061 | 10.9311 | 439.8618 | 92.714 | 118.3943 | 158.4671 | 189.302 | 221.5518 | 0.4256%
1081 | 11-56.5 | -56.2775 | 10.9311 | 427.1284 | 93.1998 | 118.7173 | 158.4784 | 189.2608 | 221.5532 | 0.4278%
1082 | 11-56.5 | -56.5488 | 10.9311 | 414.807 | 93.7196 | 119.0824 | 158.524 | 189.2465 | 221.5745 | 0.4304%
1083 | 11-57 | -56.8201 | 10.9311 | 402.9352 | 94.2643 | 119.486 | 158.6073 | 189.2633 | 221.6182 | 0.4333%
1084 | 11-57 | -57.0914 | 10.9311 | 391.5542 | 94.7806 | 119.8766 | 158.6873 | 189.2611 | 221.6128 | 0.4361%
1085 | 11-57.5 | -57.3628 | 10.9311 | 380.7077 | 95.3051 | 120.292 | 158.8006 | 189.2801 | 221.6139 | 0.4391%
1086 | 11-57.5 | -57.6341 | 10.9311 | 370.4429 | 95.822 | 120.72 | 158.9422 | 189.3186 | 221.6195 | 0.4423%
1087 | 11-58 | -57.9054 | 10.9311 | 360.8095 | 96.2832 | 121.1109 | 159.0746 | 189.3433 | 221.5928 | 0.4451%
1088 | 11-58 | -58.1767 | 10.9311 | 351.8591 | 96.7345 | 121.5255 | 159.274 | 189.4517 | 221.6656 | 0.4484%
1089 | 11-58.5 | -58.448 | 10.9311 | 343.6454 | 97.1554 | 121.945 | 159.5298 | 189.636 | 221.8306 | 0.4521%
1090 | 11-58.5 | -58.7194 | 10.9311 | 336.2221 | 97.5047 | 122.3221 | 159.8013 | 189.8572 | 222.0492 | 0.4556%
1091 | 11-59 | -58.9907 | 10.9311 | 329.6429 | 97.8158 | 122.6891 | 160.1152 | 190.1488 | 222.3615 | 0.4593%
1092 | 11-59.5 | -59.262 | 10.9311 | 323.9591 | 98.0573 | 123.0044 | 160.4183 | 190.4478 | 222.6991 | 0.4627%
1093 | 11-59.5 | -59.5333 | 10.9311 | 319.2185 | 98.1767 | 123.1942 | 160.6104 | 190.6323 | 222.9313 | 0.4647%
1094 | 11-60 | -59.8046 | 10.9311 | 315.4637 | 98.2212 | 123.3085 | 160.7376 | 190.7534 | 223.1189 | 0.466%
1095 | 11-60 | -60.076 | 10.9311 | 312.7302 | 98.1628 | 123.3104 | 160.7545 | 190.769 | 223.1957 | 0.4659%
1096 | 11-60.5 | -60.3473 | 10.9311 | 311.0449 | 97.9676 | 123.1521 | 160.5965 | 190.6152 | 223.0773 | 0.464%
1097 | 11-60.5 | -60.6186 | 10.9311 | 310.425 | 97.6788 | 122.8814 | 160.3027 | 190.3477 | 222.8431 | 0.4608%
1098 | 11-61 | -60.8899 | 10.9311 | 310.8766 | 97.346 | 122.5729 | 160.0027 | 190.1113 | 222.6485 | 0.4574%
1099 | 11-61 | -61.1613 | 10.9311 | 312.3954 | 97.047 | 122.3417 | 159.8866 | 190.1101 | 222.7079 | 0.4555%
1100 | 11-61.5 | -61.4326 | 10.9311 | 314.9657 | 96.8211 | 122.2379 | 160.0023 | 190.3694 | 223.0653 | 0.4556%
1101 | 11-61.5 | -61.7039 | 10.9311 | 318.5621 | 96.5787 | 122.1259 | 160.1316 | 190.6463 | 223.4628 | 0.4557%
1102 | 11-62 | -61.9752 | 10.9311 | 323.1504 | 96.23 | 121.8774 | 160.0603 | 190.6946 | 223.6479 | 0.454%
1103 | 11-62 | -62.2465 | 10.9311 | 328.6891 | 95.8071 | 121.5374 | 159.8354 | 190.5567 | 223.6682 | 0.451%
1104 | 11-62.5 | -62.5179 | 10.9311 | 335.1309 | 95.3225 | 121.129 | 159.5056 | 190.2805 | 223.546 | 0.447%
1105 | 11-63 | -62.7892 | 10.9311 | 342.425 | 94.8154 | 120.7054 | 159.1572 | 189.9764 | 223.3676 | 0.4428%
1106 | 11-63 | -63.0605 | 10.9311 | 350.5181 | 94.3362 | 120.3367 | 158.888 | 189.7691 | 223.2698 | 0.4393%
1107 | 11-63.5 | -63.3318 | 10.9311 | 359.3562 | 93.8679 | 119.9965 | 158.6601 | 189.6073 | 223.1954 | 0.4361%
1108 | 11-63.5 | -63.6031 | 10.9311 | 368.8858 | 93.4203 | 119.6974 | 158.4863 | 189.4933 | 223.1633 | 0.4334%
1109 | 11-64 | -63.8745 | 10.9311 | 379.0548 | 93.029 | 119.4881 | 158.4332 | 189.498 | 223.2719 | 0.4317%
1110 | 11-64 | -64.1458 | 10.9311 | 389.813 | 92.6068 | 119.2354 | 158.2973 | 189.4142 | 223.2872 | 0.4295%
1111 | 11-64.5 | -64.4171 | 10.9311 | 401.113 | 92.0528 | 118.7898 | 157.8351 | 188.9525 | 222.924 | 0.4247%
1112 | 11-64.5 | -64.6884 | 10.9311 | 412.9104 | 91.2891 | 118.049 | 156.8787 | 187.8862 | 221.9834 | 0.4161%
1113 | 11-65 | -64.9598 | 10.9311 | 425.1638 | 90.4543 | 117.2005 | 155.7449 | 186.6377 | 220.8064 | 0.4063%
1114 | 11-65 | -65.2311 | 10.9311 | 437.8348 | 89.6962 | 116.4634 | 154.8015 | 185.6192 | 219.794 | 0.3982%
1115 | 11-65.5 | -65.5024 | 10.9311 | 450.8882 | 89.1137 | 115.9832 | 154.2923 | 185.0491 | 219.2106 | 0.3932%
1116 | 11-66 | -65.7737 | 10.9311 | 464.2918 | 88.5913 | 115.583 | 153.9362 | 184.6387 | 218.736 | 0.3892%
1117 | 11-66 | -66.045 | 10.9311 | 478.0161 | 88.0694 | 115.1706 | 153.5808 | 184.2437 | 218.2405 | 0.3852%
1118 | 11-66.5 | -66.3164 | 10.9311 | 492.0342 | 87.528 | 114.722 | 153.1853 | 183.8145 | 217.709 | 0.3811%
1119 | 11-66.5 | -66.5877 | 10.9311 | 506.3217 | 86.8568 | 114.0714 | 152.5215 | 183.099 | 216.8431 | 0.375%
1120 | 11-67 | -66.859 | 10.9311 | 520.8565 | 86.0434 | 113.2025 | 151.5462 | 182.071 | 215.6286 | 0.3668%
1121 | 11-67 | -67.1303 | 10.9311 | 535.6183 | 85.1001 | 112.1364 | 150.2745 | 180.7583 | 214.1013 | 0.357%
1122 | 11-67.5 | -67.4016 | 10.9311 | 550.589 | 84.0969 | 110.9737 | 148.86 | 179.2788 | 212.4295 | 0.3464%
1123 | 11-67.5 | -67.673 | 10.9311 | 565.7518 | 83.1269 | 109.8601 | 147.5357 | 177.8506 | 210.8773 | 0.3367%
1124 | 11-68 | -67.9443 | 10.9311 | 581.0919 | 82.2279 | 108.8612 | 146.4084 | 176.6122 | 209.5488 | 0.3285%
1125 | 11-68 | -68.2156 | 10.9311 | 596.5953 | 81.5335 | 108.1351 | 145.731 | 175.9111 | 208.716 | 0.3232%
1126 | 11-68.5 | -68.4869 | 10.9311 | 612.2499 | 80.9171 | 107.5059 | 145.1922 | 175.3692 | 208.0453 | 0.3189%
1127 | 11-69 | -68.7583 | 10.9311 | 628.0441 | 80.3132 | 106.8815 | 144.6276 | 174.7939 | 207.381 | 0.3147%
1128 | 11-69 | -69.0296 | 10.9311 | 643.9678 | 79.6013 | 106.068 | 143.8606 | 174.0617 | 206.4937 | 0.3093%
1129 | 11-69.5 | -69.3009 | 10.9311 | 660.0115 | 78.883 | 105.23 | 143.1553 | 173.4563 | 205.6845 | 0.3044%
1130 | 11-69.5 | -69.5722 | 10.9311 | 676.1666 | 78.1999 | 104.4318 | 142.6106 | 173.0524 | 205.0357 | 0.3004%
1131 | 11-70 | -69.8435 | 10.9311 | 692.4254 | 77.4924 | 103.582 | 142.0026 | 172.5959 | 204.3218 | 0.2961%
1132 | 11-70 | -70.1149 | 10.9311 | 708.7808 | 76.8683 | 102.845 | 141.5261 | 172.332 | 203.8358 | 0.2929%
1133 | 11-70.5 | -70.3862 | 10.9311 | 725.2261 | 76.3547 | 102.2628 | 141.248 | 172.3267 | 203.6482 | 0.2911%
1134 | 11-70.5 | -70.6575 | 10.9311 | 741.7553 | 76.0048 | 101.9369 | 141.2633 | 172.5471 | 203.8058 | 0.2908%
1135 | 11-71 | -70.9288 | 10.9311 | 758.363 | 75.7412 | 101.7664 | 141.4012 | 172.8758 | 204.1217 | 0.2914%
1136 | 11-71 | -71.2001 | 10.9311 | 775.044 | 75.552 | 101.7278 | 141.6345 | 173.2954 | 204.5582 | 0.2926%
1137 | 11-71.5 | -71.4715 | 10.9311 | 791.7938 | 75.4148 | 101.768 | 141.971 | 173.7993 | 205.1304 | 0.2943%
1138 | 11-71.5 | -71.7428 | 10.9311 | 808.608 | 75.1951 | 101.7221 | 142.1245 | 174.0714 | 205.5548 | 0.2951%
1139 | 11-72 | -72.0141 | 10.9311 | 825.4827 | 74.8862 | 101.5707 | 142.0909 | 174.0992 | 205.792 | 0.2949%
1140 | 11-72.5 | -72.2854 | 10.9311 | 842.4142 | 74.521 | 101.3135 | 141.9297 | 173.9863 | 205.8634 | 0.294%
1141 | 11-72.5 | -72.5568 | 10.9311 | 859.3992 | 74.2211 | 101.1361 | 141.7972 | 173.8982 | 205.963 | 0.2933%
1142 | 11-73 | -72.8281 | 10.9311 | 876.4345 | 73.9809 | 101.0221 | 141.6641 | 173.7791 | 206.0619 | 0.2927%
1143 | 11-73 | -73.0994 | 10.9311 | 893.5172 | 73.7405 | 100.8802 | 141.3718 | 173.4527 | 206.0178 | 0.2915%
1144 | 11-73.5 | -73.3707 | 10.9311 | 910.6446 | 73.5683 | 100.8071 | 141.1436 | 173.1689 | 206.0471 | 0.2906%
1145 | 11-73.5 | -73.642 | 10.9311 | 927.8143 | 73.5019 | 100.8474 | 141.0773 | 173.0145 | 206.2317 | 0.2905%
1146 | 11-74 | -73.9134 | 10.9311 | 945.0239 | 73.6322 | 101.1136 | 141.3807 | 173.2483 | 206.7791 | 0.2923%
1147 | 11-74 | -74.1847 | 10.9311 | 962.2712 | 73.9209 | 101.5177 | 141.9829 | 173.8931 | 207.642 | 0.2957%
1148 | 11-74.5 | -74.456 | 10.9311 | 979.5543 | 74.3435 | 102.0151 | 142.8123 | 174.8136 | 208.7055 | 0.3003%
1149 | 11-74.5 | -74.7273 | 10.9311 | 996.8712 | 74.8096 | 102.4841 | 143.6575 | 175.7841 | 209.7237 | 0.3049%
1150 | 11-75 | -74.9986 | 10.9311 | 1014.2203 | 75.356 | 102.9855 | 144.5135 | 176.8111 | 210.7021 | 0.3098%
1151 | 11-75.5 | -75.27 | 10.9311 | 1031.5998 | 75.9794 | 103.5088 | 145.381 | 177.8684 | 211.6182 | 0.3149%
1152 | 11-75.5 | -75.5413 | 10.9311 | 1049.0082 | 76.6486 | 104.0296 | 146.2201 | 178.8976 | 212.4597 | 0.3199%
1153 | 11-76 | -75.8126 | 10.9311 | 1066.4441 | 77.3409 | 104.5559 | 146.981 | 179.8111 | 213.2117 | 0.3247%
1154 | 11-76 | -76.0839 | 10.9311 | 1083.9062 | 78.0324 | 105.0595 | 147.622 | 180.5518 | 213.8471 | 0.329%
1155 | 11-76.5 | -76.3553 | 10.9311 | 1101.3932 | 78.714 | 105.5265 | 148.1284 | 181.1086 | 214.3243 | 0.3327%
1156 | 11-76.5 | -76.6266 | 10.9311 | 1118.9038 | 79.4652 | 106.0639 | 148.6718 | 181.6838 | 214.8151 | 0.3368%
1157 | 11-77 | -76.8979 | 10.9311 | 1136.437 | 80.2796 | 106.6682 | 149.2564 | 182.2829 | 215.3079 | 0.3413%
1158 | 11-77 | -77.1692 | 10.9311 | 1153.9918 | 81.1211 | 107.2963 | 149.8206 | 182.8283 | 215.705 | 0.3457%
1159 | 11-77.5 | -77.4405 | 10.9311 | 1171.567 | 81.923 | 107.8534 | 150.1817 | 183.0804 | 215.8076 | 0.349%
1160 | 11-77.5 | -77.7119 | 10.9311 | 1189.1619 | 82.6399 | 108.3009 | 150.3135 | 183.0394 | 215.6213 | 0.351%
1161 | 11-78 | -77.9832 | 10.9311 | 1206.7756 | 83.2779 | 108.6627 | 150.2906 | 182.8208 | 215.2742 | 0.3519%
1162 | 11-78.5 | -78.2545 | 10.9311 | 1224.4071 | 83.9475 | 109.0829 | 150.3361 | 182.6636 | 215.0246 | 0.3534%
1163 | 11-78.5 | -78.5258 | 10.9311 | 1242.0557 | 84.6171 | 109.5365 | 150.4477 | 182.5785 | 214.8743 | 0.3553%
1164 | 11-79 | -78.7971 | 10.9311 | 1259.7207 | 85.2779 | 110.0194 | 150.6413 | 182.5993 | 214.8557 | 0.3577%
1165 | 11-79 | -79.0685 | 10.9311 | 1277.4014 | 85.9612 | 110.5646 | 150.9534 | 182.7744 | 215.025 | 0.361%
1166 | 11-79.5 | -79.3398 | 10.9311 | 1295.0971 | 86.5793 | 111.0723 | 151.273 | 182.9794 | 215.2306 | 0.3643%
1167 | 11-79.5 | -79.6111 | 10.9311 | 1312.8072 | 87.1095 | 111.518 | 151.575 | 183.188 | 215.4367 | 0.3672%
1168 | 11-80 | -79.8824 | 10.9311 | 1330.5311 | 87.5899 | 111.9484 | 151.9174 | 183.4718 | 215.7299 | 0.3705%
1169 | 11-80 | -80.1537 | 10.9311 | 1348.2682 | 87.9404 | 112.2807 | 152.2251 | 183.7546 | 216.0316 | 0.3732%
1170 | 11-80.5 | -80.4251 | 10.9311 | 1366.018 | 88.1331 | 112.4838 | 152.4641 | 183.9999 | 216.3234 | 0.3752%
1171 | 11-80.5 | -80.6964 | 10.9311 | 1383.7799 | 88.1692 | 112.5654 | 152.6358 | 184.206 | 216.6295 | 0.3764%
1172 | 11-81 | -80.9677 | 10.9311 | 1401.5536 | 87.9547 | 112.4152 | 152.6032 | 184.2125 | 216.7957 | 0.3758%
1173 | 11-81 | -81.239 | 10.9311 | 1419.3385 | 87.5006 | 112.0344 | 152.3409 | 183.9798 | 216.7574 | 0.3733%
1174 | 11-81.5 | -81.5104 | 10.9311 | 1437.1341 | 86.8576 | 111.4699 | 151.8796 | 183.5369 | 216.503 | 0.3691%
1175 | 11-82 | -81.7817 | 10.9311 | 1454.9402 | 85.891 | 110.4865 | 150.87 | 182.4983 | 215.5298 | 0.3608%
1176 | 11-82 | -82.053 | 10.9311 | 1472.7562 | 84.6585 | 109.1054 | 149.2399 | 180.7686 | 213.7216 | 0.3486%
1177 | 11-82.5 | -82.3243 | 10.9311 | 1490.5818 | 83.2533 | 107.4241 | 147.0408 | 178.3784 | 211.1113 | 0.3332%
1178 | 11-82.5 | -82.5956 | 10.9311 | 1508.4167 | 81.805 | 105.6356 | 144.6398 | 175.7734 | 208.2669 | 0.3173%
1179 | 11-83 | -82.867 | 10.9311 | 1526.2604 | 80.4249 | 103.8745 | 142.2278 | 173.1745 | 205.4597 | 0.3021%
1180 | 11-83 | -83.1383 | 10.9311 | 1544.1127 | 79.1523 | 102.1959 | 139.8814 | 170.6672 | 202.7714 | 0.2882%
1181 | 11-83.5 | -83.4096 | 10.9311 | 1561.9733 | 77.9166 | 100.5239 | 137.4743 | 168.0199 | 199.9333 | 0.2743%
1182 | 11-83.5 | -83.6809 | 10.9311 | 1579.8418 | 76.7057 | 98.8592 | 135.019 | 165.2614 | 196.9829 | 0.2605%
1183 | 11-84 | -83.9522 | 10.9311 | 1597.7179 | 75.5456 | 97.238 | 132.5602 | 162.4475 | 193.9561 | 0.2472%
1184 | 11-84 | -84.2236 | 10.9311 | 1615.6014 | 74.4223 | 95.6251 | 130.0384 | 159.5639 | 190.8006 | 0.2339%
1185 | 11-84.5 | -84.4949 | 10.9311 | 1633.492 | 73.3907 | 94.0973 | 127.5795 | 156.7648 | 187.6781 | 0.2214%
1186 | 11-85 | -84.7662 | 10.9311 | 1651.3895 | 72.4521 | 92.6632 | 125.2276 | 154.1173 | 184.6856 | 0.2099%
1187 | 11-85 | -85.0375 | 10.9311 | 1669.2936 | 71.6044 | 91.326 | 123.0095 | 151.6292 | 181.8597 | 0.1993%
1188 | 11-85.5 | -85.3089 | 10.9311 | 1687.2041 | 70.975 | 90.3227 | 121.2914 | 149.7104 | 179.7389 | 0.1914%
1189 | 11-85.5 | -85.5802 | 10.9311 | 1705.1208 | 70.5695 | 89.6851 | 120.1983 | 148.5126 | 178.5054 | 0.1867%
1190 | 11-86 | -85.8515 | 10.9311 | 1723.0434 | 70.333 | 89.3189 | 119.6364 | 147.9386 | 178.0079 | 0.1845%
1191 | 11-86 | -86.1228 | 10.9311 | 1740.9717 | 70.1743 | 89.0689 | 119.3015 | 147.6199 | 177.7436 | 0.1833%
1192 | 11-86.5 | -86.3941 | 10.9311 | 1758.9056 | 70.1091 | 88.9376 | 119.1713 | 147.5251 | 177.6313 | 0.1828%
1193 | 11-86.5 | -86.6655 | 10.9311 | 1776.8448 | 70.1497 | 88.9378 | 119.2269 | 147.606 | 177.5915 | 0.1829%
1194 | 11-87 | -86.9368 | 10.9311 | 1794.7892 | 70.4065 | 89.2206 | 119.695 | 148.1488 | 177.9521 | 0.1847%
1195 | 11-87 | -87.2081 | 10.9311 | 1812.7385 | 71.0125 | 89.9234 | 120.7102 | 149.2257 | 178.778 | 0.1886%
1196 | 11-87.5 | -87.4794 | 10.9311 | 1830.6927 | 71.9671 | 91.0195 | 122.1999 | 150.7088 | 179.9544 | 0.1943%
1197 | 11-88 | -87.7507 | 10.9311 | 1848.6516 | 73.2493 | 92.4776 | 124.0976 | 152.5043 | 181.4377 | 0.2017%
1198 | 11-88 | -88.0221 | 10.9311 | 1866.6149 | 74.8946 | 94.345 | 126.4316 | 154.6512 | 183.2753 | 0.2113%
1199 | 11-88.5 | -88.2934 | 10.9311 | 1884.5826 | 76.9421 | 96.6802 | 129.2238 | 157.1886 | 185.4965 | 0.2236%
1200 | 11-88.5 | -88.5647 | 10.9311 | 1902.5545 | 79.3093 | 99.4018 | 132.3425 | 160.0311 | 188.0115 | 0.2386%
1201 | 11-89 | -88.836 | 10.9311 | 1920.5305 | 82.0073 | 102.5373 | 135.759 | 163.1668 | 190.8168 | 0.2568%
1202 | 11-89 | -89.1074 | 10.9311 | 1938.5104 | 85.0889 | 106.1425 | 139.4889 | 166.6166 | 193.9507 | 0.2793%
1203 | 11-89.5 | -89.3787 | 10.9311 | 1956.4941 | 88.669 | 110.2123 | 143.6551 | 170.5305 | 197.6325 | 0.3082%
1204 | 11-89.5 | -89.65 | 10.9311 | 1974.4814 | 92.4229 | 114.3975 | 147.8731 | 174.465 | 201.3522 | 0.3416%
1205 | 11-90 | -89.9213 | 10.9311 | 1992.4723 | 96.3735 | 118.6857 | 152.1251 | 178.399 | 205.1197 | 0.3808%
1206 | 11-90 | -90.1926 | 10.9311 | 2010.4666 | 100.4639 | 123.1085 | 156.4759 | 182.4394 | 209.1073 | 0.4275%
1207 | 11-90.5 | -90.464 | 10.9311 | 2028.4642 | 104.6028 | 127.5296 | 160.7685 | 186.4583 | 213.1524 | 0.4817%
1208 | 11-90.5 | -90.7353 | 10.9311 | 2046.4651 | 108.588 | 131.7451 | 164.7635 | 190.2262 | 216.9673 | 0.5414%
1209 | 11-50 | -50.0371 | 11.2024 | 770.0346 | 96.1205 | 123.9642 | 165.57 | 194.9392 | 224.9431 | 0.4788%
1210 | 11-50.5 | -50.3084 | 11.2024 | 753.1911 | 95.9655 | 123.8682 | 165.4846 | 194.9753 | 225.1211 | 0.4781%
1211 | 11-50.5 | -50.5797 | 11.2024 | 736.4137 | 95.7862 | 123.7305 | 165.3561 | 194.9603 | 225.2322 | 0.4769%
1212 | 11-51 | -50.851 | 11.2024 | 719.7069 | 95.5932 | 123.5657 | 165.2064 | 194.9174 | 225.3062 | 0.4754%
1213 | 11-51 | -51.1224 | 11.2024 | 703.0759 | 95.4025 | 123.3936 | 165.0584 | 194.8713 | 225.3789 | 0.4739%
1214 | 11-51.5 | -51.3937 | 11.2024 | 686.5262 | 95.2046 | 123.2003 | 164.8932 | 194.7934 | 225.4045 | 0.4722%
1215 | 11-51.5 | -51.665 | 11.2024 | 670.0637 | 95.0178 | 123.0113 | 164.7376 | 194.7151 | 225.4232 | 0.4706%
1216 | 11-52 | -51.9363 | 11.2024 | 653.6952 | 94.8561 | 122.8451 | 164.6117 | 194.6621 | 225.4686 | 0.4693%
1217 | 11-52 | -52.2077 | 11.2024 | 637.4278 | 94.7027 | 122.6828 | 164.4943 | 194.6135 | 225.5074 | 0.468%
1218 | 11-52.5 | -52.479 | 11.2024 | 621.2695 | 94.5761 | 122.5502 | 164.4066 | 194.5996 | 225.5868 | 0.4671%
1219 | 11-53 | -52.7503 | 11.2024 | 605.2292 | 94.4922 | 122.4648 | 164.3636 | 194.6377 | 225.7334 | 0.4667%
1220 | 11-53 | -53.0216 | 11.2024 | 589.3164 | 94.4189 | 122.3781 | 164.306 | 194.652 | 225.8481 | 0.4663%
1221 | 11-53.5 | -53.2929 | 11.2024 | 573.5419 | 94.3813 | 122.318 | 164.267 | 194.6881 | 225.9997 | 0.4662%
1222 | 11-53.5 | -53.5643 | 11.2024 | 557.9172 | 94.3995 | 122.3035 | 164.2631 | 194.7653 | 226.2152 | 0.4666%
1223 | 11-54 | -53.8356 | 11.2024 | 542.4554 | 94.4407 | 122.3056 | 164.2703 | 194.8548 | 226.4459 | 0.4672%
1224 | 11-54 | -54.1069 | 11.2024 | 527.1709 | 94.5403 | 122.3607 | 164.3113 | 194.9859 | 226.737 | 0.4684%
1225 | 11-54.5 | -54.3782 | 11.2024 | 512.0796 | 94.717 | 122.4839 | 164.3914 | 195.1611 | 227.0902 | 0.4703%
1226 | 11-54.5 | -54.6495 | 11.2024 | 497.199 | 94.9284 | 122.6208 | 164.4415 | 195.2857 | 227.365 | 0.4721%
1227 | 11-55 | -54.9209 | 11.2024 | 482.5487 | 95.1976 | 122.7941 | 164.4838 | 195.3881 | 227.6037 | 0.4741%
1228 | 11-55 | -55.1922 | 11.2024 | 468.1503 | 95.5354 | 123.0133 | 164.5258 | 195.4773 | 227.8169 | 0.4765%
1229 | 11-55.5 | -55.4635 | 11.2024 | 454.0278 | 95.9112 | 123.2523 | 164.5484 | 195.5297 | 227.9725 | 0.4789%
1230 | 11-55.5 | -55.7348 | 11.2024 | 440.2077 | 96.3487 | 123.5384 | 164.582 | 195.5762 | 228.1106 | 0.4818%
1231 | 11-56 | -56.0061 | 11.2024 | 426.7195 | 96.8479 | 123.877 | 164.6344 | 195.6226 | 228.235 | 0.4851%
1232 | 11-56.5 | -56.2775 | 11.2024 | 413.5957 | 97.3552 | 124.2164 | 164.6645 | 195.625 | 228.2894 | 0.4883%
1233 | 11-56.5 | -56.5488 | 11.2024 | 400.8721 | 97.9067 | 124.6122 | 164.741 | 195.6679 | 228.3799 | 0.492%
1234 | 11-57 | -56.8201 | 11.2024 | 388.5879 | 98.4936 | 125.0621 | 164.8673 | 195.7542 | 228.5063 | 0.4964%
1235 | 11-57 | -57.0914 | 11.2024 | 376.7863 | 99.06 | 125.5088 | 164.9966 | 195.823 | 228.5799 | 0.5007%
1236 | 11-57.5 | -57.3628 | 11.2024 | 365.5138 | 99.6422 | 125.987 | 165.1623 | 195.9116 | 228.6556 | 0.5053%
1237 | 11-57.5 | -57.6341 | 11.2024 | 354.8211 | 100.2239 | 126.4837 | 165.3589 | 196.0171 | 228.7299 | 0.5101%
1238 | 11-58 | -57.9054 | 11.2024 | 344.7621 | 100.7521 | 126.9457 | 165.5446 | 196.1008 | 228.759 | 0.5146%
1239 | 11-58 | -58.1767 | 11.2024 | 335.3937 | 101.2742 | 127.4345 | 165.7981 | 196.2658 | 228.8858 | 0.5196%
1240 | 11-58.5 | -58.448 | 11.2024 | 326.7755 | 101.7688 | 127.9316 | 166.1112 | 196.5077 | 229.106 | 0.525%
1241 | 11-58.5 | -58.7194 | 11.2024 | 318.9681 | 102.1935 | 128.3911 | 166.4483 | 196.7965 | 229.3886 | 0.5303%
1242 | 11-59 | -58.9907 | 11.2024 | 312.0327 | 102.5809 | 128.8429 | 166.834 | 197.1639 | 229.7729 | 0.5358%
1243 | 11-59.5 | -59.262 | 11.2024 | 306.0283 | 102.8986 | 129.2436 | 167.2137 | 197.5445 | 230.1864 | 0.5408%
1244 | 11-59.5 | -59.5333 | 11.2024 | 301.0107 | 103.0915 | 129.5161 | 167.4834 | 197.8112 | 230.4897 | 0.5443%
1245 | 11-60 | -59.8046 | 11.2024 | 297.03 | 103.2088 | 129.7118 | 167.6882 | 198.0129 | 230.7419 | 0.5467%
1246 | 11-60 | -60.076 | 11.2024 | 294.1283 | 103.2202 | 129.7905 | 167.7805 | 198.1045 | 230.876 | 0.5476%
1247 | 11-60.5 | -60.3473 | 11.2024 | 292.3377 | 103.0886 | 129.7008 | 167.6925 | 198.0199 | 230.8057 | 0.5462%
1248 | 11-60.5 | -60.6186 | 11.2024 | 291.6787 | 102.8608 | 129.4969 | 167.4705 | 197.8258 | 230.6269 | 0.5432%
1249 | 11-61 | -60.8899 | 11.2024 | 292.1588 | 102.5828 | 129.2499 | 167.2369 | 197.6573 | 230.4805 | 0.5399%
1250 | 11-61 | -61.1613 | 11.2024 | 293.7727 | 102.3287 | 129.07 | 167.1736 | 197.7066 | 230.5706 | 0.538%
1251 | 11-61.5 | -61.4326 | 11.2024 | 296.5016 | 102.1434 | 129.0115 | 167.3337 | 198.0047 | 230.9531 | 0.5383%
1252 | 11-61.5 | -61.7039 | 11.2024 | 300.3153 | 101.9416 | 128.9463 | 167.5106 | 198.3253 | 231.3819 | 0.5385%
1253 | 11-62 | -61.9752 | 11.2024 | 305.173 | 101.6454 | 128.7532 | 167.5008 | 198.4367 | 231.6141 | 0.5368%
1254 | 11-62 | -62.2465 | 11.2024 | 311.0259 | 101.2877 | 128.4745 | 167.3454 | 198.3719 | 231.6907 | 0.5338%
1255 | 11-62.5 | -62.5179 | 11.2024 | 317.8189 | 100.8755 | 128.1305 | 167.0895 | 198.1745 | 231.6349 | 0.5297%
1256 | 11-63 | -62.7892 | 11.2024 | 325.4932 | 100.4442 | 127.7722 | 166.8171 | 197.953 | 231.5342 | 0.5253%
1257 | 11-63 | -63.0605 | 11.2024 | 333.988 | 100.0454 | 127.4704 | 166.6283 | 197.8359 | 231.5321 | 0.5219%
1258 | 11-63.5 | -63.3318 | 11.2024 | 343.2425 | 99.6582 | 127.1958 | 166.4808 | 197.7661 | 231.5608 | 0.5188%
1259 | 11-63.5 | -63.6031 | 11.2024 | 353.1968 | 99.2923 | 126.9609 | 166.3869 | 197.7443 | 231.6328 | 0.5162%
1260 | 11-64 | -63.8745 | 11.2024 | 363.7936 | 98.9859 | 126.8175 | 166.4166 | 197.8454 | 231.8512 | 0.5149%
1261 | 11-64 | -64.1458 | 11.2024 | 374.9784 | 98.6509 | 126.6317 | 166.365 | 197.8601 | 231.9794 | 0.5129%
1262 | 11-64.5 | -64.4171 | 11.2024 | 386.7001 | 98.1895 | 126.2583 | 165.9953 | 197.5082 | 231.745 | 0.5081%
1263 | 11-64.5 | -64.6884 | 11.2024 | 398.9113 | 97.5285 | 125.6012 | 165.1494 | 196.5771 | 230.9619 | 0.499%
1264 | 11-65 | -64.9598 | 11.2024 | 411.5686 | 96.8013 | 124.8433 | 164.1374 | 195.4803 | 229.9541 | 0.4887%
1265 | 11-65 | -65.2311 | 11.2024 | 424.632 | 96.1487 | 124.1939 | 163.3122 | 194.6094 | 229.1044 | 0.4801%
1266 | 11-65.5 | -65.5024 | 11.2024 | 438.0652 | 95.6576 | 123.7906 | 162.9049 | 194.1644 | 228.6635 | 0.475%
1267 | 11-66 | -65.7737 | 11.2024 | 451.8351 | 95.2088 | 123.4545 | 162.6327 | 193.8561 | 228.3098 | 0.4709%
1268 | 11-66 | -66.045 | 11.2024 | 465.9119 | 94.7467 | 123.0951 | 162.3466 | 193.5444 | 227.9125 | 0.4667%
1269 | 11-66.5 | -66.3164 | 11.2024 | 480.2686 | 94.2552 | 122.6907 | 162.0086 | 193.183 | 227.4583 | 0.462%
1270 | 11-66.5 | -66.5877 | 11.2024 | 494.8808 | 93.6246 | 122.0757 | 161.3894 | 192.5175 | 226.6452 | 0.4549%
1271 | 11-67 | -66.859 | 11.2024 | 509.7265 | 92.8452 | 121.2366 | 160.4492 | 191.5266 | 225.4658 | 0.4453%
1272 | 11-67 | -67.1303 | 11.2024 | 524.786 | 91.9312 | 120.1961 | 159.2062 | 190.2421 | 223.9622 | 0.4335%
1273 | 11-67.5 | -67.4016 | 11.2024 | 540.0412 | 90.9464 | 119.0488 | 157.8043 | 188.7683 | 222.2832 | 0.4208%
1274 | 11-67.5 | -67.673 | 11.2024 | 555.4761 | 89.984 | 117.9378 | 156.4763 | 187.3231 | 220.6926 | 0.4089%
1275 | 11-68 | -67.9443 | 11.2024 | 571.076 | 89.0822 | 116.93 | 155.3303 | 186.0466 | 219.2964 | 0.3985%
1276 | 11-68 | -68.2156 | 11.2024 | 586.8279 | 88.3773 | 116.1874 | 154.6249 | 185.2952 | 218.3806 | 0.3916%
1277 | 11-68.5 | -68.4869 | 11.2024 | 602.7197 | 87.748 | 115.54 | 154.0569 | 184.7016 | 217.6259 | 0.3859%
1278 | 11-69 | -68.7583 | 11.2024 | 618.7406 | 87.1313 | 114.8988 | 153.4657 | 184.0785 | 216.884 | 0.3803%
1279 | 11-69 | -69.0296 | 11.2024 | 634.8809 | 86.3942 | 114.0521 | 152.6486 | 183.2627 | 215.8654 | 0.3731%
1280 | 11-69.5 | -69.3009 | 11.2024 | 651.1317 | 85.6402 | 113.1662 | 151.8697 | 182.5354 | 214.866 | 0.3662%
1281 | 11-69.5 | -69.5722 | 11.2024 | 667.4848 | 84.9117 | 112.307 | 151.2278 | 181.9707 | 213.9874 | 0.3601%
1282 | 11-70 | -69.8435 | 11.2024 | 683.933 | 84.1586 | 111.3959 | 150.5191 | 181.3461 | 213.034 | 0.3537%
1283 | 11-70 | -70.1149 | 11.2024 | 700.4694 | 83.4887 | 110.5975 | 149.94 | 180.91 | 212.3039 | 0.3487%
1284 | 11-70.5 | -70.3862 | 11.2024 | 717.0881 | 82.9298 | 109.9547 | 149.5591 | 180.7318 | 211.8718 | 0.3452%
1285 | 11-70.5 | -70.6575 | 11.2024 | 733.7833 | 82.5432 | 109.5787 | 149.4907 | 180.81 | 211.811 | 0.3438%
1286 | 11-71 | -70.9288 | 11.2024 | 750.5499 | 82.2576 | 109.375 | 149.5735 | 181.041 | 211.9701 | 0.3437%
1287 | 11-71 | -71.2001 | 11.2024 | 767.3833 | 82.0597 | 109.3208 | 149.7779 | 181.4037 | 212.3113 | 0.3445%
1288 | 11-71.5 | -71.4715 | 11.2024 | 784.2791 | 81.9109 | 109.3417 | 150.0794 | 181.8412 | 212.7728 | 0.3459%
1289 | 11-71.5 | -71.7428 | 11.2024 | 801.2334 | 81.674 | 109.269 | 150.1853 | 182.0272 | 213.0588 | 0.3462%
1290 | 11-72 | -72.0141 | 11.2024 | 818.2424 | 81.343 | 109.0845 | 150.0946 | 181.9543 | 213.1473 | 0.3452%
1291 | 11-72.5 | -72.2854 | 11.2024 | 835.3029 | 80.9576 | 108.797 | 149.8899 | 181.7658 | 213.0948 | 0.3435%
1292 | 11-72.5 | -72.5568 | 11.2024 | 852.4117 | 80.6515 | 108.61 | 149.7535 | 181.6666 | 213.1714 | 0.3424%
1293 | 11-73 | -72.8281 | 11.2024 | 869.566 | 80.4174 | 108.5073 | 149.6537 | 181.5982 | 213.3443 | 0.3418%
1294 | 11-73 | -73.0994 | 11.2024 | 886.7631 | 80.1892 | 108.3888 | 149.4199 | 181.3654 | 213.4216 | 0.3407%
1295 | 11-73.5 | -73.3707 | 11.2024 | 904.0005 | 80.0255 | 108.3387 | 149.2552 | 181.1863 | 213.5898 | 0.3401%
1296 | 11-73.5 | -73.642 | 11.2024 | 921.2759 | 79.9604 | 108.395 | 149.2508 | 181.1377 | 213.9152 | 0.3404%
1297 | 11-74 | -73.9134 | 11.2024 | 938.5873 | 80.0755 | 108.6573 | 149.5956 | 181.4488 | 214.5617 | 0.3427%
1298 | 11-74 | -74.1847 | 11.2024 | 955.9326 | 80.3244 | 109.0305 | 150.1979 | 182.1093 | 215.4593 | 0.3466%
1299 | 11-74.5 | -74.456 | 11.2024 | 973.31 | 80.6839 | 109.4696 | 150.9858 | 182.9833 | 216.4915 | 0.3515%
1300 | 11-74.5 | -74.7273 | 11.2024 | 990.7179 | 81.0665 | 109.8552 | 151.7518 | 183.851 | 217.4106 | 0.3563%
1301 | 11-75 | -74.9986 | 11.2024 | 1008.1545 | 81.525 | 110.2685 | 152.5227 | 184.769 | 218.3002 | 0.3613%
1302 | 11-75.5 | -75.27 | 11.2024 | 1025.6185 | 82.0577 | 110.701 | 153.3043 | 185.7209 | 219.1441 | 0.3666%
1303 | 11-75.5 | -75.5413 | 11.2024 | 1043.1084 | 82.6346 | 111.1309 | 154.0619 | 186.6567 | 219.9227 | 0.3719%
1304 | 11-76 | -75.8126 | 11.2024 | 1060.6229 | 83.2258 | 111.5564 | 154.7216 | 187.4482 | 220.5858 | 0.3768%
1305 | 11-76 | -76.0839 | 11.2024 | 1078.1608 | 83.8092 | 111.9507 | 155.2465 | 188.0469 | 221.0962 | 0.381%
1306 | 11-76.5 | -76.3553 | 11.2024 | 1095.721 | 84.3792 | 112.3013 | 155.6314 | 188.4567 | 221.4271 | 0.3845%
1307 | 11-76.5 | -76.6266 | 11.2024 | 1113.3024 | 85.0208 | 112.7234 | 156.0585 | 188.897 | 221.7793 | 0.3885%
1308 | 11-77 | -76.8979 | 11.2024 | 1130.9039 | 85.7204 | 113.206 | 156.519 | 189.3533 | 222.1246 | 0.3929%
1309 | 11-77 | -77.1692 | 11.2024 | 1148.5247 | 86.435 | 113.7033 | 156.9422 | 189.7351 | 222.3609 | 0.3972%
1310 | 11-77.5 | -77.4405 | 11.2024 | 1166.1638 | 87.103 | 114.132 | 157.1621 | 189.8291 | 222.33 | 0.4002%
1311 | 11-77.5 | -77.7119 | 11.2024 | 1183.8204 | 87.6915 | 114.4612 | 157.1689 | 189.6583 | 222.0508 | 0.4018%
1312 | 11-78 | -77.9832 | 11.2024 | 1201.4937 | 88.2151 | 114.724 | 157.052 | 189.3581 | 221.653 | 0.4025%
1313 | 11-78.5 | -78.2545 | 11.2024 | 1219.1829 | 88.7827 | 115.0649 | 157.0331 | 189.1663 | 221.4006 | 0.4041%
1314 | 11-78.5 | -78.5258 | 11.2024 | 1236.8874 | 89.3542 | 115.4452 | 157.0915 | 189.0663 | 221.2679 | 0.4062%
1315 | 11-79 | -78.7971 | 11.2024 | 1254.6065 | 89.9124 | 115.8488 | 157.224 | 189.0628 | 221.26 | 0.4088%
1316 | 11-79 | -79.0685 | 11.2024 | 1272.3395 | 90.4869 | 116.3047 | 157.4579 | 189.1893 | 221.4216 | 0.4122%
1317 | 11-79.5 | -79.3398 | 11.2024 | 1290.0858 | 90.9987 | 116.7248 | 157.6999 | 189.3431 | 221.6172 | 0.4154%
1318 | 11-79.5 | -79.6111 | 11.2024 | 1307.845 | 91.429 | 117.0895 | 157.9305 | 189.503 | 221.8165 | 0.4184%
1319 | 11-80 | -79.8824 | 11.2024 | 1325.6164 | 91.8145 | 117.4447 | 158.202 | 189.7316 | 222.1014 | 0.4216%
1320 | 11-80 | -80.1537 | 11.2024 | 1343.3995 | 92.0784 | 117.7105 | 158.4466 | 189.9618 | 222.3939 | 0.4242%
1321 | 11-80.5 | -80.4251 | 11.2024 | 1361.1939 | 92.2016 | 117.8651 | 158.6468 | 190.1806 | 222.6923 | 0.426%
1322 | 11-80.5 | -80.6964 | 11.2024 | 1378.9991 | 92.2024 | 117.9245 | 158.8187 | 190.4085 | 223.0394 | 0.4272%
1323 | 11-81 | -80.9677 | 11.2024 | 1396.8147 | 91.9969 | 117.7796 | 158.8287 | 190.4893 | 223.2856 | 0.4267%
1324 | 11-81 | -81.239 | 11.2024 | 1414.6402 | 91.5802 | 117.421 | 158.6363 | 190.3626 | 223.3638 | 0.4242%
1325 | 11-81.5 | -81.5104 | 11.2024 | 1432.4753 | 90.9908 | 116.8864 | 158.2566 | 190.0368 | 223.2454 | 0.42%
1326 | 11-82 | -81.7817 | 11.2024 | 1450.3195 | 90.0626 | 115.8981 | 157.3005 | 189.0737 | 222.3575 | 0.4109%
1327 | 11-82 | -82.053 | 11.2024 | 1468.1726 | 88.8541 | 114.4806 | 155.7014 | 187.3884 | 220.5882 | 0.3971%
1328 | 11-82.5 | -82.3243 | 11.2024 | 1486.0342 | 87.4662 | 112.7433 | 153.5226 | 185.0297 | 217.9886 | 0.3797%
1329 | 11-82.5 | -82.5956 | 11.2024 | 1503.9039 | 86.0348 | 110.8943 | 151.1318 | 182.4451 | 215.1215 | 0.3617%
1330 | 11-83 | -82.867 | 11.2024 | 1521.7815 | 84.6639 | 109.0601 | 148.7009 | 179.8344 | 212.24 | 0.3444%
1331 | 11-83 | -83.1383 | 11.2024 | 1539.6667 | 83.3875 | 107.2895 | 146.2976 | 177.2698 | 209.4155 | 0.3282%
1332 | 11-83.5 | -83.4096 | 11.2024 | 1557.5591 | 82.1469 | 105.5239 | 143.8318 | 174.5684 | 206.4532 | 0.3122%
1333 | 11-83.5 | -83.6809 | 11.2024 | 1575.4585 | 80.9313 | 103.7664 | 141.319 | 171.7623 | 203.402 | 0.2964%
1334 | 11-84 | -83.9522 | 11.2024 | 1593.3647 | 79.7636 | 102.0511 | 138.8001 | 168.9026 | 200.2972 | 0.2812%
1335 | 11-84 | -84.2236 | 11.2024 | 1611.2773 | 78.6116 | 100.3245 | 136.1869 | 165.9492 | 197.0542 | 0.266%
1336 | 11-84.5 | -84.4949 | 11.2024 | 1629.1962 | 77.5225 | 98.6643 | 133.6022 | 163.0502 | 193.8253 | 0.2515%
1337 | 11-85 | -84.7662 | 11.2024 | 1647.1212 | 76.501 | 97.0796 | 131.0928 | 160.2717 | 190.691 | 0.238%
1338 | 11-85 | -85.0375 | 11.2024 | 1665.0519 | 75.5503 | 95.5754 | 128.6954 | 157.6272 | 187.6938 | 0.2255%
1339 | 11-85.5 | -85.3089 | 11.2024 | 1682.9883 | 74.8269 | 94.4274 | 126.8155 | 155.5768 | 185.4376 | 0.2161%
1340 | 11-85.5 | -85.5802 | 11.2024 | 1700.9301 | 74.339 | 93.6748 | 125.5837 | 154.2792 | 184.1137 | 0.2104%
1341 | 11-86 | -85.8515 | 11.2024 | 1718.8771 | 74.0299 | 93.2273 | 124.9198 | 153.6468 | 183.581 | 0.2077%
1342 | 11-86 | -86.1228 | 11.2024 | 1736.8291 | 73.796 | 92.9137 | 124.5195 | 153.3069 | 183.3381 | 0.2062%
1343 | 11-86.5 | -86.3941 | 11.2024 | 1754.786 | 73.646 | 92.7337 | 124.3628 | 153.2265 | 183.3022 | 0.2057%
1344 | 11-86.5 | -86.6655 | 11.2024 | 1772.7475 | 73.5946 | 92.6955 | 124.4155 | 153.347 | 183.3767 | 0.206%
1345 | 11-87 | -86.9368 | 11.2024 | 1790.7136 | 73.7529 | 92.9364 | 124.8741 | 153.9081 | 183.818 | 0.2081%
1346 | 11-87 | -87.2081 | 11.2024 | 1808.684 | 74.2548 | 93.5903 | 125.8669 | 154.9723 | 184.6794 | 0.2124%
1347 | 11-87.5 | -87.4794 | 11.2024 | 1826.6586 | 75.1024 | 94.6319 | 127.3141 | 156.409 | 185.8383 | 0.2186%
1348 | 11-88 | -87.7507 | 11.2024 | 1844.6373 | 76.2902 | 96.0523 | 129.1817 | 158.1539 | 187.2881 | 0.2268%
1349 | 11-88 | -88.0221 | 11.2024 | 1862.6199 | 77.8566 | 97.9023 | 131.501 | 160.252 | 189.0842 | 0.2374%
1350 | 11-88.5 | -88.2934 | 11.2024 | 1880.6063 | 79.8446 | 100.2482 | 134.2965 | 162.7478 | 191.2635 | 0.2511%
1351 | 11-88.5 | -88.5647 | 11.2024 | 1898.5964 | 82.1794 | 103.0235 | 137.4394 | 165.5658 | 193.7478 | 0.268%
1352 | 11-89 | -88.836 | 11.2024 | 1916.59 | 84.885 | 106.2772 | 140.9104 | 168.7065 | 196.5482 | 0.2889%
1353 | 11-89 | -89.1074 | 11.2024 | 1934.5869 | 88.0366 | 110.0646 | 144.7379 | 172.2053 | 199.7218 | 0.315%
1354 | 11-89.5 | -89.3787 | 11.2024 | 1952.5872 | 91.7748 | 114.3576 | 149.0388 | 176.2109 | 203.4883 | 0.349%
1355 | 11-89.5 | -89.65 | 11.2024 | 1970.5906 | 95.7411 | 118.7819 | 153.3981 | 180.2477 | 207.3004 | 0.389%
1356 | 11-90 | -89.9213 | 11.2024 | 1988.5971 | 99.9769 | 123.3268 | 157.8013 | 184.3012 | 211.1782 | 0.4364%
1357 | 11-90 | -90.1926 | 11.2024 | 2006.6066 | 104.3893 | 128.031 | 162.3311 | 188.4929 | 215.3172 | 0.4939%
1358 | 11-90.5 | -90.464 | 11.2024 | 2024.6189 | 108.8677 | 132.7453 | 166.8113 | 192.675 | 219.5318 | 0.5617%
1359 | 11-90.5 | -90.7353 | 11.2024 | 2042.6339 | 113.1875 | 137.2406 | 170.967 | 196.5758 | 223.4871 | 0.6373%
1360 | 11-50 | -50.0371 | 11.4737 | 762.7767 | 100.0789 | 129.0829 | 170.9384 | 199.9451 | 230.3019 | 0.5382%
1361 | 11-50.5 | -50.3084 | 11.4737 | 745.7877 | 99.9383 | 129.0308 | 170.9099 | 200.0604 | 230.5597 | 0.5378%
1362 | 11-50.5 | -50.5797 | 11.4737 | 728.8581 | 99.7702 | 128.9339 | 170.834 | 200.1177 | 230.7434 | 0.5368%
1363 | 11-51 | -50.851 | 11.4737 | 711.9923 | 99.5862 | 128.8067 | 170.7308 | 200.137 | 230.8792 | 0.5354%
1364 | 11-51 | -51.1224 | 11.4737 | 695.1949 | 99.4036 | 128.6696 | 170.6225 | 200.1416 | 231.0016 | 0.534%
1365 | 11-51.5 | -51.3937 | 11.4737 | 678.471 | 99.2125 | 128.509 | 170.494 | 200.1101 | 231.0728 | 0.5323%
1366 | 11-51.5 | -51.665 | 11.4737 | 661.8262 | 99.0319 | 128.3495 | 170.3722 | 200.0749 | 231.1363 | 0.5307%
1367 | 11-52 | -51.9363 | 11.4737 | 645.2666 | 98.8761 | 128.2096 | 170.2766 | 200.061 | 231.2265 | 0.5294%
1368 | 11-52 | -52.2077 | 11.4737 | 628.799 | 98.7279 | 128.069 | 170.1833 | 200.0427 | 231.3024 | 0.5281%
1369 | 11-52.5 | -52.479 | 11.4737 | 612.4309 | 98.6081 | 127.9566 | 170.117 | 200.0554 | 231.4159 | 0.5272%
1370 | 11-53 | -52.7503 | 11.4737 | 596.1703 | 98.5332 | 127.8912 | 170.0941 | 200.1193 | 231.5968 | 0.527%
1371 | 11-53 | -53.0216 | 11.4737 | 580.0265 | 98.469 | 127.8205 | 170.054 | 200.1567 | 231.7395 | 0.5266%
1372 | 11-53.5 | -53.2929 | 11.4737 | 564.0095 | 98.4394 | 127.7713 | 170.0293 | 200.2144 | 231.917 | 0.5266%
1373 | 11-53.5 | -53.5643 | 11.4737 | 548.1303 | 98.4637 | 127.7614 | 170.0358 | 200.3121 | 232.1581 | 0.5271%
1374 | 11-54 | -53.8356 | 11.4737 | 532.4014 | 98.5098 | 127.7638 | 170.0518 | 200.4228 | 232.4154 | 0.5279%
1375 | 11-54 | -54.1069 | 11.4737 | 516.8365 | 98.6141 | 127.8178 | 170.1039 | 200.5827 | 232.7442 | 0.5293%
1376 | 11-54.5 | -54.3782 | 11.4737 | 501.4508 | 98.7955 | 127.939 | 170.1979 | 200.7963 | 233.1492 | 0.5316%
1377 | 11-54.5 | -54.6495 | 11.4737 | 486.2615 | 99.0101 | 128.0718 | 170.2626 | 200.9638 | 233.4795 | 0.5339%
1378 | 11-55 | -54.9209 | 11.4737 | 471.2875 | 99.2817 | 128.2389 | 170.3159 | 201.106 | 233.7685 | 0.5365%
1379 | 11-55 | -55.1922 | 11.4737 | 456.55 | 99.6222 | 128.4507 | 170.3648 | 201.23 | 234.0247 | 0.5394%
1380 | 11-55.5 | -55.4635 | 11.4737 | 442.0727 | 100.0024 | 128.6837 | 170.3927 | 201.3138 | 234.2159 | 0.5425%
1381 | 11-55.5 | -55.7348 | 11.4737 | 427.882 | 100.4481 | 128.9694 | 170.4345 | 201.3947 | 234.3913 | 0.5462%
1382 | 11-56 | -56.0061 | 11.4737 | 414.0075 | 100.9614 | 129.3172 | 170.5013 | 201.4819 | 234.5581 | 0.5505%
1383 | 11-56.5 | -56.2775 | 11.4737 | 400.4819 | 101.4883 | 129.6745 | 170.5543 | 201.5348 | 234.6642 | 0.5548%
1384 | 11-56.5 | -56.5488 | 11.4737 | 387.3419 | 102.0685 | 130.0979 | 170.6648 | 201.6408 | 234.8232 | 0.56%
1385 | 11-57 | -56.8201 | 11.4737 | 374.6281 | 102.6947 | 130.586 | 170.8363 | 201.8017 | 235.0323 | 0.566%
1386 | 11-57 | -57.0914 | 11.4737 | 362.3853 | 103.308 | 131.0791 | 171.0165 | 201.9469 | 235.1881 | 0.5721%
1387 | 11-57.5 | -57.3628 | 11.4737 | 350.6629 | 103.9445 | 131.6097 | 171.2362 | 202.1115 | 235.3436 | 0.5786%
1388 | 11-57.5 | -57.6341 | 11.4737 | 339.5149 | 104.5872 | 132.1638 | 171.4888 | 202.2902 | 235.4921 | 0.5856%
1389 | 11-58 | -57.9054 | 11.4737 | 328.9995 | 105.1778 | 132.6844 | 171.7272 | 202.4373 | 235.5815 | 0.592%
1390 | 11-58 | -58.1767 | 11.4737 | 319.1794 | 105.7653 | 133.2339 | 172.0323 | 202.6607 | 235.7647 | 0.5991%
1391 | 11-58.5 | -58.448 | 11.4737 | 310.1206 | 106.327 | 133.7929 | 172.3957 | 202.9551 | 236.0366 | 0.6066%
1392 | 11-58.5 | -58.7194 | 11.4737 | 301.8918 | 106.818 | 134.3139 | 172.7812 | 203.2907 | 236.3655 | 0.6138%
1393 | 11-59 | -58.9907 | 11.4737 | 294.5624 | 107.2702 | 134.8243 | 173.2117 | 203.6978 | 236.7911 | 0.6212%
1394 | 11-59.5 | -59.262 | 11.4737 | 288.2011 | 107.6521 | 135.2823 | 173.6375 | 204.119 | 237.2468 | 0.628%
1395 | 11-59.5 | -59.5333 | 11.4737 | 282.8732 | 107.9109 | 135.6152 | 173.9661 | 204.4437 | 237.6043 | 0.633%
1396 | 11-60 | -59.8046 | 11.4737 | 278.638 | 108.0977 | 135.8764 | 174.2411 | 204.7176 | 237.9177 | 0.637%
1397 | 11-60 | -60.076 | 11.4737 | 275.546 | 108.1785 | 136.0242 | 174.4078 | 204.8863 | 238.1122 | 0.6391%
1398 | 11-60.5 | -60.3473 | 11.4737 | 273.6359 | 108.11 | 135.9996 | 174.3884 | 204.8705 | 238.0925 | 0.6384%
1399 | 11-60.5 | -60.6186 | 11.4737 | 272.9324 | 107.9431 | 135.8598 | 174.2353 | 204.7469 | 237.9689 | 0.6359%
1400 | 11-61 | -60.8899 | 11.4737 | 273.445 | 107.7177 | 135.6683 | 174.0587 | 204.633 | 237.8666 | 0.6328%
1401 | 11-61 | -61.1613 | 11.4737 | 275.1667 | 107.5015 | 135.5263 | 174.0254 | 204.6991 | 237.9716 | 0.6309%
1402 | 11-61.5 | -61.4326 | 11.4737 | 278.0753 | 107.3455 | 135.4926 | 174.1936 | 204.982 | 238.3492 | 0.631%
1403 | 11-61.5 | -61.7039 | 11.4737 | 282.1338 | 107.175 | 135.457 | 174.3878 | 205.3009 | 238.7856 | 0.6312%
1404 | 11-62 | -61.9752 | 11.4737 | 287.2937 | 106.9248 | 135.3181 | 174.4373 | 205.4719 | 239.0732 | 0.6297%
1405 | 11-62 | -62.2465 | 11.4737 | 293.4968 | 106.6297 | 135.1185 | 174.3828 | 205.5265 | 239.2544 | 0.627%
1406 | 11-62.5 | -62.5179 | 11.4737 | 300.6785 | 106.2908 | 134.8656 | 174.2474 | 205.4767 | 239.3253 | 0.6234%
1407 | 11-63 | -62.7892 | 11.4737 | 308.7707 | 105.9319 | 134.5956 | 174.0911 | 205.3966 | 239.3441 | 0.6194%
1408 | 11-63 | -63.0605 | 11.4737 | 317.7036 | 105.6005 | 134.3716 | 174.0011 | 205.3963 | 239.4414 | 0.6163%
1409 | 11-63.5 | -63.3318 | 11.4737 | 327.4085 | 105.2764 | 134.1651 | 173.9382 | 205.4243 | 239.5559 | 0.6134%
1410 | 11-63.5 | -63.6031 | 11.4737 | 337.8188 | 104.973 | 133.9938 | 173.9233 | 205.4934 | 239.713 | 0.6111%
1411 | 11-64 | -63.8745 | 11.4737 | 348.8714 | 104.7341 | 133.9166 | 174.037 | 205.6929 | 240.0265 | 0.6102%
1412 | 11-64 | -64.1458 | 11.4737 | 360.5073 | 104.4705 | 133.7994 | 174.0732 | 205.8116 | 240.2565 | 0.6086%
1413 | 11-64.5 | -64.4171 | 11.4737 | 372.6716 | 104.0903 | 133.5044 | 173.8071 | 205.5865 | 240.1453 | 0.604%
1414 | 11-64.5 | -64.6884 | 11.4737 | 385.3145 | 103.5276 | 132.9461 | 173.0981 | 204.8297 | 239.5274 | 0.5949%
1415 | 11-65 | -64.9598 | 11.4737 | 398.3903 | 102.9098 | 132.3024 | 172.2495 | 203.9465 | 238.7131 | 0.5846%
1416 | 11-65 | -65.2311 | 11.4737 | 411.8578 | 102.3636 | 131.7624 | 171.5801 | 203.2788 | 238.0461 | 0.5762%
1417 | 11-65.5 | -65.5024 | 11.4737 | 425.6798 | 101.9642 | 131.4444 | 171.2884 | 202.979 | 237.7417 | 0.5713%
1418 | 11-66 | -65.7737 | 11.4737 | 439.8228 | 101.5897 | 131.168 | 171.0917 | 202.7597 | 237.478 | 0.5672%
1419 | 11-66 | -66.045 | 11.4737 | 454.2569 | 101.1893 | 130.855 | 170.8625 | 202.5121 | 237.1507 | 0.5626%
1420 | 11-66.5 | -66.3164 | 11.4737 | 468.9551 | 100.756 | 130.4943 | 170.5804 | 202.2157 | 236.7689 | 0.5575%
1421 | 11-66.5 | -66.5877 | 11.4737 | 483.8934 | 100.1826 | 129.9228 | 170.0191 | 201.6199 | 236.0363 | 0.5495%
1422 | 11-67 | -66.859 | 11.4737 | 499.0502 | 99.4584 | 129.126 | 169.1362 | 200.699 | 234.9406 | 0.5386%
1423 | 11-67 | -67.1303 | 11.4737 | 514.4062 | 98.5963 | 128.1256 | 167.9475 | 199.4813 | 233.5175 | 0.5251%
1424 | 11-67.5 | -67.4016 | 11.4737 | 529.944 | 97.6497 | 127.0063 | 166.5792 | 198.0445 | 231.8771 | 0.5101%
1425 | 11-67.5 | -67.673 | 11.4737 | 545.6481 | 96.71 | 125.9099 | 165.2624 | 196.6039 | 230.279 | 0.4959%
1426 | 11-68 | -67.9443 | 11.4737 | 561.5045 | 95.8162 | 124.9038 | 164.106 | 195.3009 | 228.831 | 0.4831%
1427 | 11-68 | -68.2156 | 11.4737 | 577.5006 | 95.1007 | 124.1465 | 163.3612 | 194.4797 | 227.8094 | 0.4741%
1428 | 11-68.5 | -68.4869 | 11.4737 | 593.6252 | 94.4481 | 123.473 | 162.7316 | 193.782 | 226.9157 | 0.4664%
1429 | 11-69 | -68.7583 | 11.4737 | 609.868 | 93.7984 | 122.7968 | 162.0605 | 193.0256 | 226.0098 | 0.4586%
1430 | 11-69 | -69.0296 | 11.4737 | 626.2198 | 93.0203 | 121.9075 | 161.1468 | 192.0485 | 224.8033 | 0.4488%
1431 | 11-69.5 | -69.3009 | 11.4737 | 642.6723 | 92.2197 | 120.9731 | 160.2552 | 191.1322 | 223.5931 | 0.4392%
1432 | 11-69.5 | -69.5722 | 11.4737 | 659.2179 | 91.4401 | 120.06 | 159.485 | 190.3504 | 222.4813 | 0.4304%
1433 | 11-70 | -69.8435 | 11.4737 | 675.8497 | 90.6369 | 119.096 | 158.6447 | 189.5013 | 221.2839 | 0.4213%
1434 | 11-70 | -70.1149 | 11.4737 | 692.5616 | 89.9157 | 118.2433 | 157.9282 | 188.8299 | 220.2932 | 0.4137%
1435 | 11-70.5 | -70.3862 | 11.4737 | 709.3478 | 89.3045 | 117.5449 | 157.4054 | 188.4082 | 219.5861 | 0.408%
1436 | 11-70.5 | -70.6575 | 11.4737 | 726.2032 | 88.8747 | 117.1237 | 157.2176 | 188.281 | 219.2704 | 0.405%
1437 | 11-71 | -70.9288 | 11.4737 | 743.123 | 88.5651 | 116.8946 | 157.2208 | 188.3701 | 219.2346 | 0.4038%
1438 | 11-71 | -71.2001 | 11.4737 | 760.1029 | 88.3617 | 116.8338 | 157.3835 | 188.6515 | 219.4433 | 0.4041%
1439 | 11-71.5 | -71.4715 | 11.4737 | 777.139 | 88.2087 | 116.8503 | 157.6482 | 189.0157 | 219.7911 | 0.4052%
1440 | 11-71.5 | -71.7428 | 11.4737 | 794.2277 | 87.9727 | 116.7786 | 157.7298 | 189.1488 | 219.9925 | 0.405%
1441 | 11-72 | -72.0141 | 11.4737 | 811.3655 | 87.6485 | 116.6002 | 157.6297 | 189.0477 | 220.0216 | 0.4035%
1442 | 11-72.5 | -72.2854 | 11.4737 | 828.5494 | 87.2786 | 116.3274 | 157.4411 | 188.8738 | 219.9491 | 0.4013%
1443 | 11-72.5 | -72.5568 | 11.4737 | 845.7766 | 86.994 | 116.1629 | 157.3451 | 188.8313 | 220.0452 | 0.4001%
1444 | 11-73 | -72.8281 | 11.4737 | 863.0444 | 86.7859 | 116.0895 | 157.309 | 188.8602 | 220.2752 | 0.3997%
1445 | 11-73 | -73.0994 | 11.4737 | 880.3505 | 86.5845 | 116.0036 | 157.1579 | 188.7602 | 220.4453 | 0.3989%
1446 | 11-73.5 | -73.3707 | 11.4737 | 897.6927 | 86.443 | 115.9839 | 157.0829 | 188.7287 | 220.7302 | 0.3987%
1447 | 11-73.5 | -73.642 | 11.4737 | 915.0688 | 86.39 | 116.063 | 157.1648 | 188.8264 | 221.1721 | 0.3995%
1448 | 11-74 | -73.9134 | 11.4737 | 932.4769 | 86.4924 | 116.3224 | 157.5608 | 189.2334 | 221.8961 | 0.4025%
1449 | 11-74 | -74.1847 | 11.4737 | 949.9153 | 86.6934 | 116.6543 | 158.15 | 189.8909 | 222.8011 | 0.4067%
1450 | 11-74.5 | -74.456 | 11.4737 | 967.3822 | 86.9728 | 117.0169 | 158.8667 | 190.6741 | 223.776 | 0.4117%
1451 | 11-74.5 | -74.7273 | 11.4737 | 984.8762 | 87.2532 | 117.301 | 159.5243 | 191.3958 | 224.5915 | 0.4162%
1452 | 11-75 | -74.9986 | 11.4737 | 1002.3959 | 87.6037 | 117.6049 | 160.182 | 192.1651 | 225.3756 | 0.421%
1453 | 11-75.5 | -75.27 | 11.4737 | 1019.9398 | 88.0233 | 117.9222 | 160.8487 | 192.971 | 226.1171 | 0.4261%
1454 | 11-75.5 | -75.5413 | 11.4737 | 1037.5067 | 88.4831 | 118.234 | 161.4926 | 193.7676 | 226.7999 | 0.4312%
1455 | 11-76 | -75.8126 | 11.4737 | 1055.0954 | 88.9497 | 118.5358 | 162.0284 | 194.4082 | 227.3585 | 0.4358%
1456 | 11-76 | -76.0839 | 11.4737 | 1072.705 | 89.4022 | 118.8008 | 162.4215 | 194.8477 | 227.757 | 0.4396%
1457 | 11-76.5 | -76.3553 | 11.4737 | 1090.3342 | 89.8363 | 119.0172 | 162.6698 | 195.0955 | 227.9712 | 0.4425%
1458 | 11-76.5 | -76.6266 | 11.4737 | 1107.9822 | 90.339 | 119.3032 | 162.958 | 195.3745 | 228.2023 | 0.446%
1459 | 11-77 | -76.8979 | 11.4737 | 1125.6481 | 90.8946 | 119.6444 | 163.2707 | 195.6602 | 228.4141 | 0.4499%
1460 | 11-77 | -77.1692 | 11.4737 | 1143.3309 | 91.4639 | 119.9966 | 163.5401 | 195.8671 | 228.5181 | 0.4535%
1461 | 11-77.5 | -77.4405 | 11.4737 | 1161.03 | 91.9988 | 120.2936 | 163.6285 | 195.8259 | 228.3919 | 0.456%
1462 | 11-77.5 | -77.7119 | 11.4737 | 1178.7446 | 92.4697 | 120.5101 | 163.5347 | 195.5704 | 228.0572 | 0.4573%
1463 | 11-78 | -77.9832 | 11.4737 | 1196.4738 | 92.891 | 120.6805 | 163.3479 | 195.2334 | 227.6439 | 0.4578%
1464 | 11-78.5 | -78.2545 | 11.4737 | 1214.2172 | 93.3638 | 120.9409 | 163.2726 | 195.0265 | 227.4026 | 0.4594%
1465 | 11-78.5 | -78.5258 | 11.4737 | 1231.974 | 93.844 | 121.2457 | 163.2799 | 194.9199 | 227.2923 | 0.4616%
1466 | 11-79 | -78.7971 | 11.4737 | 1249.7437 | 94.3111 | 121.5722 | 163.3573 | 194.9037 | 227.3023 | 0.4642%
1467 | 11-79 | -79.0685 | 11.4737 | 1267.5256 | 94.7935 | 121.9476 | 163.5276 | 195.004 | 227.4718 | 0.4677%
1468 | 11-79.5 | -79.3398 | 11.4737 | 1285.3194 | 95.2192 | 122.2912 | 163.7093 | 195.1315 | 227.6762 | 0.471%
1469 | 11-79.5 | -79.6111 | 11.4737 | 1303.1243 | 95.5722 | 122.5877 | 163.8874 | 195.2698 | 227.8909 | 0.474%
1470 | 11-80 | -79.8824 | 11.4737 | 1320.9401 | 95.889 | 122.8833 | 164.112 | 195.4783 | 228.1969 | 0.4772%
1471 | 11-80 | -80.1537 | 11.4737 | 1338.7662 | 96.0954 | 123.0985 | 164.3179 | 195.6909 | 228.51 | 0.4797%
1472 | 11-80.5 | -80.4251 | 11.4737 | 1356.6021 | 96.1746 | 123.2147 | 164.4945 | 195.9042 | 228.8333 | 0.4815%
1473 | 11-80.5 | -80.6964 | 11.4737 | 1374.4476 | 96.1461 | 123.252 | 164.6644 | 196.1491 | 229.2193 | 0.4827%
1474 | 11-81 | -80.9677 | 11.4737 | 1392.3022 | 95.9321 | 123.1104 | 164.7126 | 196.2955 | 229.5363 | 0.4822%
1475 | 11-81 | -81.239 | 11.4737 | 1410.1655 | 95.5383 | 122.7793 | 164.5976 | 196.283 | 229.718 | 0.4797%
1476 | 11-81.5 | -81.5104 | 11.4737 | 1428.0371 | 95.002 | 122.2912 | 164.3269 | 196.1106 | 229.7504 | 0.4755%
1477 | 11-82 | -81.7817 | 11.4737 | 1445.9169 | 94.1212 | 121.3245 | 163.4729 | 195.2914 | 229.0036 | 0.4659%
1478 | 11-82 | -82.053 | 11.4737 | 1463.8043 | 92.946 | 119.8969 | 161.9626 | 193.7352 | 227.3584 | 0.4508%
1479 | 11-82.5 | -82.3243 | 11.4737 | 1481.6992 | 91.578 | 118.1217 | 159.8603 | 191.4952 | 224.8708 | 0.4317%
1480 | 11-82.5 | -82.5956 | 11.4737 | 1499.6012 | 90.1508 | 116.2132 | 157.5174 | 188.9857 | 222.0454 | 0.4116%
1481 | 11-83 | -82.867 | 11.4737 | 1517.5101 | 88.7619 | 114.2923 | 155.0906 | 186.3858 | 219.1104 | 0.392%
1482 | 11-83 | -83.1383 | 11.4737 | 1535.4256 | 87.4415 | 112.4043 | 152.6366 | 183.7589 | 216.1331 | 0.3732%
1483 | 11-83.5 | -83.4096 | 11.4737 | 1553.3474 | 86.1469 | 110.5066 | 150.0973 | 180.9826 | 213.0053 | 0.3546%
1484 | 11-83.5 | -83.6809 | 11.4737 | 1571.2754 | 84.8774 | 108.6106 | 147.4983 | 178.1015 | 209.7997 | 0.3363%
1485 | 11-84 | -83.9522 | 11.4737 | 1589.2092 | 83.6542 | 106.7508 | 144.8813 | 175.1662 | 206.5541 | 0.3186%
1486 | 11-84 | -84.2236 | 11.4737 | 1607.1487 | 82.4445 | 104.8758 | 142.1634 | 172.1401 | 203.1884 | 0.3011%
1487 | 11-84.5 | -84.4949 | 11.4737 | 1625.0936 | 81.29 | 103.0549 | 139.4526 | 169.1455 | 199.8343 | 0.2844%
1488 | 11-85 | -84.7662 | 11.4737 | 1643.0438 | 80.1822 | 101.2956 | 136.7924 | 166.2399 | 196.5627 | 0.2687%
1489 | 11-85 | -85.0375 | 11.4737 | 1660.999 | 79.119 | 99.6001 | 134.2156 | 163.4295 | 193.381 | 0.254%
1490 | 11-85.5 | -85.3089 | 11.4737 | 1678.9591 | 78.2909 | 98.2868 | 132.1661 | 161.2206 | 190.9456 | 0.2429%
1491 | 11-85.5 | -85.5802 | 11.4737 | 1696.9239 | 77.7122 | 97.4024 | 130.7802 | 159.779 | 189.4554 | 0.2358%
1492 | 11-86 | -85.8515 | 11.4737 | 1714.8932 | 77.3243 | 96.8577 | 129.985 | 159.0219 | 188.774 | 0.2321%
1493 | 11-86 | -86.1228 | 11.4737 | 1732.8669 | 77.021 | 96.4739 | 129.4929 | 158.6064 | 188.453 | 0.23%
1494 | 11-86.5 | -86.3941 | 11.4737 | 1750.8447 | 76.8056 | 96.248 | 129.2876 | 158.5049 | 188.4205 | 0.2293%
1495 | 11-86.5 | -86.6655 | 11.4737 | 1768.8266 | 76.6956 | 96.1842 | 129.3308 | 158.6545 | 188.5696 | 0.2297%
1496 | 11-87 | -86.9368 | 11.4737 | 1786.8124 | 76.7988 | 96.4061 | 129.7916 | 159.235 | 189.0705 | 0.232%
1497 | 11-87 | -87.2081 | 11.4737 | 1804.802 | 77.2385 | 97.0404 | 130.7842 | 160.2959 | 189.9588 | 0.2368%
1498 | 11-87.5 | -87.4794 | 11.4737 | 1822.7952 | 78.0186 | 98.062 | 132.223 | 161.7043 | 191.1052 | 0.2435%
1499 | 11-88 | -87.7507 | 11.4737 | 1840.7918 | 79.1389 | 99.4649 | 134.0737 | 163.3985 | 192.5064 | 0.2524%
1500 | 11-88 | -88.0221 | 11.4737 | 1858.7919 | 80.6398 | 101.3036 | 136.3678 | 165.4275 | 194.2289 | 0.2639%
1501 | 11-88.5 | -88.2934 | 11.4737 | 1876.7952 | 82.5694 | 103.6534 | 139.1351 | 167.8462 | 196.3246 | 0.2789%
1502 | 11-88.5 | -88.5647 | 11.4737 | 1894.8016 | 84.8683 | 106.469 | 142.267 | 170.6042 | 198.7452 | 0.2976%
1503 | 11-89 | -88.836 | 11.4737 | 1912.8111 | 87.5721 | 109.8172 | 145.752 | 173.713 | 201.5137 | 0.3209%
1504 | 11-89 | -89.1074 | 11.4737 | 1930.8234 | 90.7746 | 113.7548 | 149.6297 | 177.2191 | 204.6994 | 0.3507%
1505 | 11-89.5 | -89.3787 | 11.4737 | 1948.8386 | 94.6407 | 118.2358 | 154.0196 | 181.2774 | 208.5301 | 0.3899%
1506 | 11-89.5 | -89.65 | 11.4737 | 1966.8564 | 98.7821 | 122.8638 | 158.4799 | 185.3849 | 212.4276 | 0.4365%
1507 | 11-90 | -89.9213 | 11.4737 | 1984.8769 | 103.2595 | 127.6317 | 163.0003 | 189.5349 | 216.4234 | 0.4928%
1508 | 11-90 | -90.1926 | 11.4737 | 2002.8999 | 107.965 | 132.5838 | 167.6759 | 193.8585 | 220.7273 | 0.5622%
1509 | 11-90.5 | -90.464 | 11.4737 | 2020.9253 | 112.753 | 137.5614 | 172.3151 | 198.1916 | 225.1337 | 0.6452%
1510 | 11-90.5 | -90.7353 | 11.4737 | 2038.953 | 117.3837 | 142.314 | 176.6153 | 202.2284 | 229.2663 | 0.7391%
1511 | 12-50 | -50.0371 | 11.745 | 755.9092 | 103.8946 | 133.9777 | 175.8144 | 204.3459 | 235.281 | 0.6012%
1512 | 12-50.5 | -50.3084 | 11.745 | 738.781 | 103.7674 | 133.9669 | 175.841 | 204.5232 | 235.6051 | 0.6011%
1513 | 12-50.5 | -50.5797 | 11.745 | 721.7059 | 103.6106 | 133.91 | 175.8176 | 204.6388 | 235.8499 | 0.6003%
1514 | 12-51 | -50.851 | 11.745 | 704.6876 | 103.4367 | 133.8213 | 175.7619 | 204.7087 | 236.0365 | 0.5991%
1515 | 12-51 | -51.1224 | 11.745 | 687.7304 | 103.2638 | 133.7221 | 175.6946 | 204.7561 | 236.1969 | 0.5978%
1516 | 12-51.5 | -51.3937 | 11.745 | 670.8389 | 103.0823 | 133.5987 | 175.6054 | 204.7654 | 236.3042 | 0.5962%
1517 | 12-51.5 | -51.665 | 11.745 | 654.0183 | 102.9115 | 133.4756 | 175.5213 | 204.7722 | 236.4067 | 0.5946%
1518 | 12-52 | -51.9363 | 11.745 | 637.2743 | 102.7666 | 133.371 | 175.4615 | 204.8017 | 236.5395 | 0.5935%
1519 | 12-52 | -52.2077 | 11.745 | 620.6129 | 102.6289 | 133.2617 | 175.3985 | 204.8197 | 236.652 | 0.5922%
1520 | 12-52.5 | -52.479 | 11.745 | 604.0411 | 102.521 | 133.1786 | 175.3593 | 204.8645 | 236.7994 | 0.5915%
1521 | 12-53 | -52.7503 | 11.745 | 587.5665 | 102.4598 | 133.1408 | 175.3619 | 204.9589 | 237.0141 | 0.5914%
1522 | 12-53 | -53.0216 | 11.745 | 571.1976 | 102.4096 | 133.0938 | 175.3452 | 205.0246 | 237.1855 | 0.5912%
1523 | 12-53.5 | -53.2929 | 11.745 | 554.9436 | 102.3936 | 133.0632 | 175.3408 | 205.1088 | 237.3882 | 0.5913%
1524 | 12-53.5 | -53.5643 | 11.745 | 538.815 | 102.4299 | 133.066 | 175.3638 | 205.2313 | 237.6523 | 0.5921%
1525 | 12-54 | -53.8356 | 11.745 | 522.8235 | 102.4873 | 133.0766 | 175.3945 | 205.366 | 237.933 | 0.5931%
1526 | 12-54 | -54.1069 | 11.745 | 506.982 | 102.6028 | 133.1373 | 175.4638 | 205.5579 | 238.2971 | 0.595%
1527 | 12-54.5 | -54.3782 | 11.745 | 491.305 | 102.7952 | 133.2642 | 175.5787 | 205.814 | 238.753 | 0.5978%
1528 | 12-54.5 | -54.6495 | 11.745 | 475.8089 | 103.0193 | 133.4001 | 175.6664 | 206.0307 | 239.1423 | 0.6007%
1529 | 12-55 | -54.9209 | 11.745 | 460.5119 | 103.2988 | 133.5675 | 175.7399 | 206.2216 | 239.487 | 0.6039%
1530 | 12-55 | -55.1922 | 11.745 | 445.4346 | 103.646 | 133.7773 | 175.8054 | 206.3914 | 239.7928 | 0.6076%
1531 | 12-55.5 | -55.4635 | 11.745 | 430.6 | 104.0326 | 134.0078 | 175.8471 | 206.5171 | 240.0248 | 0.6115%
1532 | 12-55.5 | -55.7348 | 11.745 | 416.0342 | 104.4876 | 134.2968 | 175.9054 | 206.6435 | 240.2432 | 0.6161%
1533 | 12-56 | -56.0061 | 11.745 | 401.7664 | 105.0158 | 134.653 | 175.9949 | 206.7835 | 240.4591 | 0.6217%
1534 | 12-56.5 | -56.2775 | 11.745 | 387.8295 | 105.5624 | 135.0242 | 176.0786 | 206.8987 | 240.6227 | 0.6273%
1535 | 12-56.5 | -56.5488 | 11.745 | 374.2604 | 106.1707 | 135.47 | 176.2291 | 207.0776 | 240.8533 | 0.6342%
1536 | 12-57 | -56.8201 | 11.745 | 361.1008 | 106.8347 | 135.9898 | 176.4502 | 207.3211 | 241.1465 | 0.6422%
1537 | 12-57 | -57.0914 | 11.745 | 348.3969 | 107.4925 | 136.5214 | 176.6847 | 207.5505 | 241.3884 | 0.6503%
1538 | 12-57.5 | -57.3628 | 11.745 | 336.2005 | 108.1799 | 137.0949 | 176.9612 | 207.7991 | 241.6285 | 0.6592%
1539 | 12-57.5 | -57.6341 | 11.745 | 324.5688 | 108.879 | 137.6956 | 177.2715 | 208.0587 | 241.8566 | 0.6685%
1540 | 12-58 | -57.9054 | 11.745 | 313.5647 | 109.5271 | 138.263 | 177.5629 | 208.2754 | 242.0104 | 0.6773%
1541 | 12-58 | -58.1767 | 11.745 | 303.2565 | 110.1747 | 138.8604 | 177.9173 | 208.5588 | 242.2497 | 0.6869%
1542 | 12-58.5 | -58.448 | 11.745 | 293.7175 | 110.7977 | 139.4668 | 178.3248 | 208.9013 | 242.5668 | 0.6968%
1543 | 12-58.5 | -58.7194 | 11.745 | 285.025 | 111.3477 | 140.0312 | 178.7453 | 209.268 | 242.9256 | 0.7062%
1544 | 12-59 | -58.9907 | 11.745 | 277.2585 | 111.8561 | 140.579 | 179.2008 | 209.6895 | 243.3689 | 0.7157%
1545 | 12-59.5 | -59.262 | 11.745 | 270.498 | 112.2935 | 141.0712 | 179.6502 | 210.1208 | 243.8394 | 0.7244%
1546 | 12-59.5 | -59.5333 | 11.745 | 264.8203 | 112.6111 | 141.4483 | 180.0188 | 210.4783 | 244.2296 | 0.7311%
1547 | 12-60 | -59.8046 | 11.745 | 260.2965 | 112.8623 | 141.7643 | 180.3494 | 210.8058 | 244.5915 | 0.7369%
1548 | 12-60 | -60.076 | 11.745 | 256.9875 | 113.009 | 141.9733 | 180.5808 | 211.0399 | 244.8435 | 0.7406%
1549 | 12-60.5 | -60.3473 | 11.745 | 254.9406 | 113.0031 | 142.0097 | 180.6261 | 211.0894 | 244.8811 | 0.741%
1550 | 12-60.5 | -60.6186 | 11.745 | 254.1862 | 112.8996 | 141.934 | 180.5433 | 211.039 | 244.8245 | 0.7393%
1551 | 12-61 | -60.8899 | 11.745 | 254.7359 | 112.7297 | 141.7983 | 180.4243 | 210.9803 | 244.7767 | 0.7365%
1552 | 12-61 | -61.1613 | 11.745 | 256.5812 | 112.551 | 141.6894 | 180.412 | 211.0494 | 244.8972 | 0.7346%
1553 | 12-61.5 | -61.4326 | 11.745 | 259.6947 | 112.4197 | 141.6694 | 180.569 | 211.2972 | 245.2614 | 0.7345%
1554 | 12-61.5 | -61.7039 | 11.745 | 264.0313 | 112.2752 | 141.6519 | 180.7607 | 211.5919 | 245.6973 | 0.7346%
1555 | 12-62 | -61.9752 | 11.745 | 269.532 | 112.0683 | 141.5613 | 180.8609 | 211.8107 | 246.0433 | 0.7332%
1556 | 12-62 | -62.2465 | 11.745 | 276.1274 | 111.8372 | 141.4425 | 180.9123 | 211.9935 | 246.3463 | 0.7313%
1557 | 12-62.5 | -62.5179 | 11.745 | 283.741 | 111.572 | 141.2865 | 180.9099 | 212.1111 | 246.5697 | 0.7286%
1558 | 12-63 | -62.7892 | 11.745 | 292.2933 | 111.2838 | 141.1098 | 180.8806 | 212.19 | 246.7322 | 0.7254%
1559 | 12-63 | -63.0605 | 11.745 | 301.7045 | 111.0141 | 140.9635 | 180.8916 | 212.3111 | 246.9424 | 0.7228%
1560 | 12-63.5 | -63.3318 | 11.745 | 311.8968 | 110.7433 | 140.8224 | 180.9103 | 212.4333 | 247.148 | 0.7202%
1561 | 12-63.5 | -63.6031 | 11.745 | 322.7962 | 110.4884 | 140.7101 | 180.968 | 212.5848 | 247.3872 | 0.7182%
1562 | 12-64 | -63.8745 | 11.745 | 334.3335 | 110.2973 | 140.6918 | 181.1546 | 212.8677 | 247.7838 | 0.7178%
1563 | 12-64 | -64.1458 | 11.745 | 346.4451 | 110.0825 | 140.6368 | 181.2702 | 213.0799 | 248.102 | 0.7167%
1564 | 12-64.5 | -64.4171 | 11.745 | 359.0728 | 109.7615 | 140.4216 | 181.1123 | 212.9898 | 248.1087 | 0.7124%
1565 | 12-64.5 | -64.6884 | 11.745 | 372.164 | 109.2889 | 139.9761 | 180.566 | 212.4464 | 247.6725 | 0.7038%
1566 | 12-65 | -64.9598 | 11.745 | 385.6716 | 108.7733 | 139.4648 | 179.9137 | 211.8171 | 247.0698 | 0.694%
1567 | 12-65 | -65.2311 | 11.745 | 399.5533 | 108.3191 | 139.0469 | 179.4236 | 211.3818 | 246.5909 | 0.6862%
1568 | 12-65.5 | -65.5024 | 11.745 | 413.7714 | 107.986 | 138.8159 | 179.2517 | 211.2339 | 246.4094 | 0.6817%
1569 | 12-66 | -65.7737 | 11.745 | 428.2924 | 107.6582 | 138.5965 | 179.1252 | 211.0954 | 246.2139 | 0.6775%
1570 | 12-66 | -66.045 | 11.745 | 443.0865 | 107.2975 | 138.3284 | 178.948 | 210.9036 | 245.9373 | 0.6726%
1571 | 12-66.5 | -66.3164 | 11.745 | 458.1273 | 106.9058 | 138.0141 | 178.7231 | 210.6718 | 245.6172 | 0.6671%
1572 | 12-66.5 | -66.5877 | 11.745 | 473.3912 | 106.3815 | 137.4951 | 178.2322 | 210.1622 | 244.9609 | 0.6584%
1573 | 12-67 | -66.859 | 11.745 | 488.8572 | 105.7134 | 136.7549 | 177.4283 | 209.3414 | 243.9479 | 0.6462%
1574 | 12-67 | -67.1303 | 11.745 | 504.5069 | 104.9129 | 135.8125 | 176.3222 | 208.2303 | 242.6205 | 0.6312%
1575 | 12-67.5 | -67.4016 | 11.745 | 520.3235 | 104.0199 | 134.7416 | 175.0203 | 206.877 | 241.0463 | 0.6142%
1576 | 12-67.5 | -67.673 | 11.745 | 536.2924 | 103.1222 | 133.6781 | 173.7442 | 205.483 | 239.4734 | 0.5976%
1577 | 12-68 | -67.9443 | 11.745 | 552.4002 | 102.2579 | 132.6875 | 172.5999 | 204.1853 | 238.0111 | 0.5825%
1578 | 12-68 | -68.2156 | 11.745 | 568.6352 | 101.5391 | 131.9184 | 171.819 | 203.2982 | 236.9093 | 0.5712%
1579 | 12-68.5 | -68.4869 | 11.745 | 584.9868 | 100.8675 | 131.2188 | 171.1257 | 202.4911 | 235.9012 | 0.5611%
1580 | 12-69 | -68.7583 | 11.745 | 601.4454 | 100.1917 | 130.5088 | 170.3737 | 201.5959 | 234.8605 | 0.5508%
1581 | 12-69 | -69.0296 | 11.745 | 618.0024 | 99.3867 | 129.5836 | 169.3714 | 200.4656 | 233.5066 | 0.538%
1582 | 12-69.5 | -69.3009 | 11.745 | 634.6501 | 98.5526 | 128.6073 | 168.376 | 199.3699 | 232.1272 | 0.5253%
1583 | 12-69.5 | -69.5722 | 11.745 | 651.3816 | 97.7314 | 127.6451 | 167.4841 | 198.3778 | 230.8209 | 0.5134%
1584 | 12-70 | -69.8435 | 11.745 | 668.1906 | 96.8864 | 126.6317 | 166.5173 | 197.309 | 229.4123 | 0.5012%
1585 | 12-70 | -70.1149 | 11.745 | 685.0712 | 96.1176 | 125.7245 | 165.6613 | 196.3963 | 228.1903 | 0.4906%
1586 | 12-70.5 | -70.3862 | 11.745 | 702.0184 | 95.4531 | 124.9664 | 164.9868 | 195.713 | 227.2339 | 0.4821%
1587 | 12-70.5 | -70.6575 | 11.745 | 719.0274 | 94.9785 | 124.4948 | 164.6678 | 195.3597 | 226.6781 | 0.477%
1588 | 12-71 | -70.9288 | 11.745 | 736.0939 | 94.6446 | 124.2352 | 164.579 | 195.2856 | 226.4538 | 0.4745%
1589 | 12-71 | -71.2001 | 11.745 | 753.214 | 94.4367 | 124.1635 | 164.688 | 195.4645 | 226.5287 | 0.474%
1590 | 12-71.5 | -71.4715 | 11.745 | 770.384 | 94.2828 | 124.1736 | 164.9081 | 195.7411 | 226.7555 | 0.4746%
1591 | 12-71.5 | -71.7428 | 11.745 | 787.6007 | 94.0611 | 124.1104 | 164.9741 | 195.8322 | 226.8723 | 0.474%
1592 | 12-72 | -72.0141 | 11.745 | 804.8611 | 93.7663 | 123.9554 | 164.8886 | 195.7375 | 226.855 | 0.4722%
1593 | 12-72.5 | -72.2854 | 11.745 | 822.1624 | 93.4339 | 123.7153 | 164.7371 | 195.6082 | 226.7679 | 0.4697%
1594 | 12-72.5 | -72.5568 | 11.745 | 839.502 | 93.1883 | 123.5873 | 164.6914 | 195.6345 | 226.8729 | 0.4685%
1595 | 12-73 | -72.8281 | 11.745 | 856.8776 | 93.0201 | 123.5542 | 164.7198 | 195.7588 | 227.1359 | 0.4684%
1596 | 12-73 | -73.0994 | 11.745 | 874.2871 | 92.8616 | 123.5155 | 164.6545 | 195.7925 | 227.3694 | 0.4679%
1597 | 12-73.5 | -73.3707 | 11.745 | 891.7284 | 92.7577 | 123.5431 | 164.6733 | 195.912 | 227.7396 | 0.4683%
1598 | 12-73.5 | -73.642 | 11.745 | 909.1996 | 92.7306 | 123.663 | 164.8447 | 196.1583 | 228.273 | 0.4699%
1599 | 12-74 | -73.9134 | 11.745 | 926.6992 | 92.8284 | 123.9351 | 165.2867 | 196.6517 | 229.0469 | 0.4735%
1600 | 12-74 | -74.1847 | 11.745 | 944.2253 | 92.978 | 124.2322 | 165.8428 | 197.2746 | 229.9195 | 0.4778%
1601 | 12-74.5 | -74.456 | 11.745 | 961.7767 | 93.1627 | 124.5175 | 166.4583 | 197.9215 | 230.7902 | 0.4825%
1602 | 12-74.5 | -74.7273 | 11.745 | 979.3519 | 93.3215 | 124.6972 | 166.9776 | 198.4543 | 231.4594 | 0.4862%
1603 | 12-75 | -74.9986 | 11.745 | 996.9496 | 93.5403 | 124.8848 | 167.4884 | 199.0273 | 232.0944 | 0.4901%
1604 | 12-75.5 | -75.27 | 11.745 | 1014.5686 | 93.8205 | 125.0755 | 168.0009 | 199.6316 | 232.6863 | 0.4943%
1605 | 12-75.5 | -75.5413 | 11.745 | 1032.2079 | 94.1352 | 125.2533 | 168.4869 | 200.2263 | 233.2232 | 0.4986%
1606 | 12-76 | -75.8126 | 11.745 | 1049.8663 | 94.4579 | 125.4195 | 168.8682 | 200.6746 | 233.6448 | 0.5023%
1607 | 12-76 | -76.0839 | 11.745 | 1067.543 | 94.7685 | 125.5483 | 169.1113 | 200.9335 | 233.9152 | 0.5051%
1608 | 12-76.5 | -76.3553 | 11.745 | 1085.2369 | 95.0621 | 125.6275 | 169.2138 | 201.0115 | 234.009 | 0.507%
1609 | 12-76.5 | -76.6266 | 11.745 | 1102.9473 | 95.4225 | 125.7714 | 169.3518 | 201.1185 | 234.1198 | 0.5096%
1610 | 12-77 | -76.8979 | 11.745 | 1120.6733 | 95.8333 | 125.9649 | 169.5079 | 201.2266 | 234.2076 | 0.5125%
1611 | 12-77 | -77.1692 | 11.745 | 1138.4142 | 96.2601 | 126.1695 | 169.624 | 201.2653 | 234.1949 | 0.5153%
1612 | 12-77.5 | -77.4405 | 11.745 | 1156.1693 | 96.672 | 126.3393 | 169.5978 | 201.1201 | 234.0037 | 0.5171%
1613 | 12-77.5 | -77.7119 | 11.745 | 1173.9379 | 97.0421 | 126.4543 | 169.4311 | 200.8271 | 233.6549 | 0.5179%
1614 | 12-78 | -77.9832 | 11.745 | 1191.7194 | 97.3824 | 126.5448 | 169.2033 | 200.5011 | 233.2666 | 0.5183%
1615 | 12-78.5 | -78.2545 | 11.745 | 1209.5131 | 97.7797 | 126.7331 | 169.0906 | 200.3113 | 233.0644 | 0.52%
1616 | 12-78.5 | -78.5258 | 11.745 | 1227.3186 | 98.1879 | 126.9709 | 169.0622 | 200.2232 | 232.9993 | 0.5223%
1617 | 12-79 | -78.7971 | 11.745 | 1245.1353 | 98.5836 | 127.2325 | 169.1026 | 200.2207 | 233.0521 | 0.5251%
1618 | 12-79 | -79.0685 | 11.745 | 1262.9628 | 98.9951 | 127.5435 | 169.232 | 200.327 | 233.2586 | 0.5288%
1619 | 12-79.5 | -79.3398 | 11.745 | 1280.8004 | 99.3543 | 127.8284 | 169.3767 | 200.4609 | 233.5021 | 0.5322%
1620 | 12-79.5 | -79.6111 | 11.745 | 1298.6479 | 99.6475 | 128.0744 | 169.5249 | 200.6091 | 233.7614 | 0.5353%
1621 | 12-80 | -79.8824 | 11.745 | 1316.5048 | 99.9116 | 128.3274 | 169.7253 | 200.8293 | 234.1175 | 0.5386%
1622 | 12-80 | -80.1537 | 11.745 | 1334.3706 | 100.0728 | 128.507 | 169.9126 | 201.0517 | 234.4764 | 0.5412%
1623 | 12-80.5 | -80.4251 | 11.745 | 1352.245 | 100.1156 | 128.5948 | 170.0772 | 201.2742 | 234.8395 | 0.5429%
1624 | 12-80.5 | -80.6964 | 11.745 | 1370.1277 | 100.0607 | 128.6118 | 170.2438 | 201.5311 | 235.2625 | 0.5439%
1625 | 12-81 | -80.9677 | 11.745 | 1388.0182 | 99.838 | 128.4708 | 170.3217 | 201.7277 | 235.6397 | 0.5433%
1626 | 12-81 | -81.239 | 11.745 | 1405.9164 | 99.4551 | 128.1646 | 170.277 | 201.8158 | 235.9148 | 0.5408%
1627 | 12-81.5 | -81.5104 | 11.745 | 1423.8218 | 98.9507 | 127.7242 | 170.1147 | 201.7927 | 236.0743 | 0.5367%
1628 | 12-82 | -81.7817 | 11.745 | 1441.7341 | 98.1027 | 126.784 | 169.3736 | 201.1307 | 235.4568 | 0.5264%
1629 | 12-82 | -82.053 | 11.745 | 1459.6532 | 96.9457 | 125.3491 | 167.9677 | 199.7266 | 233.9414 | 0.51%
1630 | 12-82.5 | -82.3243 | 11.745 | 1477.5787 | 95.5753 | 123.5312 | 165.9557 | 197.629 | 231.5798 | 0.489%
1631 | 12-82.5 | -82.5956 | 11.745 | 1495.5104 | 94.1173 | 121.5487 | 163.6648 | 195.2073 | 228.8013 | 0.4664%
1632 | 12-83 | -82.867 | 11.745 | 1513.4479 | 92.6621 | 119.5194 | 161.2396 | 192.6234 | 225.81 | 0.444%
1633 | 12-83 | -83.1383 | 11.745 | 1531.3912 | 91.2432 | 117.4866 | 158.732 | 189.935 | 222.6834 | 0.422%
1634 | 12-83.5 | -83.4096 | 11.745 | 1549.34 | 89.8281 | 115.4128 | 156.1026 | 187.0684 | 219.3686 | 0.4002%
1635 | 12-83.5 | -83.6809 | 11.745 | 1567.294 | 88.4247 | 113.3207 | 153.3778 | 184.0838 | 215.9603 | 0.3787%
1636 | 12-84 | -83.9522 | 11.745 | 1585.2531 | 87.0626 | 111.2481 | 150.6042 | 181.0339 | 212.5082 | 0.3579%
1637 | 12-84 | -84.2236 | 11.745 | 1603.217 | 85.7249 | 109.1704 | 147.7467 | 177.9166 | 208.9747 | 0.3376%
1638 | 12-84.5 | -84.4949 | 11.745 | 1621.1856 | 84.4492 | 107.1485 | 144.8957 | 174.8227 | 205.4667 | 0.3183%
1639 | 12-85 | -84.7662 | 11.745 | 1639.1588 | 83.226 | 105.1878 | 142.0899 | 171.7975 | 202.0426 | 0.3002%
1640 | 12-85 | -85.0375 | 11.745 | 1657.1362 | 82.0409 | 103.2795 | 139.3437 | 168.8289 | 198.6817 | 0.2831%
1641 | 12-85.5 | -85.3089 | 11.745 | 1675.1178 | 81.1012 | 101.7855 | 137.1351 | 166.4617 | 196.0667 | 0.2701%
1642 | 12-85.5 | -85.5802 | 11.745 | 1693.1035 | 80.4298 | 100.7613 | 135.6067 | 164.8686 | 194.3919 | 0.2615%
1643 | 12-86 | -85.8515 | 11.745 | 1711.093 | 79.9617 | 100.1063 | 134.669 | 163.9535 | 193.5022 | 0.2566%
1644 | 12-86 | -86.1228 | 11.745 | 1729.0862 | 79.5938 | 99.6366 | 134.0597 | 163.416 | 193.0201 | 0.2535%
1645 | 12-86.5 | -86.3941 | 11.745 | 1747.083 | 79.3276 | 99.3474 | 133.771 | 163.2383 | 192.8913 | 0.2522%
1646 | 12-86.5 | -86.6655 | 11.745 | 1765.0833 | 79.1907 | 99.2487 | 133.7771 | 163.3692 | 193.011 | 0.2524%
1647 | 12-87 | -86.9368 | 11.745 | 1783.0868 | 79.281 | 99.4594 | 134.2309 | 163.9383 | 193.4964 | 0.2549%
1648 | 12-87 | -87.2081 | 11.745 | 1801.0936 | 79.7135 | 100.0966 | 135.241 | 164.9827 | 194.379 | 0.26%
1649 | 12-87.5 | -87.4794 | 11.745 | 1819.1034 | 80.484 | 101.1327 | 136.7103 | 166.3672 | 195.5151 | 0.2673%
1650 | 12-88 | -87.7507 | 11.745 | 1837.1162 | 81.5801 | 102.5382 | 138.5611 | 168.0017 | 196.861 | 0.2769%
1651 | 12-88 | -88.0221 | 11.745 | 1855.1318 | 83.0417 | 104.3684 | 140.8219 | 169.9366 | 198.488 | 0.2891%
1652 | 12-88.5 | -88.2934 | 11.745 | 1873.1502 | 84.9226 | 106.7078 | 143.529 | 172.2404 | 200.4702 | 0.3051%
1653 | 12-88.5 | -88.5647 | 11.745 | 1891.1712 | 87.1852 | 109.5403 | 146.6097 | 174.8983 | 202.8011 | 0.3252%
1654 | 12-89 | -88.836 | 11.745 | 1909.1948 | 89.8741 | 112.9432 | 150.058 | 177.9299 | 205.5111 | 0.3506%
1655 | 12-89 | -89.1074 | 11.745 | 1927.2208 | 93.0931 | 116.9825 | 153.9178 | 181.3843 | 208.6701 | 0.3834%
1656 | 12-89.5 | -89.3787 | 11.745 | 1945.2491 | 97.0319 | 121.6013 | 158.3367 | 185.4423 | 212.5391 | 0.4273%
1657 | 12-89.5 | -89.65 | 11.745 | 1963.2797 | 101.2879 | 126.3895 | 162.8542 | 189.5829 | 216.521 | 0.4801%
1658 | 12-90 | -89.9213 | 11.745 | 1981.3125 | 105.936 | 131.3417 | 167.4602 | 193.8069 | 220.6547 | 0.5449%
1659 | 12-90 | -90.1926 | 11.745 | 1999.3474 | 110.8651 | 136.498 | 172.2413 | 198.2399 | 225.1381 | 0.6257%
1660 | 12-90.5 | -90.464 | 11.745 | 2017.3843 | 115.9183 | 141.6942 | 176.9948 | 202.708 | 229.7504 | 0.7238%
1661 | 12-90.5 | -90.7353 | 11.745 | 2035.4231 | 120.8217 | 146.6649 | 181.4011 | 206.8805 | 234.0772 | 0.8364%
1662 | 12-50 | -50.0371 | 12.0164 | 749.4428 | 107.649 | 138.7561 | 180.3034 | 208.5497 | 240.1093 | 0.67%
1663 | 12-50.5 | -50.3084 | 12.0164 | 732.1826 | 107.5341 | 138.782 | 180.3788 | 208.7712 | 240.48 | 0.6702%
1664 | 12-50.5 | -50.5797 | 12.0164 | 714.969 | 107.3882 | 138.7627 | 180.4039 | 208.9302 | 240.7686 | 0.6696%
1665 | 12-51 | -50.851 | 12.0164 | 697.8055 | 107.2249 | 138.7125 | 180.3937 | 209.0397 | 240.9909 | 0.6686%
1666 | 12-51 | -51.1224 | 12.0164 | 680.696 | 107.0637 | 138.653 | 180.3676 | 209.1223 | 241.1774 | 0.6674%
1667 | 12-51.5 | -51.3937 | 12.0164 | 663.6445 | 106.8942 | 138.5695 | 180.3178 | 209.1654 | 241.3091 | 0.6659%
1668 | 12-51.5 | -51.665 | 12.0164 | 646.6557 | 106.7365 | 138.4863 | 180.2725 | 209.2082 | 241.4409 | 0.6644%
1669 | 12-52 | -51.9363 | 12.0164 | 629.7347 | 106.6066 | 138.4211 | 180.2512 | 209.2777 | 241.6109 | 0.6634%
1670 | 12-52 | -52.2077 | 12.0164 | 612.8872 | 106.4836 | 138.3485 | 180.2221 | 209.3313 | 241.7565 | 0.6624%
1671 | 12-52.5 | -52.479 | 12.0164 | 596.1193 | 106.3909 | 138.2991 | 180.2135 | 209.4089 | 241.9345 | 0.6618%
1672 | 12-53 | -52.7503 | 12.0164 | 579.4381 | 106.3457 | 138.2913 | 180.2437 | 209.5348 | 242.1794 | 0.662%
1673 | 12-53 | -53.0216 | 12.0164 | 562.8513 | 106.3114 | 138.2702 | 180.2516 | 209.6269 | 242.3746 | 0.662%
1674 | 12-53.5 | -53.2929 | 12.0164 | 546.3674 | 106.311 | 138.2608 | 180.2679 | 209.7336 | 242.5965 | 0.6624%
1675 | 12-53.5 | -53.5643 | 12.0164 | 529.9961 | 106.3618 | 138.2785 | 180.3073 | 209.8757 | 242.8763 | 0.6635%
1676 | 12-54 | -53.8356 | 12.0164 | 513.7483 | 106.4326 | 138.2989 | 180.3512 | 210.0263 | 243.1709 | 0.6648%
1677 | 12-54 | -54.1069 | 12.0164 | 497.6359 | 106.5615 | 138.3672 | 180.436 | 210.2394 | 243.5595 | 0.667%
1678 | 12-54.5 | -54.3782 | 12.0164 | 481.6726 | 106.7669 | 138.4994 | 180.57 | 210.5246 | 244.0544 | 0.6705%
1679 | 12-54.5 | -54.6495 | 12.0164 | 465.8739 | 107.0024 | 138.6385 | 180.6803 | 210.7755 | 244.4927 | 0.674%
1680 | 12-55 | -54.9209 | 12.0164 | 450.2569 | 107.2922 | 138.8069 | 180.7769 | 211.0025 | 244.8883 | 0.678%
1681 | 12-55 | -55.1922 | 12.0164 | 434.8413 | 107.6491 | 139.0154 | 180.8654 | 211.2098 | 245.2449 | 0.6826%
1682 | 12-55.5 | -55.4635 | 12.0164 | 419.6494 | 108.0443 | 139.244 | 180.9287 | 211.3694 | 245.5193 | 0.6874%
1683 | 12-55.5 | -55.7348 | 12.0164 | 404.7063 | 108.5115 | 139.5339 | 181.0134 | 211.5363 | 245.7852 | 0.6931%
1684 | 12-56 | -56.0061 | 12.0164 | 390.0407 | 109.0587 | 139.8971 | 181.1376 | 211.7274 | 246.0585 | 0.7001%
1685 | 12-56.5 | -56.2775 | 12.0164 | 375.685 | 109.6298 | 140.2818 | 181.264 | 211.9016 | 246.2872 | 0.7074%
1686 | 12-56.5 | -56.5488 | 12.0164 | 361.6763 | 110.2713 | 140.7486 | 181.4664 | 212.1516 | 246.5968 | 0.7163%
1687 | 12-57 | -56.8201 | 12.0164 | 348.0563 | 110.9792 | 141.298 | 181.7488 | 212.4776 | 246.9814 | 0.7267%
1688 | 12-57 | -57.0914 | 12.0164 | 334.8726 | 111.6856 | 141.8639 | 182.0478 | 212.792 | 247.3184 | 0.7373%
1689 | 12-57.5 | -57.3628 | 12.0164 | 322.1788 | 112.4267 | 142.4746 | 182.3904 | 213.1279 | 247.6542 | 0.749%
1690 | 12-57.5 | -57.6341 | 12.0164 | 310.0351 | 113.1839 | 143.1146 | 182.7662 | 213.4735 | 247.9741 | 0.7613%
1691 | 12-58 | -57.9054 | 12.0164 | 298.5085 | 113.8903 | 143.7211 | 183.1166 | 213.7646 | 248.2026 | 0.773%
1692 | 12-58 | -58.1767 | 12.0164 | 287.6734 | 114.5974 | 144.3564 | 183.5227 | 214.1125 | 248.5028 | 0.7855%
1693 | 12-58.5 | -58.448 | 12.0164 | 277.6106 | 115.2803 | 144.9992 | 183.9731 | 214.5073 | 248.8647 | 0.7983%
1694 | 12-58.5 | -58.7194 | 12.0164 | 268.4072 | 115.887 | 145.5963 | 184.425 | 214.9106 | 249.2489 | 0.8104%
1695 | 12-59 | -58.9907 | 12.0164 | 260.1543 | 116.4493 | 146.1722 | 184.9019 | 215.3574 | 249.7061 | 0.8224%
1696 | 12-59.5 | -59.262 | 12.0164 | 252.945 | 116.938 | 146.6901 | 185.3665 | 215.8054 | 250.1827 | 0.8333%
1697 | 12-59.5 | -59.5333 | 12.0164 | 246.8707 | 117.3051 | 147.096 | 185.7543 | 216.1786 | 250.5823 | 0.842%
1698 | 12-60 | -59.8046 | 12.0164 | 242.017 | 117.6063 | 147.4449 | 186.1101 | 216.5247 | 250.9607 | 0.8495%
1699 | 12-60 | -60.076 | 12.0164 | 238.4584 | 117.8039 | 147.6924 | 186.3758 | 216.7832 | 251.2407 | 0.8548%
1700 | 12-60.5 | -60.3473 | 12.0164 | 236.2534 | 117.8504 | 147.7761 | 186.4703 | 216.8772 | 251.3262 | 0.8564%
1701 | 12-60.5 | -60.6186 | 12.0164 | 235.44 | 117.8085 | 147.7616 | 186.4584 | 216.9006 | 251.3454 | 0.8558%
1702 | 12-61 | -60.8899 | 12.0164 | 236.0327 | 117.6964 | 147.6846 | 186.4056 | 216.9076 | 251.3698 | 0.8539%
1703 | 12-61 | -61.1613 | 12.0164 | 238.021 | 117.556 | 147.6101 | 186.4201 | 216.9923 | 251.5202 | 0.8521%
1704 | 12-61.5 | -61.4326 | 12.0164 | 241.3703 | 117.4486 | 147.6029 | 186.5691 | 217.2299 | 251.8847 | 0.8519%
1705 | 12-61.5 | -61.7039 | 12.0164 | 246.025 | 117.3249 | 147.5968 | 186.7514 | 217.5154 | 252.3245 | 0.8518%
1706 | 12-62 | -61.9752 | 12.0164 | 251.9129 | 117.1497 | 147.5384 | 186.8788 | 217.756 | 252.7137 | 0.8504%
1707 | 12-62 | -62.2465 | 12.0164 | 258.9498 | 116.9648 | 147.4747 | 186.9965 | 217.9975 | 253.1032 | 0.849%
1708 | 12-62.5 | -62.5179 | 12.0164 | 267.0449 | 116.7534 | 147.3864 | 187.0813 | 218.2 | 253.4357 | 0.8468%
1709 | 12-63 | -62.7892 | 12.0164 | 276.105 | 116.5195 | 147.2778 | 187.1394 | 218.3622 | 253.7064 | 0.8442%
1710 | 12-63 | -63.0605 | 12.0164 | 286.0386 | 116.3009 | 147.1926 | 187.2254 | 218.5543 | 254.0107 | 0.842%
1711 | 12-63.5 | -63.3318 | 12.0164 | 296.7579 | 116.0782 | 147.1073 | 187.3111 | 218.7421 | 254.302 | 0.8398%
1712 | 12-63.5 | -63.6031 | 12.0164 | 308.1809 | 115.8666 | 147.0448 | 187.4271 | 218.9547 | 254.6169 | 0.838%
1713 | 12-64 | -63.8745 | 12.0164 | 320.2323 | 115.712 | 147.0668 | 187.6573 | 219.2796 | 255.0719 | 0.8379%
1714 | 12-64 | -64.1458 | 12.0164 | 332.8438 | 115.535 | 147.0574 | 187.827 | 219.5507 | 255.4562 | 0.8371%
1715 | 12-64.5 | -64.4171 | 12.0164 | 345.9542 | 115.2701 | 146.9174 | 187.773 | 219.5918 | 255.5825 | 0.8334%
1716 | 12-64.5 | -64.6884 | 12.0164 | 359.5089 | 114.8887 | 146.5991 | 187.4153 | 219.293 | 255.3606 | 0.8259%
1717 | 12-65 | -64.9598 | 12.0164 | 373.4594 | 114.4738 | 146.2305 | 186.9776 | 218.9209 | 254.993 | 0.8173%
1718 | 12-65 | -65.2311 | 12.0164 | 387.7631 | 114.1065 | 145.9345 | 186.667 | 218.6879 | 254.705 | 0.8104%
1719 | 12-65.5 | -65.5024 | 12.0164 | 402.3823 | 113.8338 | 145.7824 | 186.601 | 218.6551 | 254.6358 | 0.8065%
1720 | 12-66 | -65.7737 | 12.0164 | 417.2838 | 113.5517 | 145.6191 | 186.5419 | 218.5918 | 254.5116 | 0.8024%
1721 | 12-66 | -66.045 | 12.0164 | 432.4384 | 113.2322 | 145.4017 | 186.4242 | 218.4646 | 254.2999 | 0.7973%
1722 | 12-66.5 | -66.3164 | 12.0164 | 447.8203 | 112.8827 | 145.1414 | 186.2659 | 218.3086 | 254.0558 | 0.7915%
1723 | 12-66.5 | -66.5877 | 12.0164 | 463.407 | 112.4041 | 144.6866 | 185.8616 | 217.906 | 253.4953 | 0.7823%
1724 | 12-67 | -66.859 | 12.0164 | 479.1784 | 111.785 | 144.0199 | 185.1618 | 217.2195 | 252.594 | 0.7692%
1725 | 12-67 | -67.1303 | 12.0164 | 495.1169 | 111.0363 | 143.1584 | 184.1734 | 216.2634 | 251.3901 | 0.7528%
1726 | 12-67.5 | -67.4016 | 12.0164 | 511.2068 | 110.1958 | 142.1683 | 182.9906 | 215.0688 | 249.9349 | 0.7342%
1727 | 12-67.5 | -67.673 | 12.0164 | 527.4342 | 109.3447 | 141.1694 | 181.8077 | 213.797 | 248.4482 | 0.7158%
1728 | 12-68 | -67.9443 | 12.0164 | 543.7868 | 108.5168 | 140.2198 | 180.7186 | 212.5674 | 247.033 | 0.6985%
1729 | 12-68 | -68.2156 | 12.0164 | 560.2536 | 107.8037 | 139.4526 | 179.9274 | 211.654 | 245.8917 | 0.6849%
1730 | 12-68.5 | -68.4869 | 12.0164 | 576.8249 | 107.1306 | 138.7513 | 179.2162 | 210.8081 | 244.8356 | 0.6725%
1731 | 12-69 | -68.7583 | 12.0164 | 593.4918 | 106.4579 | 138.0533 | 178.468 | 209.9034 | 243.7727 | 0.6601%
1732 | 12-69 | -69.0296 | 12.0164 | 610.2465 | 105.6562 | 137.1512 | 177.4846 | 208.783 | 242.4075 | 0.645%
1733 | 12-69.5 | -69.3009 | 12.0164 | 627.0819 | 104.8209 | 136.1887 | 176.4883 | 207.665 | 240.9897 | 0.6296%
1734 | 12-69.5 | -69.5722 | 12.0164 | 643.9918 | 103.9902 | 135.2242 | 175.5631 | 206.5994 | 239.6051 | 0.6149%
1735 | 12-70 | -69.8435 | 12.0164 | 660.9702 | 103.1331 | 134.2034 | 174.5507 | 205.4369 | 238.0924 | 0.5997%
1736 | 12-70 | -70.1149 | 12.0164 | 678.0122 | 102.3472 | 133.2771 | 173.6246 | 204.3916 | 236.7323 | 0.5862%
1737 | 12-70.5 | -70.3862 | 12.0164 | 695.1129 | 101.6605 | 132.4874 | 172.8543 | 203.5355 | 235.6039 | 0.5749%
1738 | 12-70.5 | -70.6575 | 12.0164 | 712.2682 | 101.1623 | 131.9834 | 172.4403 | 203.0135 | 234.8733 | 0.5677%
1739 | 12-71 | -70.9288 | 12.0164 | 729.4741 | 100.8136 | 131.6979 | 172.2689 | 202.791 | 234.4874 | 0.5636%
1740 | 12-71 | -71.2001 | 12.0164 | 746.7272 | 100.5972 | 131.6072 | 172.3083 | 202.8425 | 234.415 | 0.5622%
1741 | 12-71.5 | -71.4715 | 12.0164 | 764.0242 | 100.4361 | 131.6004 | 172.4624 | 202.998 | 234.4844 | 0.5619%
1742 | 12-71.5 | -71.7428 | 12.0164 | 781.3622 | 100.228 | 131.5387 | 172.4953 | 203.0183 | 234.4829 | 0.5607%
1743 | 12-72 | -72.0141 | 12.0164 | 798.7384 | 99.9646 | 131.4015 | 172.4064 | 202.8986 | 234.3784 | 0.5583%
1744 | 12-72.5 | -72.2854 | 12.0164 | 816.1506 | 99.6571 | 131.1748 | 172.2471 | 202.7397 | 234.2004 | 0.5551%
1745 | 12-72.5 | -72.5568 | 12.0164 | 833.5962 | 99.4337 | 131.0593 | 172.1974 | 202.7458 | 234.2276 | 0.5534%
1746 | 12-73 | -72.8281 | 12.0164 | 851.0734 | 99.2805 | 131.0403 | 172.2313 | 202.8685 | 234.432 | 0.5531%
1747 | 12-73 | -73.0994 | 12.0164 | 868.58 | 99.1405 | 131.0279 | 172.2015 | 202.9517 | 234.6451 | 0.5526%
1748 | 12-73.5 | -73.3707 | 12.0164 | 886.1145 | 99.0526 | 131.0829 | 172.266 | 203.141 | 235.02 | 0.5532%
1749 | 12-73.5 | -73.642 | 12.0164 | 903.6751 | 99.0316 | 131.2239 | 172.4801 | 203.4579 | 235.5678 | 0.5552%
1750 | 12-74 | -73.9134 | 12.0164 | 921.2604 | 99.1044 | 131.489 | 172.9226 | 203.9627 | 236.3199 | 0.559%
1751 | 12-74 | -74.1847 | 12.0164 | 938.8688 | 99.1961 | 131.7365 | 173.4082 | 204.4925 | 237.1033 | 0.5631%
1752 | 12-74.5 | -74.456 | 12.0164 | 956.4992 | 99.289 | 131.9346 | 173.8937 | 204.9781 | 237.8269 | 0.5669%
1753 | 12-74.5 | -74.7273 | 12.0164 | 974.1502 | 99.3303 | 132.0058 | 174.2519 | 205.306 | 238.316 | 0.5691%
1754 | 12-75 | -74.9986 | 12.0164 | 991.8209 | 99.4114 | 132.0677 | 174.5794 | 205.6459 | 238.756 | 0.5715%
1755 | 12-75.5 | -75.27 | 12.0164 | 1009.51 | 99.5353 | 132.1165 | 174.8882 | 205.9909 | 239.1404 | 0.574%
1756 | 12-75.5 | -75.5413 | 12.0164 | 1027.2167 | 99.6816 | 132.1409 | 175.1586 | 206.3119 | 239.4667 | 0.5763%
1757 | 12-76 | -75.8126 | 12.0164 | 1044.9401 | 99.848 | 132.1613 | 175.3456 | 206.5223 | 239.7078 | 0.5783%
1758 | 12-76 | -76.0839 | 12.0164 | 1062.6792 | 100.016 | 132.1546 | 175.4186 | 206.5818 | 239.8294 | 0.5796%
1759 | 12-76.5 | -76.3553 | 12.0164 | 1080.4333 | 100.1784 | 132.1085 | 175.3734 | 206.4944 | 239.8034 | 0.5801%
1760 | 12-76.5 | -76.6266 | 12.0164 | 1098.2016 | 100.4069 | 132.1261 | 175.3641 | 206.4382 | 239.8029 | 0.5814%
1761 | 12-77 | -76.8979 | 12.0164 | 1115.9834 | 100.6843 | 132.1899 | 175.3714 | 206.3842 | 239.7833 | 0.5831%
1762 | 12-77 | -77.1692 | 12.0164 | 1133.7781 | 100.9815 | 132.2672 | 175.3472 | 206.2771 | 239.6774 | 0.5847%
1763 | 12-77.5 | -77.4405 | 12.0164 | 1151.5851 | 101.2875 | 132.3315 | 175.2253 | 206.0583 | 239.4496 | 0.5859%
1764 | 12-77.5 | -77.7119 | 12.0164 | 1169.4037 | 101.5736 | 132.3658 | 175.0091 | 205.7628 | 239.1169 | 0.5864%
1765 | 12-78 | -77.9832 | 12.0164 | 1187.2334 | 101.8442 | 132.3951 | 174.7656 | 205.4686 | 238.7844 | 0.5867%
1766 | 12-78.5 | -78.2545 | 12.0164 | 1205.0738 | 102.1777 | 132.5252 | 174.6431 | 205.3236 | 238.6548 | 0.5885%
1767 | 12-78.5 | -78.5258 | 12.0164 | 1222.9242 | 102.5261 | 132.7073 | 174.6077 | 205.2858 | 238.6699 | 0.5911%
1768 | 12-79 | -78.7971 | 12.0164 | 1240.7843 | 102.8647 | 132.9145 | 174.6394 | 205.3321 | 238.8004 | 0.5942%
1769 | 12-79 | -79.0685 | 12.0164 | 1258.6536 | 103.2203 | 133.1709 | 174.7556 | 205.4833 | 239.0781 | 0.5981%
1770 | 12-79.5 | -79.3398 | 12.0164 | 1276.5317 | 103.5279 | 133.4074 | 174.8892 | 205.6614 | 239.3917 | 0.6018%
1771 | 12-79.5 | -79.6111 | 12.0164 | 1294.4183 | 103.7747 | 133.6121 | 175.0298 | 205.8531 | 239.7215 | 0.6052%
1772 | 12-80 | -79.8824 | 12.0164 | 1312.3128 | 103.9971 | 133.8279 | 175.2231 | 206.114 | 240.146 | 0.6087%
1773 | 12-80 | -80.1537 | 12.0164 | 1330.2151 | 104.1214 | 133.9753 | 175.4023 | 206.3672 | 240.5609 | 0.6114%
1774 | 12-80.5 | -80.4251 | 12.0164 | 1348.1248 | 104.1334 | 134.0386 | 175.5592 | 206.6086 | 240.9657 | 0.6129%
1775 | 12-80.5 | -80.6964 | 12.0164 | 1366.0415 | 104.0553 | 134.0396 | 175.7206 | 206.8769 | 241.4208 | 0.6137%
1776 | 12-81 | -80.9677 | 12.0164 | 1383.965 | 103.8217 | 133.8972 | 175.8127 | 207.0978 | 241.8369 | 0.6127%
1777 | 12-81 | -81.239 | 12.0164 | 1401.895 | 103.4412 | 133.6068 | 175.808 | 207.2395 | 242.1678 | 0.6098%
1778 | 12-81.5 | -81.5104 | 12.0164 | 1419.8312 | 102.9511 | 133.199 | 175.7115 | 207.3001 | 242.403 | 0.6054%
1779 | 12-82 | -81.7817 | 12.0164 | 1437.7733 | 102.1009 | 132.2687 | 175.0381 | 206.7241 | 241.8388 | 0.5939%
1780 | 12-82 | -82.053 | 12.0164 | 1455.7212 | 100.9151 | 130.8072 | 173.6923 | 205.4014 | 240.3506 | 0.5753%
1781 | 12-82.5 | -82.3243 | 12.0164 | 1473.6745 | 99.4856 | 128.923 | 171.7276 | 203.3774 | 238.0156 | 0.5513%
1782 | 12-82.5 | -82.5956 | 12.0164 | 1491.6331 | 97.9481 | 126.8468 | 169.4585 | 200.9925 | 235.2162 | 0.5255%
1783 | 12-83 | -82.867 | 12.0164 | 1509.5967 | 96.3926 | 124.6937 | 167.0208 | 198.3996 | 232.147 | 0.4996%
1784 | 12-83 | -83.1383 | 12.0164 | 1527.5652 | 94.8514 | 122.5048 | 164.4622 | 195.6547 | 228.8909 | 0.474%
1785 | 12-83.5 | -83.4096 | 12.0164 | 1545.5383 | 93.2807 | 120.2275 | 161.7425 | 192.6921 | 225.3928 | 0.4483%
1786 | 12-83.5 | -83.6809 | 12.0164 | 1563.5159 | 91.6975 | 117.8932 | 158.8652 | 189.5838 | 221.7623 | 0.4228%
1787 | 12-84 | -83.9522 | 12.0164 | 1581.4978 | 90.1348 | 115.5441 | 155.886 | 186.3857 | 218.062 | 0.3981%
1788 | 12-84 | -84.2236 | 12.0164 | 1599.4838 | 88.6077 | 113.2065 | 152.8547 | 183.1534 | 214.3243 | 0.3743%
1789 | 12-84.5 | -84.4949 | 12.0164 | 1617.4737 | 87.155 | 110.9436 | 149.8561 | 179.9633 | 210.6432 | 0.3521%
1790 | 12-85 | -84.7662 | 12.0164 | 1635.4675 | 85.7697 | 108.7622 | 146.9285 | 176.8474 | 207.0679 | 0.3314%
1791 | 12-85 | -85.0375 | 12.0164 | 1653.4649 | 84.4257 | 106.6345 | 144.0547 | 173.7693 | 203.5437 | 0.3119%
1792 | 12-85.5 | -85.3089 | 12.0164 | 1671.4658 | 83.3626 | 104.9629 | 141.7383 | 171.2972 | 200.7904 | 0.297%
1793 | 12-85.5 | -85.5802 | 12.0164 | 1689.4701 | 82.6071 | 103.8105 | 140.1237 | 169.6063 | 199.0008 | 0.2871%
1794 | 12-86 | -85.8515 | 12.0164 | 1707.4777 | 82.0732 | 103.048 | 139.075 | 168.5642 | 197.942 | 0.281%
1795 | 12-86 | -86.1228 | 12.0164 | 1725.4883 | 81.6467 | 102.4817 | 138.3482 | 167.8992 | 197.2814 | 0.277%
1796 | 12-86.5 | -86.3941 | 12.0164 | 1743.502 | 81.3301 | 102.1072 | 137.9468 | 167.6022 | 196.9815 | 0.2748%
1797 | 12-86.5 | -86.6655 | 12.0164 | 1761.5186 | 81.1597 | 101.95 | 137.8781 | 167.6474 | 196.9707 | 0.2744%
1798 | 12-87 | -86.9368 | 12.0164 | 1779.5379 | 81.2429 | 102.1445 | 138.2965 | 168.1526 | 197.3695 | 0.2766%
1799 | 12-87 | -87.2081 | 12.0164 | 1797.5599 | 81.6843 | 102.7975 | 139.3257 | 169.1485 | 198.2064 | 0.282%
1800 | 12-87.5 | -87.4794 | 12.0164 | 1815.5844 | 82.4766 | 103.8752 | 140.8509 | 170.4985 | 199.3231 | 0.29%
1801 | 12-88 | -87.7507 | 12.0164 | 1833.6114 | 83.5779 | 105.3002 | 142.7127 | 172.0594 | 200.6064 | 0.3001%
1802 | 12-88 | -88.0221 | 12.0164 | 1851.6407 | 85.0262 | 107.1252 | 144.9325 | 173.8805 | 202.1303 | 0.313%
1803 | 12-88.5 | -88.2934 | 12.0164 | 1869.6723 | 86.881 | 109.4454 | 147.5525 | 176.0442 | 203.9922 | 0.3297%
1804 | 12-88.5 | -88.5647 | 12.0164 | 1887.7061 | 89.1284 | 112.2802 | 150.5481 | 178.5777 | 206.2295 | 0.351%
1805 | 12-89 | -88.836 | 12.0164 | 1905.742 | 91.812 | 115.7125 | 153.9147 | 181.5051 | 208.874 | 0.3782%
1806 | 12-89 | -89.1074 | 12.0164 | 1923.7799 | 95.0377 | 119.8084 | 157.6952 | 184.8696 | 211.9842 | 0.4135%
1807 | 12-89.5 | -89.3787 | 12.0164 | 1941.8197 | 99.0268 | 124.5273 | 162.0934 | 188.8996 | 215.8829 | 0.4615%
1808 | 12-89.5 | -89.65 | 12.0164 | 1959.8614 | 103.3698 | 129.4457 | 166.6359 | 193.0624 | 219.9633 | 0.5201%
1809 | 12-90 | -89.9213 | 12.0164 | 1977.9048 | 108.1447 | 134.5571 | 171.3067 | 197.3594 | 224.2573 | 0.5928%
1810 | 12-90 | -90.1926 | 12.0164 | 1995.9499 | 113.2403 | 139.8864 | 176.1624 | 201.8951 | 228.9248 | 0.6845%
1811 | 12-90.5 | -90.464 | 12.0164 | 2013.9967 | 118.5042 | 145.2667 | 180.9922 | 206.4906 | 233.7348 | 0.797%
1812 | 12-90.5 | -90.7353 | 12.0164 | 2032.045 | 123.6496 | 150.4222 | 185.469 | 210.7991 | 238.2532 | 0.9279%
1813 | 12-50 | -50.0371 | 12.2877 | 743.3879 | 111.251 | 143.3116 | 184.2283 | 212.3927 | 244.4884 | 0.7427%
1814 | 12-50.5 | -50.3084 | 12.2877 | 726.0034 | 111.1461 | 143.3639 | 184.349 | 212.6504 | 244.8956 | 0.7431%
1815 | 12-50.5 | -50.5797 | 12.2877 | 708.6594 | 111.0094 | 143.3723 | 184.4211 | 212.8459 | 245.2197 | 0.7427%
1816 | 12-51 | -50.851 | 12.2877 | 691.3588 | 110.8554 | 143.3501 | 184.4561 | 212.9896 | 245.472 | 0.7418%
1817 | 12-51 | -51.1224 | 12.2877 | 674.1051 | 110.7049 | 143.3191 | 184.4721 | 213.103 | 245.6808 | 0.7407%
1818 | 12-51.5 | -51.3937 | 12.2877 | 656.902 | 110.5464 | 143.2644 | 184.4617 | 213.1747 | 245.8314 | 0.7392%
1819 | 12-51.5 | -51.665 | 12.2877 | 639.7536 | 110.4005 | 143.2097 | 184.4543 | 213.2477 | 245.9855 | 0.7379%
1820 | 12-52 | -51.9363 | 12.2877 | 622.6644 | 110.284 | 143.1723 | 184.4698 | 213.3509 | 246.1847 | 0.737%
1821 | 12-52 | -52.2077 | 12.2877 | 605.6394 | 110.1739 | 143.1253 | 184.4738 | 213.4353 | 246.3575 | 0.7361%
1822 | 12-52.5 | -52.479 | 12.2877 | 588.6844 | 110.0944 | 143.0988 | 184.495 | 213.5417 | 246.5607 | 0.7357%
1823 | 12-53 | -52.7503 | 12.2877 | 571.8054 | 110.0629 | 143.1104 | 184.5518 | 213.6947 | 246.8297 | 0.7361%
1824 | 12-53 | -53.0216 | 12.2877 | 555.0094 | 110.0421 | 143.106 | 184.5828 | 213.809 | 247.0434 | 0.7364%
1825 | 12-53.5 | -53.2929 | 12.2877 | 538.3044 | 110.0552 | 143.1099 | 184.6178 | 213.9335 | 247.2784 | 0.7371%
1826 | 12-53.5 | -53.5643 | 12.2877 | 521.6989 | 110.1187 | 143.1363 | 184.6709 | 214.0898 | 247.5674 | 0.7384%
1827 | 12-54 | -53.8356 | 12.2877 | 505.2029 | 110.2013 | 143.1629 | 184.725 | 214.2514 | 247.8697 | 0.74%
1828 | 12-54 | -54.1069 | 12.2877 | 488.8275 | 110.3423 | 143.2362 | 184.8219 | 214.4798 | 248.2743 | 0.7427%
1829 | 12-54.5 | -54.3782 | 12.2877 | 472.5852 | 110.5595 | 143.3718 | 184.9712 | 214.7873 | 248.7968 | 0.7467%
1830 | 12-54.5 | -54.6495 | 12.2877 | 456.4902 | 110.8061 | 143.5145 | 185.1023 | 215.0674 | 249.2753 | 0.7509%
1831 | 12-55 | -54.9209 | 12.2877 | 440.5587 | 111.1065 | 143.686 | 185.2239 | 215.3291 | 249.7187 | 0.7557%
1832 | 12-55 | -55.1922 | 12.2877 | 424.8092 | 111.4735 | 143.8973 | 185.341 | 215.5755 | 250.1286 | 0.7613%
1833 | 12-55.5 | -55.4635 | 12.2877 | 409.2626 | 111.8775 | 144.1282 | 185.4334 | 215.7719 | 250.4506 | 0.7671%
1834 | 12-55.5 | -55.7348 | 12.2877 | 393.9431 | 112.3558 | 144.4225 | 185.5517 | 215.9814 | 250.769 | 0.7742%
1835 | 12-56 | -56.0061 | 12.2877 | 378.8781 | 112.9197 | 144.7951 | 185.7171 | 216.2244 | 251.1035 | 0.7828%
1836 | 12-56.5 | -56.2775 | 12.2877 | 364.0994 | 113.513 | 145.1952 | 185.8922 | 216.4579 | 251.4005 | 0.792%
1837 | 12-56.5 | -56.5488 | 12.2877 | 349.6431 | 114.1851 | 145.6841 | 186.1517 | 216.7787 | 251.7911 | 0.8031%
1838 | 12-57 | -56.8201 | 12.2877 | 335.5511 | 114.9339 | 146.2634 | 186.4997 | 217.186 | 252.2682 | 0.8162%
1839 | 12-57 | -57.0914 | 12.2877 | 321.8711 | 115.6857 | 146.8633 | 186.8667 | 217.5843 | 252.7011 | 0.8297%
1840 | 12-57.5 | -57.3628 | 12.2877 | 308.658 | 116.4766 | 147.5094 | 187.2771 | 218.0053 | 253.1325 | 0.8445%
1841 | 12-57.5 | -57.6341 | 12.2877 | 295.9744 | 117.2875 | 148.186 | 187.7186 | 218.4339 | 253.5436 | 0.8602%
1842 | 12-58 | -57.9054 | 12.2877 | 283.8912 | 118.0482 | 148.8283 | 188.128 | 218.7977 | 253.848 | 0.8752%
1843 | 12-58 | -58.1767 | 12.2877 | 272.4883 | 118.8107 | 149.4968 | 188.5832 | 219.2068 | 254.2068 | 0.891%
1844 | 12-58.5 | -58.448 | 12.2877 | 261.8547 | 119.5492 | 150.1698 | 189.0716 | 219.6495 | 254.6083 | 0.9072%
1845 | 12-58.5 | -58.7194 | 12.2877 | 252.0878 | 120.2091 | 150.7934 | 189.5496 | 220.0854 | 255.012 | 0.9224%
1846 | 12-59 | -58.9907 | 12.2877 | 243.2918 | 120.8231 | 151.3922 | 190.0434 | 220.5558 | 255.4785 | 0.9372%
1847 | 12-59.5 | -59.262 | 12.2877 | 235.5757 | 121.3606 | 151.9291 | 190.5157 | 221.0167 | 255.9525 | 0.9508%
1848 | 12-59.5 | -59.5333 | 12.2877 | 229.0486 | 121.7715 | 152.3511 | 190.9043 | 221.3921 | 256.3394 | 0.9616%
1849 | 12-60 | -59.8046 | 12.2877 | 223.8146 | 122.1127 | 152.7133 | 191.2548 | 221.7326 | 256.6979 | 0.9709%
1850 | 12-60 | -60.076 | 12.2877 | 219.966 | 122.3507 | 152.9796 | 191.5236 | 221.9912 | 256.9688 | 0.9777%
1851 | 12-60.5 | -60.3473 | 12.2877 | 217.5764 | 122.4469 | 153.1019 | 191.6532 | 222.1133 | 257.0852 | 0.9806%
1852 | 12-60.5 | -60.6186 | 12.2877 | 216.6939 | 122.4708 | 153.1502 | 191.7143 | 222.1999 | 257.1819 | 0.9817%
1853 | 12-61 | -60.8899 | 12.2877 | 217.337 | 122.4243 | 153.1387 | 191.738 | 222.2731 | 257.2896 | 0.9812%
1854 | 12-61 | -61.1613 | 12.2877 | 219.4923 | 122.3287 | 153.1035 | 191.7872 | 222.3861 | 257.4775 | 0.98%
1855 | 12-61.5 | -61.4326 | 12.2877 | 223.1159 | 122.2495 | 153.1115 | 191.9312 | 222.6214 | 257.8436 | 0.9798%
1856 | 12-61.5 | -61.7039 | 12.2877 | 228.1379 | 122.147 | 153.113 | 192.0967 | 222.8969 | 258.2781 | 0.9795%
1857 | 12-62 | -61.9752 | 12.2877 | 234.4684 | 121.9979 | 153.074 | 192.2278 | 223.145 | 258.6862 | 0.978%
1858 | 12-62 | -62.2465 | 12.2877 | 242.0048 | 121.8473 | 153.0429 | 192.3712 | 223.4139 | 259.1206 | 0.9766%
1859 | 12-62.5 | -62.5179 | 12.2877 | 250.6383 | 121.6756 | 152.996 | 192.4961 | 223.6561 | 259.5138 | 0.9748%
1860 | 12-63 | -62.7892 | 12.2877 | 260.2598 | 121.4843 | 152.9327 | 192.5996 | 223.8632 | 259.8511 | 0.9724%
1861 | 12-63 | -63.0605 | 12.2877 | 270.7638 | 121.3104 | 152.8938 | 192.7323 | 224.1032 | 260.2243 | 0.9706%
1862 | 12-63.5 | -63.3318 | 12.2877 | 282.0519 | 121.1343 | 152.8573 | 192.8693 | 224.3444 | 260.591 | 0.9688%
1863 | 12-63.5 | -63.6031 | 12.2877 | 294.0337 | 120.9648 | 152.8381 | 193.0285 | 224.6038 | 260.9726 | 0.9673%
1864 | 12-64 | -63.8745 | 12.2877 | 306.6279 | 120.8381 | 152.883 | 193.27 | 224.9463 | 261.4563 | 0.9673%
1865 | 12-64 | -64.1458 | 12.2877 | 319.7621 | 120.6911 | 152.9045 | 193.4679 | 225.2455 | 261.8815 | 0.9667%
1866 | 12-64.5 | -64.4171 | 12.2877 | 333.3725 | 120.4831 | 152.8391 | 193.5163 | 225.4079 | 262.1292 | 0.9638%
1867 | 12-64.5 | -64.6884 | 12.2877 | 347.4031 | 120.2064 | 152.6663 | 193.3767 | 225.3719 | 262.1615 | 0.9584%
1868 | 12-65 | -64.9598 | 12.2877 | 361.8051 | 119.9026 | 152.4544 | 193.176 | 225.2621 | 262.0611 | 0.952%
1869 | 12-65 | -65.2311 | 12.2877 | 376.5357 | 119.6245 | 152.2813 | 193.0456 | 225.1978 | 261.9715 | 0.9466%
1870 | 12-65.5 | -65.5024 | 12.2877 | 391.5579 | 119.4072 | 152.1973 | 193.0648 | 225.2389 | 262.0021 | 0.9433%
1871 | 12-66 | -65.7737 | 12.2877 | 406.8393 | 119.1699 | 152.0856 | 193.0622 | 225.2254 | 261.9478 | 0.9394%
1872 | 12-66 | -66.045 | 12.2877 | 422.3519 | 118.8956 | 151.9216 | 193.0048 | 225.1504 | 261.8103 | 0.9344%
1873 | 12-66.5 | -66.3164 | 12.2877 | 438.071 | 118.594 | 151.7202 | 192.9176 | 225.0554 | 261.6531 | 0.9287%
1874 | 12-66.5 | -66.5877 | 12.2877 | 453.9751 | 118.1705 | 151.3403 | 192.6144 | 224.7361 | 261.2086 | 0.9193%
1875 | 12-67 | -66.859 | 12.2877 | 470.0455 | 117.6148 | 150.7649 | 192.0459 | 224.1693 | 260.4516 | 0.9058%
1876 | 12-67 | -67.1303 | 12.2877 | 486.2657 | 116.9372 | 150.0094 | 191.215 | 223.3743 | 259.4169 | 0.8887%
1877 | 12-67.5 | -67.4016 | 12.2877 | 502.6211 | 116.1712 | 149.1366 | 190.2116 | 222.3766 | 258.1503 | 0.8693%
1878 | 12-67.5 | -67.673 | 12.2877 | 519.0989 | 115.3806 | 148.2379 | 189.1803 | 221.2956 | 256.82 | 0.8496%
1879 | 12-68 | -67.9443 | 12.2877 | 535.6878 | 114.5972 | 147.3578 | 188.1922 | 220.1994 | 255.5127 | 0.8306%
1880 | 12-68 | -68.2156 | 12.2877 | 552.3778 | 113.892 | 146.609 | 187.4182 | 219.2997 | 254.3695 | 0.8146%
1881 | 12-68.5 | -68.4869 | 12.2877 | 569.16 | 113.2285 | 145.9335 | 186.7366 | 218.4847 | 253.3257 | 0.8001%
1882 | 12-69 | -68.7583 | 12.2877 | 586.0265 | 112.5864 | 145.2982 | 186.0798 | 217.7003 | 252.3472 | 0.7865%
1883 | 12-69 | -69.0296 | 12.2877 | 602.97 | 111.8317 | 144.4854 | 185.2322 | 216.7284 | 251.1025 | 0.7701%
1884 | 12-69.5 | -69.3009 | 12.2877 | 619.9844 | 111.0365 | 143.5998 | 184.3479 | 215.7122 | 249.7715 | 0.7531%
1885 | 12-69.5 | -69.5722 | 12.2877 | 637.0638 | 110.2309 | 142.686 | 183.4862 | 214.6812 | 248.4178 | 0.7362%
1886 | 12-70 | -69.8435 | 12.2877 | 654.2033 | 109.3929 | 141.7063 | 182.5175 | 213.5294 | 246.9037 | 0.7185%
1887 | 12-70 | -70.1149 | 12.2877 | 671.3981 | 108.6158 | 140.8014 | 181.5968 | 212.4575 | 245.4947 | 0.7023%
1888 | 12-70.5 | -70.3862 | 12.2877 | 688.6441 | 107.927 | 140.0118 | 180.7913 | 211.5237 | 244.2682 | 0.6884%
1889 | 12-70.5 | -70.6575 | 12.2877 | 705.9375 | 107.4185 | 139.4957 | 180.3218 | 210.8945 | 243.4151 | 0.6791%
1890 | 12-71 | -70.9288 | 12.2877 | 723.2749 | 107.0558 | 139.1893 | 180.0791 | 210.542 | 242.8883 | 0.6732%
1891 | 12-71 | -71.2001 | 12.2877 | 740.6532 | 106.8226 | 139.0704 | 180.0344 | 210.4451 | 242.6593 | 0.6704%
1892 | 12-71.5 | -71.4715 | 12.2877 | 758.0696 | 106.644 | 139.036 | 180.1067 | 210.4581 | 242.5562 | 0.669%
1893 | 12-71.5 | -71.7428 | 12.2877 | 775.5214 | 106.4466 | 138.9695 | 180.0982 | 210.3967 | 242.4303 | 0.6669%
1894 | 12-72 | -72.0141 | 12.2877 | 793.0064 | 106.2154 | 138.8456 | 179.9997 | 210.2432 | 242.2482 | 0.664%
1895 | 12-72.5 | -72.2854 | 12.2877 | 810.5222 | 105.9175 | 138.6144 | 179.7999 | 210.0054 | 241.9404 | 0.6596%
1896 | 12-72.5 | -72.5568 | 12.2877 | 828.0671 | 105.686 | 138.4886 | 179.7027 | 209.9235 | 241.8375 | 0.6569%
1897 | 12-73 | -72.8281 | 12.2877 | 845.639 | 105.5162 | 138.4589 | 179.692 | 209.9648 | 241.9223 | 0.6557%
1898 | 12-73 | -73.0994 | 12.2877 | 863.2365 | 105.3668 | 138.4542 | 179.6569 | 210.0306 | 242.061 | 0.6547%
1899 | 12-73.5 | -73.3707 | 12.2877 | 880.8578 | 105.2676 | 138.5187 | 179.727 | 210.2234 | 242.3849 | 0.6551%
1900 | 12-73.5 | -73.642 | 12.2877 | 898.5016 | 105.2281 | 138.6633 | 179.9439 | 210.5448 | 242.8908 | 0.657%
1901 | 12-74 | -73.9134 | 12.2877 | 916.1665 | 105.2595 | 138.9028 | 180.3464 | 210.9946 | 243.5669 | 0.6605%
1902 | 12-74 | -74.1847 | 12.2877 | 933.8514 | 105.2815 | 139.084 | 180.7278 | 211.4057 | 244.2147 | 0.6637%
1903 | 12-74.5 | -74.456 | 12.2877 | 951.5551 | 105.2787 | 139.1808 | 181.0571 | 211.7233 | 244.754 | 0.6659%
1904 | 12-74.5 | -74.7273 | 12.2877 | 969.2765 | 105.2077 | 139.132 | 181.2348 | 211.8506 | 245.0335 | 0.666%
1905 | 12-75 | -74.9986 | 12.2877 | 987.0147 | 105.1516 | 139.0475 | 181.3433 | 211.9353 | 245.2294 | 0.6659%
1906 | 12-75.5 | -75.27 | 12.2877 | 1004.7687 | 105.1075 | 138.925 | 181.3969 | 211.9747 | 245.3386 | 0.6653%
1907 | 12-75.5 | -75.5413 | 12.2877 | 1022.5377 | 105.0662 | 138.7623 | 181.3902 | 211.9601 | 245.3596 | 0.6643%
1908 | 12-76 | -75.8126 | 12.2877 | 1040.321 | 105.0692 | 138.6146 | 181.34 | 211.8977 | 245.3614 | 0.6636%
1909 | 12-76 | -76.0839 | 12.2877 | 1058.1177 | 105.1001 | 138.4615 | 181.2207 | 211.754 | 245.2994 | 0.6626%
1910 | 12-76.5 | -76.3553 | 12.2877 | 1075.9272 | 105.1432 | 138.2888 | 181.0248 | 211.5256 | 245.1422 | 0.6613%
1911 | 12-76.5 | -76.6266 | 12.2877 | 1093.7489 | 105.2535 | 138.179 | 180.8694 | 211.3351 | 245.0267 | 0.6609%
1912 | 12-77 | -76.8979 | 12.2877 | 1111.582 | 105.4122 | 138.1138 | 180.7327 | 211.1506 | 244.9028 | 0.661%
1913 | 12-77 | -77.1692 | 12.2877 | 1129.4262 | 105.5937 | 138.0668 | 180.5774 | 210.9332 | 244.713 | 0.6613%
1914 | 12-77.5 | -77.4405 | 12.2877 | 1147.2807 | 105.8011 | 138.0325 | 180.3748 | 210.6818 | 244.4619 | 0.6615%
1915 | 12-77.5 | -77.7119 | 12.2877 | 1165.1452 | 106.0085 | 137.9965 | 180.1283 | 210.4022 | 244.1611 | 0.6616%
1916 | 12-78 | -77.9832 | 12.2877 | 1183.0191 | 106.2174 | 137.9776 | 179.89 | 210.1544 | 243.9001 | 0.6618%
1917 | 12-78.5 | -78.2545 | 12.2877 | 1200.902 | 106.4962 | 138.0627 | 179.7782 | 210.0674 | 243.8574 | 0.6638%
1918 | 12-78.5 | -78.5258 | 12.2877 | 1218.7935 | 106.7956 | 138.2031 | 179.7559 | 210.0928 | 243.9676 | 0.6668%
1919 | 12-79 | -78.7971 | 12.2877 | 1236.6932 | 107.0887 | 138.3699 | 179.7989 | 210.2015 | 244.1929 | 0.6702%
1920 | 12-79 | -79.0685 | 12.2877 | 1254.6007 | 107.4004 | 138.5846 | 179.9216 | 210.4117 | 244.5605 | 0.6745%
1921 | 12-79.5 | -79.3398 | 12.2877 | 1272.5157 | 107.6684 | 138.7838 | 180.063 | 210.6486 | 244.9642 | 0.6786%
1922 | 12-79.5 | -79.6111 | 12.2877 | 1290.4378 | 107.8802 | 138.9566 | 180.213 | 210.8975 | 245.3823 | 0.6822%
1923 | 12-80 | -79.8824 | 12.2877 | 1308.3667 | 108.0711 | 139.1431 | 180.4126 | 211.2099 | 245.8878 | 0.686%
1924 | 12-80 | -80.1537 | 12.2877 | 1326.3021 | 108.1669 | 139.2654 | 180.5934 | 211.5025 | 246.3679 | 0.6887%
1925 | 12-80.5 | -80.4251 | 12.2877 | 1344.2437 | 108.1546 | 139.3087 | 180.7477 | 211.7707 | 246.8218 | 0.6901%
1926 | 12-80.5 | -80.6964 | 12.2877 | 1362.1913 | 108.058 | 139.2958 | 180.9051 | 212.0568 | 247.3136 | 0.6906%
1927 | 12-81 | -80.9677 | 12.2877 | 1380.1446 | 107.8141 | 139.1515 | 181.0005 | 212.2923 | 247.7621 | 0.6891%
1928 | 12-81 | -81.239 | 12.2877 | 1398.1033 | 107.4311 | 138.8727 | 181.0116 | 212.4512 | 248.1294 | 0.6856%
1929 | 12-81.5 | -81.5104 | 12.2877 | 1416.0673 | 106.9453 | 138.4888 | 180.9444 | 212.5347 | 248.4095 | 0.6805%
1930 | 12-82 | -81.7817 | 12.2877 | 1434.0362 | 106.0801 | 137.5621 | 180.3008 | 211.9724 | 247.8661 | 0.6671%
1931 | 12-82 | -82.053 | 12.2877 | 1452.01 | 104.8497 | 136.0649 | 178.9787 | 210.6631 | 246.371 | 0.6457%
1932 | 12-82.5 | -82.3243 | 12.2877 | 1469.9883 | 103.3426 | 134.1033 | 177.0272 | 208.6487 | 244.0068 | 0.618%
1933 | 12-82.5 | -82.5956 | 12.2877 | 1487.9711 | 101.7085 | 131.9276 | 174.7602 | 206.2595 | 241.1596 | 0.5882%
1934 | 12-83 | -82.867 | 12.2877 | 1505.958 | 100.0372 | 129.6519 | 172.3075 | 203.6435 | 238.0201 | 0.5582%
1935 | 12-83 | -83.1383 | 12.2877 | 1523.9491 | 98.3601 | 127.3153 | 169.7125 | 200.8538 | 234.6684 | 0.5286%
1936 | 12-83.5 | -83.4096 | 12.2877 | 1541.9439 | 96.619 | 124.8428 | 166.9234 | 197.8127 | 231.028 | 0.4985%
1937 | 12-83.5 | -83.6809 | 12.2877 | 1559.9426 | 94.8403 | 122.2738 | 163.9299 | 194.5996 | 227.2154 | 0.4686%
1938 | 12-84 | -83.9522 | 12.2877 | 1577.9447 | 93.06 | 119.6548 | 160.78 | 191.273 | 223.3065 | 0.4394%
1939 | 12-84 | -84.2236 | 12.2877 | 1595.9503 | 91.3232 | 117.0581 | 157.6 | 187.931 | 219.3833 | 0.4118%
1940 | 12-84.5 | -84.4949 | 12.2877 | 1613.9592 | 89.6733 | 114.5498 | 154.4763 | 184.6481 | 215.5349 | 0.3862%
1941 | 12-85 | -84.7662 | 12.2877 | 1631.9713 | 88.1081 | 112.1412 | 151.451 | 181.4561 | 211.8061 | 0.3627%
1942 | 12-85 | -85.0375 | 12.2877 | 1649.9863 | 86.5907 | 109.7882 | 148.4776 | 178.301 | 208.1205 | 0.3407%
1943 | 12-85.5 | -85.3089 | 12.2877 | 1668.0043 | 85.3871 | 107.9283 | 146.077 | 175.765 | 205.2273 | 0.3239%
1944 | 12-85.5 | -85.5802 | 12.2877 | 1686.025 | 84.5298 | 106.6372 | 144.3938 | 174.0089 | 203.3156 | 0.3126%
1945 | 12-86 | -85.8515 | 12.2877 | 1704.0484 | 83.9216 | 105.7654 | 143.2601 | 172.8769 | 202.1125 | 0.3054%
1946 | 12-86 | -86.1228 | 12.2877 | 1722.0744 | 83.4337 | 105.1012 | 142.4373 | 172.1054 | 201.286 | 0.3003%
1947 | 12-86.5 | -86.3941 | 12.2877 | 1740.1028 | 83.0658 | 104.6383 | 141.9364 | 171.688 | 200.8042 | 0.2972%
1948 | 12-86.5 | -86.6655 | 12.2877 | 1758.1336 | 82.8629 | 104.4186 | 141.798 | 171.624 | 200.6333 | 0.2961%
1949 | 12-87 | -86.9368 | 12.2877 | 1776.1667 | 82.9437 | 104.5971 | 142.178 | 172.0388 | 200.9164 | 0.298%
1950 | 12-87 | -87.2081 | 12.2877 | 1794.2019 | 83.4014 | 105.27 | 143.2011 | 172.9592 | 201.6843 | 0.3035%
1951 | 12-87.5 | -87.4794 | 12.2877 | 1812.2391 | 84.2204 | 106.3901 | 144.7555 | 174.2428 | 202.757 | 0.312%
1952 | 12-88 | -87.7507 | 12.2877 | 1830.2784 | 85.331 | 107.8355 | 146.6093 | 175.7099 | 203.9735 | 0.3227%
1953 | 12-88 | -88.0221 | 12.2877 | 1848.3196 | 86.7687 | 109.6564 | 148.7763 | 177.4143 | 205.4113 | 0.3361%
1954 | 12-88.5 | -88.2934 | 12.2877 | 1866.3626 | 88.5974 | 111.9565 | 151.3027 | 179.453 | 207.186 | 0.3535%
1955 | 12-88.5 | -88.5647 | 12.2877 | 1884.4073 | 90.8254 | 114.7882 | 154.2059 | 181.8749 | 209.3583 | 0.3758%
1956 | 12-89 | -88.836 | 12.2877 | 1902.4537 | 93.4982 | 118.2375 | 157.4787 | 184.7028 | 211.9568 | 0.4046%
1957 | 12-89 | -89.1074 | 12.2877 | 1920.5017 | 96.721 | 122.3698 | 161.1631 | 187.9782 | 215.0352 | 0.4423%
1958 | 12-89.5 | -89.3787 | 12.2877 | 1938.5513 | 100.7342 | 127.1628 | 165.5026 | 191.9617 | 218.9577 | 0.494%
1959 | 12-89.5 | -89.65 | 12.2877 | 1956.6023 | 105.1281 | 132.1779 | 170.0205 | 196.1194 | 223.1111 | 0.5577%
1960 | 12-90 | -89.9213 | 12.2877 | 1974.6546 | 109.9876 | 137.4084 | 174.6971 | 200.4579 | 227.5291 | 0.6376%
1961 | 12-90 | -90.1926 | 12.2877 | 1992.7084 | 115.1991 | 142.8633 | 179.557 | 205.0592 | 232.3354 | 0.7388%
1962 | 12-90.5 | -90.464 | 12.2877 | 2010.7633 | 120.6147 | 148.3741 | 184.3939 | 209.743 | 237.2921 | 0.8642%
1963 | 12-90.5 | -90.7353 | 12.2877 | 2028.8195 | 125.9442 | 153.6598 | 188.8919 | 214.1553 | 241.9556 | 1.012%
1964 | 13-50 | -50.0371 | 12.559 | 737.7548 | 114.7437 | 147.5925 | 187.6369 | 215.9422 | 248.5024 | 0.8195%
1965 | 13-50.5 | -50.3084 | 12.559 | 720.2544 | 114.6463 | 147.6665 | 187.7966 | 216.2282 | 248.9396 | 0.8201%
1966 | 13-50.5 | -50.5797 | 12.559 | 702.7885 | 114.5165 | 147.6984 | 187.9115 | 216.4543 | 249.2957 | 0.8199%
1967 | 13-51 | -50.851 | 12.559 | 685.3598 | 114.3699 | 147.701 | 187.9903 | 216.6289 | 249.5789 | 0.819%
1968 | 13-51 | -51.1224 | 12.559 | 667.9711 | 114.2282 | 147.6956 | 188.0497 | 216.7728 | 249.8159 | 0.818%
1969 | 13-51.5 | -51.3937 | 12.559 | 650.6257 | 114.0789 | 147.6662 | 188.0803 | 216.8726 | 249.9902 | 0.8166%
1970 | 13-51.5 | -51.665 | 12.559 | 633.3271 | 113.9426 | 147.6357 | 188.1111 | 216.9734 | 250.168 | 0.8154%
1971 | 13-52 | -51.9363 | 12.559 | 616.0795 | 113.8364 | 147.6209 | 188.1626 | 217.106 | 250.3942 | 0.8147%
1972 | 13-52 | -52.2077 | 12.559 | 598.8871 | 113.7356 | 147.5941 | 188.1984 | 217.2169 | 250.5916 | 0.8139%
1973 | 13-52.5 | -52.479 | 12.559 | 581.7549 | 113.6654 | 147.5856 | 188.2481 | 217.3473 | 250.817 | 0.8136%
1974 | 13-53 | -52.7503 | 12.559 | 564.6883 | 113.644 | 147.6124 | 188.3298 | 217.5229 | 251.1065 | 0.8143%
1975 | 13-53 | -53.0216 | 12.559 | 547.6937 | 113.6331 | 147.6213 | 188.3826 | 217.6557 | 251.3358 | 0.8147%
1976 | 13-53.5 | -53.2929 | 12.559 | 530.7778 | 113.6563 | 147.6356 | 188.4354 | 217.7955 | 251.5827 | 0.8156%
1977 | 13-53.5 | -53.5643 | 12.559 | 513.9486 | 113.7291 | 147.6682 | 188.5019 | 217.9643 | 251.8807 | 0.8173%
1978 | 13-54 | -53.8356 | 12.559 | 497.2147 | 113.8206 | 147.6986 | 188.5653 | 218.1346 | 252.1886 | 0.8192%
1979 | 13-54 | -54.1069 | 12.559 | 480.5862 | 113.9708 | 147.7742 | 188.6715 | 218.3736 | 252.6018 | 0.8222%
1980 | 13-54.5 | -54.3782 | 12.559 | 464.0745 | 114.1969 | 147.9101 | 188.8318 | 218.6959 | 253.139 | 0.8268%
1981 | 13-54.5 | -54.6495 | 12.559 | 447.6925 | 114.4519 | 148.054 | 188.9793 | 218.9972 | 253.6429 | 0.8317%
1982 | 13-55 | -54.9209 | 12.559 | 431.455 | 114.7606 | 148.2274 | 189.1241 | 219.2879 | 254.1234 | 0.8373%
1983 | 13-55 | -55.1922 | 12.559 | 415.3789 | 115.1352 | 148.4409 | 189.2708 | 219.5707 | 254.5802 | 0.8439%
1984 | 13-55.5 | -55.4635 | 12.559 | 399.4838 | 115.5446 | 148.6737 | 189.3939 | 219.8011 | 254.9445 | 0.8509%
1985 | 13-55.5 | -55.7348 | 12.559 | 383.7921 | 116.0294 | 148.9712 | 189.5469 | 220.0487 | 255.3082 | 0.8593%
1986 | 13-56 | -56.0061 | 12.559 | 368.33 | 116.6037 | 149.3505 | 189.7533 | 220.337 | 255.6943 | 0.8696%
1987 | 13-56.5 | -56.2775 | 12.559 | 353.1276 | 117.2126 | 149.7631 | 189.9766 | 220.6226 | 256.0501 | 0.8807%
1988 | 13-56.5 | -56.5488 | 12.559 | 338.2198 | 117.908 | 150.2703 | 190.2918 | 221.0056 | 256.5105 | 0.8942%
1989 | 13-57 | -56.8201 | 12.559 | 323.6476 | 118.6897 | 150.8747 | 190.7026 | 221.4846 | 257.0676 | 0.9101%
1990 | 13-57 | -57.0914 | 12.559 | 309.4582 | 119.4792 | 151.5035 | 191.1337 | 221.9568 | 257.5832 | 0.9268%
1991 | 13-57.5 | -57.3628 | 12.559 | 295.7068 | 120.3124 | 152.1799 | 191.6081 | 222.4537 | 258.0994 | 0.9449%
1992 | 13-57.5 | -57.6341 | 12.559 | 282.4574 | 121.1701 | 152.888 | 192.1119 | 222.9577 | 258.5938 | 0.9643%
1993 | 13-58 | -57.9054 | 12.559 | 269.7841 | 121.98 | 153.5624 | 192.5789 | 223.3904 | 258.9725 | 0.9829%
1994 | 13-58 | -58.1767 | 12.559 | 257.7718 | 122.7938 | 154.2603 | 193.0818 | 223.8585 | 259.3907 | 1.003%
1995 | 13-58.5 | -58.448 | 12.559 | 246.5171 | 123.585 | 154.96 | 193.6071 | 224.3486 | 259.8346 | 1.023%
1996 | 13-58.5 | -58.7194 | 12.559 | 236.1285 | 124.2968 | 155.6076 | 194.1108 | 224.8185 | 260.2627 | 1.041%
1997 | 13-59 | -58.9907 | 12.559 | 226.725 | 124.963 | 156.228 | 194.6237 | 225.3183 | 260.7483 | 1.06%
1998 | 13-59.5 | -59.262 | 12.559 | 218.434 | 125.551 | 156.7833 | 195.1062 | 225.7992 | 261.2308 | 1.076%
1999 | 13-59.5 | -59.5333 | 12.559 | 211.3864 | 126.0075 | 157.2187 | 195.4927 | 226.1797 | 261.6086 | 1.09%
2000 | 13-60 | -59.8046 | 12.559 | 205.7099 | 126.3886 | 157.5878 | 195.8281 | 226.5108 | 261.9408 | 1.101%
2001 | 13-60 | -60.076 | 12.559 | 201.5206 | 126.6669 | 157.8652 | 196.0869 | 226.7621 | 262.1902 | 1.109%
2002 | 13-60.5 | -60.3473 | 12.559 | 198.9124 | 126.8145 | 158.021 | 196.242 | 226.9072 | 262.3268 | 1.114%
2003 | 13-60.5 | -60.6186 | 12.559 | 197.9478 | 126.9069 | 158.1288 | 196.3694 | 227.0538 | 262.4921 | 1.117%
2004 | 13-61 | -60.8899 | 12.559 | 198.6509 | 126.9304 | 158.1816 | 196.4666 | 227.1931 | 262.6773 | 1.119%
2005 | 13-61 | -61.1613 | 12.559 | 201.004 | 126.8862 | 158.1879 | 196.5518 | 227.3383 | 262.9008 | 1.119%
2006 | 13-61.5 | -61.4326 | 12.559 | 204.9503 | 126.8428 | 158.2149 | 196.6947 | 227.5765 | 263.2669 | 1.119%
2007 | 13-61.5 | -61.7039 | 12.559 | 210.4003 | 126.7678 | 158.2262 | 196.8437 | 227.8439 | 263.6901 | 1.118%
2008 | 13-62 | -61.9752 | 12.559 | 217.2407 | 126.647 | 158.2027 | 196.968 | 228.0929 | 264.1011 | 1.117%
2009 | 13-62 | -62.2465 | 12.559 | 225.345 | 126.5292 | 158.194 | 197.1158 | 228.3741 | 264.5548 | 1.116%
2010 | 13-62.5 | -62.5179 | 12.559 | 234.5822 | 126.3936 | 158.1752 | 197.2537 | 228.6367 | 264.9784 | 1.114%
2011 | 13-63 | -62.7892 | 12.559 | 244.8242 | 126.241 | 158.1449 | 197.3775 | 228.8708 | 265.3549 | 1.112%
2012 | 13-63 | -63.0605 | 12.559 | 255.9502 | 126.1099 | 158.1439 | 197.5391 | 229.1482 | 265.7809 | 1.11%
2013 | 13-63.5 | -63.3318 | 12.559 | 267.8501 | 125.9798 | 158.1514 | 197.7162 | 229.439 | 266.2169 | 1.109%
2014 | 13-63.5 | -63.6031 | 12.559 | 280.4255 | 125.852 | 158.1712 | 197.9094 | 229.7436 | 266.6631 | 1.108%
2015 | 13-64 | -63.8745 | 12.559 | 293.5895 | 125.7507 | 158.2324 | 198.1485 | 230.099 | 267.1699 | 1.108%
2016 | 13-64 | -64.1458 | 12.559 | 307.2665 | 125.631 | 158.2779 | 198.361 | 230.4191 | 267.6275 | 1.108%
2017 | 13-64.5 | -64.4171 | 12.559 | 321.3909 | 125.4768 | 158.2804 | 198.4994 | 230.6642 | 267.9849 | 1.106%
2018 | 13-64.5 | -64.6884 | 12.559 | 335.9063 | 125.3004 | 158.2455 | 198.5649 | 230.8448 | 268.2555 | 1.103%
2019 | 13-65 | -64.9598 | 12.559 | 350.7642 | 125.1004 | 158.1787 | 198.5817 | 230.944 | 268.4024 | 1.099%
2020 | 13-65 | -65.2311 | 12.559 | 365.9228 | 124.9028 | 158.1152 | 198.6083 | 231.0145 | 268.4927 | 1.096%
2021 | 13-65.5 | -65.5024 | 12.559 | 381.3462 | 124.7334 | 158.0873 | 198.6911 | 231.1172 | 268.6116 | 1.093%
2022 | 13-66 | -65.7737 | 12.559 | 397.0036 | 124.5363 | 158.0201 | 198.7316 | 231.1483 | 268.6245 | 1.089%
2023 | 13-66 | -66.045 | 12.559 | 412.8683 | 124.3051 | 157.9061 | 198.7269 | 231.124 | 268.563 | 1.085%
2024 | 13-66.5 | -66.3164 | 12.559 | 428.9173 | 124.0504 | 157.7611 | 198.7041 | 231.0888 | 268.4947 | 1.079%
2025 | 13-66.5 | -66.5877 | 12.559 | 445.1307 | 123.6851 | 157.4591 | 198.5053 | 230.8578 | 268.176 | 1.07%
2026 | 13-67 | -66.859 | 12.559 | 461.491 | 123.2005 | 156.9851 | 198.0839 | 230.411 | 267.5844 | 1.057%
2027 | 13-67 | -67.1303 | 12.559 | 477.9832 | 122.607 | 156.3528 | 197.4389 | 229.7702 | 266.7525 | 1.04%
2028 | 13-67.5 | -67.4016 | 12.559 | 494.5941 | 121.9318 | 155.6194 | 196.6511 | 228.9728 | 265.7147 | 1.02%
2029 | 13-67.5 | -67.673 | 12.559 | 511.3121 | 121.2196 | 154.8446 | 195.8098 | 228.0935 | 264.5852 | 1%
2030 | 13-68 | -67.9443 | 12.559 | 528.127 | 120.4931 | 154.0578 | 194.9613 | 227.1767 | 263.4227 | 0.9799%
2031 | 13-68 | -68.2156 | 12.559 | 545.0298 | 119.8073 | 153.3484 | 194.2385 | 226.3386 | 262.3235 | 0.9617%
2032 | 13-68.5 | -68.4869 | 12.559 | 562.0125 | 119.1668 | 152.7195 | 193.6204 | 225.603 | 261.3391 | 0.9455%
2033 | 13-69 | -68.7583 | 12.559 | 579.0682 | 118.5719 | 152.1689 | 193.093 | 224.966 | 260.491 | 0.9311%
2034 | 13-69 | -69.0296 | 12.559 | 596.1905 | 117.8819 | 151.4703 | 192.4252 | 224.1519 | 259.4128 | 0.9141%
2035 | 13-69.5 | -69.3009 | 12.559 | 613.3737 | 117.1431 | 150.6854 | 191.6961 | 223.2435 | 258.2127 | 0.8958%
2036 | 13-69.5 | -69.5722 | 12.559 | 630.613 | 116.3774 | 149.8439 | 190.9375 | 222.2734 | 256.932 | 0.877%
2037 | 13-70 | -69.8435 | 12.559 | 647.9038 | 115.5744 | 148.9295 | 190.0578 | 221.1651 | 255.464 | 0.857%
2038 | 13-70 | -70.1149 | 12.559 | 665.2421 | 114.8204 | 148.068 | 189.1842 | 220.1003 | 254.0507 | 0.8385%
2039 | 13-70.5 | -70.3862 | 12.559 | 682.6242 | 114.1416 | 147.2975 | 188.3793 | 219.1332 | 252.7652 | 0.822%
2040 | 13-70.5 | -70.6575 | 12.559 | 700.0469 | 113.6289 | 146.779 | 187.8734 | 218.4342 | 251.8134 | 0.8105%
2041 | 13-71 | -70.9288 | 12.559 | 717.5071 | 113.2539 | 146.4544 | 187.5666 | 217.9637 | 251.1599 | 0.8027%
2042 | 13-71 | -71.2001 | 12.559 | 735.0023 | 113.0017 | 146.3039 | 187.4348 | 217.7153 | 250.7813 | 0.7982%
2043 | 13-71.5 | -71.4715 | 12.559 | 752.5298 | 112.7993 | 146.2338 | 187.4153 | 217.5726 | 250.5189 | 0.7952%
2044 | 13-71.5 | -71.7428 | 12.559 | 770.0875 | 112.5908 | 146.1536 | 187.3541 | 217.4149 | 250.2715 | 0.792%
2045 | 13-72 | -72.0141 | 12.559 | 787.6734 | 112.3584 | 146.0337 | 187.2339 | 217.2116 | 249.9961 | 0.7881%
2046 | 13-72.5 | -72.2854 | 12.559 | 805.2855 | 112.0462 | 145.788 | 186.9784 | 216.8728 | 249.5515 | 0.7821%
2047 | 13-72.5 | -72.5568 | 12.559 | 822.9222 | 111.7953 | 145.6415 | 186.8147 | 216.6734 | 249.3044 | 0.7779%
2048 | 13-73 | -72.8281 | 12.559 | 840.5819 | 111.6039 | 145.5899 | 186.7371 | 216.6075 | 249.2483 | 0.7754%
2049 | 13-73 | -73.0994 | 12.559 | 858.2631 | 111.4405 | 145.5827 | 186.6748 | 216.6015 | 249.2864 | 0.7736%
2050 | 13-73.5 | -73.3707 | 12.559 | 875.9646 | 111.3229 | 145.6423 | 186.7199 | 216.7299 | 249.5215 | 0.7733%
2051 | 13-73.5 | -73.642 | 12.559 | 893.6851 | 111.2552 | 145.7721 | 186.9021 | 216.9849 | 249.9392 | 0.7745%
2052 | 13-74 | -73.9134 | 12.559 | 911.4234 | 111.2339 | 145.9665 | 187.2257 | 217.3391 | 250.4931 | 0.7771%
2053 | 13-74 | -74.1847 | 12.559 | 929.1786 | 111.1774 | 146.0673 | 187.4754 | 217.6184 | 250.9703 | 0.7786%
2054 | 13-74.5 | -74.456 | 12.559 | 946.9496 | 111.0727 | 146.0543 | 187.6321 | 217.7755 | 251.3004 | 0.7784%
2055 | 13-74.5 | -74.7273 | 12.559 | 964.7356 | 110.8852 | 145.8815 | 187.6209 | 217.7197 | 251.3515 | 0.7756%
2056 | 13-75 | -74.9986 | 12.559 | 982.5357 | 110.6965 | 145.6494 | 187.5067 | 217.572 | 251.2881 | 0.7721%
2057 | 13-75.5 | -75.27 | 12.559 | 1000.3491 | 110.5049 | 145.3575 | 187.3052 | 217.3321 | 251.1081 | 0.7678%
2058 | 13-75.5 | -75.5413 | 12.559 | 1018.1752 | 110.3073 | 145.0118 | 187.0246 | 217.0114 | 250.8249 | 0.7627%
2059 | 13-76 | -75.8126 | 12.559 | 1036.0132 | 110.168 | 144.7032 | 186.746 | 216.7137 | 250.5783 | 0.7586%
2060 | 13-76 | -76.0839 | 12.559 | 1053.8625 | 110.0718 | 144.4138 | 186.4497 | 216.4138 | 250.3301 | 0.7548%
2061 | 13-76.5 | -76.3553 | 12.559 | 1071.7225 | 110.0016 | 144.1274 | 186.1246 | 216.0908 | 250.0475 | 0.7513%
2062 | 13-76.5 | -76.6266 | 12.559 | 1089.5927 | 110.0007 | 143.9045 | 185.8474 | 215.8205 | 249.8289 | 0.7489%
2063 | 13-77 | -76.8979 | 12.559 | 1107.4725 | 110.0492 | 143.7263 | 185.5943 | 215.5671 | 249.6189 | 0.7473%
2064 | 13-77 | -77.1692 | 12.559 | 1125.3616 | 110.125 | 143.5729 | 185.3382 | 215.2973 | 249.3667 | 0.7459%
2065 | 13-77.5 | -77.4405 | 12.559 | 1143.2593 | 110.2447 | 143.4576 | 185.0831 | 215.0366 | 249.1102 | 0.7452%
2066 | 13-77.5 | -77.7119 | 12.559 | 1161.1654 | 110.3843 | 143.3677 | 184.8304 | 214.786 | 248.8541 | 0.7448%
2067 | 13-78 | -77.9832 | 12.559 | 1179.0793 | 110.5426 | 143.315 | 184.6173 | 214.5936 | 248.6721 | 0.745%
2068 | 13-78.5 | -78.2545 | 12.559 | 1197.0007 | 110.7778 | 143.3696 | 184.5349 | 214.5721 | 248.7218 | 0.7472%
2069 | 13-78.5 | -78.5258 | 12.559 | 1214.9293 | 111.0397 | 143.4825 | 184.5438 | 214.6685 | 248.933 | 0.7506%
2070 | 13-79 | -78.7971 | 12.559 | 1232.8647 | 111.2992 | 143.6231 | 184.6164 | 214.8491 | 249.2621 | 0.7545%
2071 | 13-79 | -79.0685 | 12.559 | 1250.8067 | 111.5793 | 143.8103 | 184.765 | 215.1313 | 249.7343 | 0.7593%
2072 | 13-79.5 | -79.3398 | 12.559 | 1268.7548 | 111.8199 | 143.9858 | 184.9333 | 215.4411 | 250.2449 | 0.7639%
2073 | 13-79.5 | -79.6111 | 12.559 | 1286.7088 | 112.0083 | 144.139 | 185.1102 | 215.7611 | 250.768 | 0.7679%
2074 | 13-80 | -79.8824 | 12.559 | 1304.6685 | 112.1787 | 144.3073 | 185.3315 | 216.1376 | 251.3686 | 0.7721%
2075 | 13-80 | -80.1537 | 12.559 | 1322.6336 | 112.2558 | 144.4134 | 185.5267 | 216.4817 | 251.928 | 0.775%
2076 | 13-80.5 | -80.4251 | 12.559 | 1340.6038 | 112.2271 | 144.4435 | 185.6889 | 216.7891 | 252.4462 | 0.7762%
2077 | 13-80.5 | -80.6964 | 12.559 | 1358.579 | 112.118 | 144.4207 | 185.8493 | 217.1053 | 252.9911 | 0.7764%
2078 | 13-81 | -80.9677 | 12.559 | 1376.5588 | 111.8661 | 144.2736 | 185.9471 | 217.3628 | 253.4826 | 0.7743%
2079 | 13-81 | -81.239 | 12.559 | 1394.5432 | 111.4794 | 143.9999 | 185.9642 | 217.5407 | 253.8903 | 0.7699%
2080 | 13-81.5 | -81.5104 | 12.559 | 1412.5318 | 110.9928 | 143.6279 | 185.9086 | 217.6441 | 254.2137 | 0.7638%
2081 | 13-82 | -81.7817 | 12.559 | 1430.5246 | 110.1042 | 142.7083 | 185.2762 | 217.0806 | 253.6877 | 0.7483%
2082 | 13-82 | -82.053 | 12.559 | 1448.5213 | 108.8173 | 141.1755 | 183.9596 | 215.7482 | 252.18 | 0.7232%
2083 | 13-82.5 | -82.3243 | 12.559 | 1466.5218 | 107.2177 | 139.1336 | 182.0031 | 213.7082 | 249.7762 | 0.691%
2084 | 13-82.5 | -82.5956 | 12.559 | 1484.5259 | 105.4725 | 136.8586 | 179.7278 | 211.2913 | 246.8789 | 0.6564%
2085 | 13-83 | -82.867 | 12.559 | 1502.5335 | 103.6728 | 134.4655 | 177.2597 | 208.6435 | 243.6798 | 0.6216%
2086 | 13-83 | -83.1383 | 12.559 | 1520.5443 | 101.8495 | 131.9916 | 174.639 | 205.8148 | 240.2568 | 0.5873%
2087 | 13-83.5 | -83.4096 | 12.559 | 1538.5584 | 99.9322 | 129.3425 | 171.8009 | 202.7119 | 236.5107 | 0.5523%
2088 | 13-83.5 | -83.6809 | 12.559 | 1556.5754 | 97.9558 | 126.5638 | 168.74 | 199.4185 | 232.5613 | 0.5175%
2089 | 13-84 | -83.9522 | 12.559 | 1574.5953 | 95.9588 | 123.705 | 165.4848 | 195.9943 | 228.4899 | 0.4836%
2090 | 13-84 | -84.2236 | 12.559 | 1592.6181 | 94.0055 | 120.8672 | 162.2009 | 192.5533 | 224.4007 | 0.4517%
2091 | 13-84.5 | -84.4949 | 12.559 | 1610.6435 | 92.144 | 118.1202 | 158.9781 | 189.1703 | 220.3858 | 0.4224%
2092 | 13-85 | -84.7662 | 12.559 | 1628.6714 | 90.3778 | 115.4807 | 155.8632 | 185.8781 | 216.4901 | 0.3956%
2093 | 13-85 | -85.0375 | 12.559 | 1646.7017 | 88.6619 | 112.8921 | 152.7854 | 182.6134 | 212.6155 | 0.3705%
2094 | 13-85.5 | -85.3089 | 12.559 | 1664.7344 | 87.2891 | 110.8068 | 150.2772 | 179.981 | 209.54 | 0.3513%
2095 | 13-85.5 | -85.5802 | 12.559 | 1682.7694 | 86.2993 | 109.3345 | 148.4853 | 178.137 | 207.4533 | 0.3383%
2096 | 13-86 | -85.8515 | 12.559 | 1700.8064 | 85.5961 | 108.3258 | 147.2467 | 176.9054 | 206.0801 | 0.3296%
2097 | 13-86 | -86.1228 | 12.559 | 1718.8455 | 85.032 | 107.543 | 146.3169 | 176.0163 | 205.0697 | 0.3233%
2098 | 13-86.5 | -86.3941 | 12.559 | 1736.8866 | 84.6015 | 106.9743 | 145.708 | 175.4601 | 204.3883 | 0.319%
2099 | 13-86.5 | -86.6655 | 12.559 | 1754.9295 | 84.3537 | 106.6711 | 145.4827 | 175.2538 | 204.0308 | 0.3171%
2100 | 13-87 | -86.9368 | 12.559 | 1772.9742 | 84.4152 | 106.8048 | 145.7899 | 175.5331 | 204.1629 | 0.3184%
2101 | 13-87 | -87.2081 | 12.559 | 1791.0206 | 84.8674 | 107.4605 | 146.7421 | 176.32 | 204.8161 | 0.3237%
2102 | 13-87.5 | -87.4794 | 12.559 | 1809.0686 | 85.6803 | 108.5695 | 148.2358 | 177.4704 | 205.7825 | 0.3322%
2103 | 13-88 | -87.7507 | 12.559 | 1827.1182 | 86.7683 | 109.9853 | 150.0067 | 178.7962 | 206.886 | 0.3429%
2104 | 13-88 | -88.0221 | 12.559 | 1845.1693 | 88.1662 | 111.7585 | 152.0647 | 180.3547 | 208.2064 | 0.3564%
2105 | 13-88.5 | -88.2934 | 12.559 | 1863.2218 | 89.942 | 114 | 154.4579 | 182.2518 | 209.8716 | 0.374%
2106 | 13-88.5 | -88.5647 | 12.559 | 1881.2756 | 92.1221 | 116.789 | 157.2381 | 184.5471 | 211.9608 | 0.3969%
2107 | 13-89 | -88.836 | 12.559 | 1899.3307 | 94.7528 | 120.2126 | 160.3929 | 187.2604 | 214.4967 | 0.4267%
2108 | 13-89 | -89.1074 | 12.559 | 1917.387 | 97.9395 | 124.336 | 163.963 | 190.4346 | 217.531 | 0.4659%
2109 | 13-89.5 | -89.3787 | 12.559 | 1935.4445 | 101.9265 | 129.1427 | 168.193 | 194.3335 | 221.4294 | 0.5199%
2110 | 13-89.5 | -89.65 | 12.559 | 1953.5031 | 106.3105 | 134.1976 | 172.619 | 198.433 | 225.5863 | 0.5867%
2111 | 13-90 | -89.9213 | 12.559 | 1971.5628 | 111.1841 | 139.4833 | 177.224 | 202.7505 | 230.0439 | 0.6711%
2112 | 13-90 | -90.1926 | 12.559 | 1989.6234 | 116.4319 | 144.9929 | 182.0109 | 207.3512 | 234.8969 | 0.7784%
2113 | 13-90.5 | -90.464 | 12.559 | 2007.6849 | 121.911 | 150.5592 | 186.791 | 212.0585 | 239.9065 | 0.9119%
2114 | 13-90.5 | -90.7353 | 12.559 | 2025.7474 | 127.335 | 155.9047 | 191.2572 | 216.5243 | 244.6343 | 1.07%
2115 | 13-50 | -50.0371 | 12.8303 | 732.5531 | 118.2088 | 151.6555 | 190.6654 | 219.3553 | 252.3641 | 0.9025%
2116 | 13-50.5 | -50.3084 | 12.8303 | 714.9459 | 118.1157 | 151.7447 | 190.8487 | 219.6602 | 252.8232 | 0.9032%
2117 | 13-50.5 | -50.5797 | 12.8303 | 697.3675 | 117.9903 | 151.7951 | 190.9929 | 219.9103 | 253.2077 | 0.903%
2118 | 13-51 | -50.851 | 12.8303 | 679.8202 | 117.8491 | 151.819 | 191.1064 | 220.1139 | 253.5258 | 0.9022%
2119 | 13-51 | -51.1224 | 12.8303 | 662.3064 | 117.715 | 151.8376 | 191.206 | 220.2919 | 253.8037 | 0.9013%
2120 | 13-51.5 | -51.3937 | 12.8303 | 644.829 | 117.5741 | 151.8328 | 191.2763 | 220.4243 | 254.0154 | 0.9%
2121 | 13-51.5 | -51.665 | 12.8303 | 627.3909 | 117.4465 | 151.8257 | 191.3448 | 220.5558 | 254.2273 | 0.8989%
2122 | 13-52 | -51.9363 | 12.8303 | 609.9956 | 117.3492 | 151.8325 | 191.4318 | 220.7185 | 254.4869 | 0.8983%
2123 | 13-52 | -52.2077 | 12.8303 | 592.647 | 117.2549 | 151.8238 | 191.4983 | 220.8541 | 254.7113 | 0.8976%
2124 | 13-52.5 | -52.479 | 12.8303 | 575.3491 | 117.1911 | 151.8306 | 191.5754 | 221.0063 | 254.9599 | 0.8975%
2125 | 13-53 | -52.7503 | 12.8303 | 558.1068 | 117.1767 | 151.8701 | 191.6813 | 221.202 | 255.2705 | 0.8983%
2126 | 13-53 | -53.0216 | 12.8303 | 540.9254 | 117.1728 | 151.8898 | 191.7555 | 221.3517 | 255.5174 | 0.899%
2127 | 13-53.5 | -53.2929 | 12.8303 | 523.8109 | 117.203 | 151.9126 | 191.8276 | 221.5073 | 255.7809 | 0.9002%
2128 | 13-53.5 | -53.5643 | 12.8303 | 506.7702 | 117.2823 | 151.9506 | 191.9114 | 221.692 | 256.0959 | 0.9021%
2129 | 13-54 | -53.8356 | 12.8303 | 489.8109 | 117.3795 | 151.9834 | 191.986 | 221.8715 | 256.4116 | 0.9043%
2130 | 13-54 | -54.1069 | 12.8303 | 472.9419 | 117.5352 | 152.0585 | 192.1001 | 222.117 | 256.8271 | 0.9077%
2131 | 13-54.5 | -54.3782 | 12.8303 | 456.1731 | 117.7658 | 152.1907 | 192.2664 | 222.4452 | 257.3641 | 0.9128%
2132 | 13-54.5 | -54.6495 | 12.8303 | 439.5161 | 118.0246 | 152.3306 | 192.4228 | 222.7549 | 257.8718 | 0.9183%
2133 | 13-55 | -54.9209 | 12.8303 | 422.984 | 118.3365 | 152.501 | 192.5841 | 223.0627 | 258.3684 | 0.9247%
2134 | 13-55 | -55.1922 | 12.8303 | 406.5923 | 118.7129 | 152.712 | 192.7553 | 223.3711 | 258.8534 | 0.9322%
2135 | 13-55.5 | -55.4635 | 12.8303 | 390.3585 | 119.1209 | 152.9412 | 192.9034 | 223.6231 | 259.2386 | 0.9402%
2136 | 13-55.5 | -55.7348 | 12.8303 | 374.3032 | 119.6048 | 153.2363 | 193.0852 | 223.8945 | 259.6239 | 0.9499%
2137 | 13-56 | -56.0061 | 12.8303 | 358.4506 | 120.1818 | 153.6164 | 193.3262 | 224.2118 | 260.036 | 0.9618%
2138 | 13-56.5 | -56.2775 | 12.8303 | 342.8285 | 120.7985 | 154.0356 | 193.5921 | 224.5338 | 260.4258 | 0.9748%
2139 | 13-56.5 | -56.5488 | 12.8303 | 327.4702 | 121.5096 | 154.5551 | 193.9564 | 224.9623 | 260.9302 | 0.9907%
2140 | 13-57 | -56.8201 | 12.8303 | 312.4146 | 122.3165 | 155.1779 | 194.4222 | 225.4953 | 261.5404 | 1.01%
2141 | 13-57 | -57.0914 | 12.8303 | 297.7075 | 123.1366 | 155.8284 | 194.9085 | 226.023 | 262.1109 | 1.029%
2142 | 13-57.5 | -57.3628 | 12.8303 | 283.4032 | 124.0056 | 156.5289 | 195.4403 | 226.5817 | 262.6919 | 1.051%
2143 | 13-57.5 | -57.6341 | 12.8303 | 269.566 | 124.9049 | 157.2637 | 196.0024 | 227.1514 | 263.2575 | 1.075%
2144 | 13-58 | -57.9054 | 12.8303 | 256.2715 | 125.7615 | 157.968 | 196.5269 | 227.6498 | 263.7081 | 1.097%
2145 | 13-58 | -58.1767 | 12.8303 | 243.6086 | 126.6263 | 158.6949 | 197.0804 | 228.179 | 264.1916 | 1.121%
2146 | 13-58.5 | -58.448 | 12.8303 | 231.6808 | 127.4722 | 159.4225 | 197.6478 | 228.7231 | 264.6909 | 1.146%
2147 | 13-58.5 | -58.7194 | 12.8303 | 220.6076 | 128.2396 | 160.0966 | 198.1851 | 229.2374 | 265.1614 | 1.169%
2148 | 13-59 | -58.9907 | 12.8303 | 210.5238 | 128.9637 | 160.7434 | 198.7307 | 229.7831 | 265.6935 | 1.191%
2149 | 13-59.5 | -59.262 | 12.8303 | 201.5779 | 129.61 | 161.3235 | 199.2419 | 230.3059 | 266.2186 | 1.212%
2150 | 13-59.5 | -59.5333 | 12.8303 | 193.9275 | 130.1219 | 161.7799 | 199.6473 | 230.7147 | 266.6217 | 1.229%
2151 | 13-60 | -59.8046 | 12.8303 | 187.7311 | 130.5536 | 162.1641 | 199.9898 | 231.0583 | 266.9583 | 1.243%
2152 | 13-60 | -60.076 | 12.8303 | 183.1363 | 130.881 | 162.4576 | 200.2525 | 231.3177 | 267.2069 | 1.254%
2153 | 13-60.5 | -60.3473 | 12.8303 | 180.2656 | 131.0828 | 162.6426 | 200.4266 | 231.4868 | 267.3651 | 1.261%
2154 | 13-60.5 | -60.6186 | 12.8303 | 179.2019 | 131.2402 | 162.7969 | 200.5993 | 231.6803 | 267.5815 | 1.267%
2155 | 13-61 | -60.8899 | 12.8303 | 179.9773 | 131.3298 | 162.9003 | 200.7474 | 231.8701 | 267.8226 | 1.27%
2156 | 13-61 | -61.1613 | 12.8303 | 182.5683 | 131.34 | 162.9437 | 200.86 | 232.0437 | 268.0735 | 1.271%
2157 | 13-61.5 | -61.4326 | 12.8303 | 186.8994 | 131.3412 | 162.9938 | 201.0118 | 232.2912 | 268.4432 | 1.273%
2158 | 13-61.5 | -61.7039 | 12.8303 | 192.8534 | 131.3042 | 163.0222 | 201.1642 | 232.5598 | 268.861 | 1.273%
2159 | 13-62 | -61.9752 | 12.8303 | 200.2857 | 131.2202 | 163.019 | 201.2964 | 232.8149 | 269.2746 | 1.271%
2160 | 13-62 | -62.2465 | 12.8303 | 209.0385 | 131.1422 | 163.0357 | 201.4582 | 233.1111 | 269.7439 | 1.27%
2161 | 13-62.5 | -62.5179 | 12.8303 | 218.9537 | 131.0479 | 163.0464 | 201.6131 | 233.3933 | 270.1901 | 1.269%
2162 | 13-63 | -62.7892 | 12.8303 | 229.8807 | 130.9374 | 163.0487 | 201.7569 | 233.652 | 270.5967 | 1.267%
2163 | 13-63 | -63.0605 | 12.8303 | 241.6825 | 130.8503 | 163.0845 | 201.9462 | 233.9667 | 271.0718 | 1.267%
2164 | 13-63.5 | -63.3318 | 12.8303 | 254.2371 | 130.7654 | 163.1334 | 202.1585 | 234.3076 | 271.5765 | 1.266%
2165 | 13-63.5 | -63.6031 | 12.8303 | 267.4386 | 130.6789 | 163.192 | 202.3854 | 234.6626 | 272.0941 | 1.266%
2166 | 13-64 | -63.8745 | 12.8303 | 281.1958 | 130.608 | 163.2767 | 202.639 | 235.0486 | 272.6476 | 1.266%
2167 | 13-64 | -64.1458 | 12.8303 | 295.4312 | 130.518 | 163.3486 | 202.8686 | 235.3986 | 273.1503 | 1.266%
2168 | 13-64.5 | -64.4171 | 12.8303 | 310.0788 | 130.4082 | 163.4035 | 203.0681 | 235.704 | 273.5902 | 1.265%
2169 | 13-64.5 | -64.6884 | 12.8303 | 325.083 | 130.3039 | 163.4638 | 203.2665 | 236.0024 | 274.0153 | 1.264%
2170 | 13-65 | -64.9598 | 12.8303 | 340.3964 | 130.1766 | 163.4961 | 203.4175 | 236.2231 | 274.3239 | 1.263%
2171 | 13-65 | -65.2311 | 12.8303 | 355.9793 | 130.0369 | 163.5095 | 203.5357 | 236.3852 | 274.5407 | 1.261%
2172 | 13-65.5 | -65.5024 | 12.8303 | 371.7978 | 129.9065 | 163.5267 | 203.6553 | 236.5389 | 274.7361 | 1.259%
2173 | 13-66 | -65.7737 | 12.8303 | 387.8229 | 129.7434 | 163.498 | 203.7211 | 236.6105 | 274.813 | 1.255%
2174 | 13-66 | -66.045 | 12.8303 | 404.03 | 129.5484 | 163.4261 | 203.7486 | 236.6305 | 274.8221 | 1.251%
2175 | 13-66.5 | -66.3164 | 12.8303 | 420.3982 | 129.3337 | 163.3283 | 203.7668 | 236.6469 | 274.8352 | 1.245%
2176 | 13-66.5 | -66.5877 | 12.8303 | 436.9093 | 129.023 | 163.0991 | 203.6559 | 236.5003 | 274.6406 | 1.237%
2177 | 13-67 | -66.859 | 12.8303 | 453.5475 | 128.6105 | 162.7277 | 203.3769 | 236.1769 | 274.2226 | 1.224%
2178 | 13-67 | -67.1303 | 12.8303 | 470.2996 | 128.1065 | 162.2263 | 202.9259 | 235.6985 | 273.613 | 1.208%
2179 | 13-67.5 | -67.4016 | 12.8303 | 487.1536 | 127.5255 | 161.6351 | 202.3533 | 235.0735 | 272.8097 | 1.189%
2180 | 13-67.5 | -67.673 | 12.8303 | 504.0993 | 126.8995 | 160.9927 | 201.7156 | 234.3665 | 271.8964 | 1.169%
2181 | 13-68 | -67.9443 | 12.8303 | 521.1278 | 126.2456 | 160.3194 | 201.0395 | 233.6119 | 270.9187 | 1.148%
2182 | 13-68 | -68.2156 | 12.8303 | 538.2311 | 125.6006 | 159.6781 | 200.4145 | 232.8593 | 269.9296 | 1.129%
2183 | 13-68.5 | -68.4869 | 12.8303 | 555.4024 | 124.9945 | 159.109 | 199.8807 | 232.1863 | 269.0415 | 1.111%
2184 | 13-69 | -68.7583 | 12.8303 | 572.6355 | 124.4403 | 158.6287 | 199.4565 | 231.628 | 268.3066 | 1.096%
2185 | 13-69 | -69.0296 | 12.8303 | 589.925 | 123.7979 | 158.0136 | 198.9137 | 230.9007 | 267.3478 | 1.077%
2186 | 13-69.5 | -69.3009 | 12.8303 | 607.266 | 123.0994 | 157.3006 | 198.2881 | 230.058 | 266.2359 | 1.057%
2187 | 13-69.5 | -69.5722 | 12.8303 | 624.6542 | 122.3623 | 156.5109 | 197.5961 | 229.1239 | 265.0017 | 1.036%
2188 | 13-70 | -69.8435 | 12.8303 | 642.0857 | 121.5906 | 155.6539 | 196.7919 | 228.0486 | 263.5701 | 1.014%
2189 | 13-70 | -70.1149 | 12.8303 | 659.5572 | 120.8594 | 154.8344 | 195.9634 | 226.9883 | 262.1513 | 0.9928%
2190 | 13-70.5 | -70.3862 | 12.8303 | 677.0654 | 120.1927 | 154.0856 | 195.1649 | 225.991 | 260.8113 | 0.9736%
2191 | 13-70.5 | -70.6575 | 12.8303 | 694.6076 | 119.6736 | 153.5606 | 194.616 | 225.2206 | 259.7528 | 0.9596%
2192 | 13-71 | -70.9288 | 12.8303 | 712.1813 | 119.286 | 153.2182 | 194.2474 | 224.667 | 258.9783 | 0.9496%
2193 | 13-71 | -71.2001 | 12.8303 | 729.7841 | 119.0167 | 153.0411 | 194.0395 | 224.3132 | 258.4698 | 0.9434%
2194 | 13-71.5 | -71.4715 | 12.8303 | 747.414 | 118.7859 | 152.93 | 193.9208 | 224.0301 | 258.054 | 0.9385%
2195 | 13-71.5 | -71.7428 | 12.8303 | 765.0691 | 118.5565 | 152.8217 | 193.7834 | 223.7643 | 257.6738 | 0.9337%
2196 | 13-72 | -72.0141 | 12.8303 | 782.7476 | 118.3109 | 152.6872 | 193.6105 | 223.4813 | 257.2841 | 0.9284%
2197 | 13-72.5 | -72.2854 | 12.8303 | 800.448 | 117.9834 | 152.426 | 193.2975 | 223.0507 | 256.7084 | 0.9206%
2198 | 13-72.5 | -72.5568 | 12.8303 | 818.1688 | 117.7152 | 152.2618 | 193.0723 | 222.7562 | 256.3251 | 0.9147%
2199 | 13-73 | -72.8281 | 12.8303 | 835.9087 | 117.5053 | 152.193 | 192.9352 | 222.5959 | 256.1335 | 0.9108%
2200 | 13-73 | -73.0994 | 12.8303 | 853.6666 | 117.3275 | 152.1815 | 192.8407 | 222.5123 | 256.0573 | 0.908%
2201 | 13-73.5 | -73.3707 | 12.8303 | 871.4411 | 117.1845 | 152.2233 | 192.8355 | 222.5546 | 256.1704 | 0.9065%
2202 | 13-73.5 | -73.642 | 12.8303 | 889.2315 | 117.0757 | 152.3165 | 192.942 | 222.71 | 256.4518 | 0.9064%
2203 | 13-74 | -73.9134 | 12.8303 | 907.0366 | 116.9877 | 152.4427 | 193.1441 | 222.9347 | 256.8353 | 0.9072%
2204 | 13-74 | -74.1847 | 12.8303 | 924.8556 | 116.8452 | 152.4515 | 193.2401 | 223.0628 | 257.1134 | 0.906%
2205 | 13-74.5 | -74.456 | 12.8303 | 942.6878 | 116.6367 | 152.3264 | 193.2183 | 223.0509 | 257.2204 | 0.9026%
2206 | 13-74.5 | -74.7273 | 12.8303 | 960.5323 | 116.3342 | 152.032 | 193.0204 | 222.8172 | 257.0357 | 0.896%
2207 | 13-75 | -74.9986 | 12.8303 | 978.3884 | 116.0262 | 151.6746 | 192.7204 | 222.4954 | 256.739 | 0.8885%
2208 | 13-75.5 | -75.27 | 12.8303 | 996.2556 | 115.7115 | 151.2538 | 192.3335 | 222.084 | 256.3271 | 0.8803%
2209 | 13-75.5 | -75.5413 | 12.8303 | 1014.1331 | 115.3904 | 150.7795 | 191.8721 | 221.5966 | 255.817 | 0.8713%
2210 | 13-76 | -75.8126 | 12.8303 | 1032.0205 | 115.1369 | 150.3567 | 191.4458 | 221.1634 | 255.3835 | 0.8637%
2211 | 13-76 | -76.0839 | 12.8303 | 1049.9172 | 114.9369 | 149.9698 | 191.0393 | 220.7631 | 254.9953 | 0.8572%
2212 | 13-76.5 | -76.3553 | 12.8303 | 1067.8227 | 114.7727 | 149.6018 | 190.6398 | 220.3752 | 254.622 | 0.8513%
2213 | 13-76.5 | -76.6266 | 12.8303 | 1085.7365 | 114.6809 | 149.2991 | 190.2976 | 220.0582 | 254.3393 | 0.8469%
2214 | 13-77 | -76.8979 | 12.8303 | 1103.6582 | 114.6412 | 149.0435 | 189.988 | 219.7725 | 254.0866 | 0.8436%
2215 | 13-77 | -77.1692 | 12.8303 | 1121.5875 | 114.6345 | 148.8198 | 189.6905 | 219.4873 | 253.8155 | 0.8408%
2216 | 13-77.5 | -77.4405 | 12.8303 | 1139.5239 | 114.6871 | 148.6537 | 189.4297 | 219.2441 | 253.5842 | 0.8392%
2217 | 13-77.5 | -77.7119 | 12.8303 | 1157.4671 | 114.7758 | 148.5324 | 189.2027 | 219.038 | 253.3884 | 0.8385%
2218 | 13-78 | -77.9832 | 12.8303 | 1175.4168 | 114.8966 | 148.4624 | 189.0352 | 218.9079 | 253.2893 | 0.8387%
2219 | 13-78.5 | -78.2545 | 12.8303 | 1193.3725 | 115.1013 | 148.5025 | 189.0023 | 218.9587 | 253.4357 | 0.8413%
2220 | 13-78.5 | -78.5258 | 12.8303 | 1211.3342 | 115.3388 | 148.6038 | 189.0621 | 219.1339 | 253.7525 | 0.8453%
2221 | 13-79 | -78.7971 | 12.8303 | 1229.3013 | 115.5781 | 148.7343 | 189.1851 | 219.3972 | 254.1942 | 0.8499%
2222 | 13-79 | -79.0685 | 12.8303 | 1247.2738 | 115.8405 | 148.9111 | 189.3836 | 219.7674 | 254.7875 | 0.8555%
2223 | 13-79.5 | -79.3398 | 12.8303 | 1265.2512 | 116.0673 | 149.0794 | 189.6028 | 220.1682 | 255.4249 | 0.8608%
2224 | 13-79.5 | -79.6111 | 12.8303 | 1283.2335 | 116.2455 | 149.2283 | 189.8285 | 220.5767 | 256.0728 | 0.8655%
2225 | 13-80 | -79.8824 | 12.8303 | 1301.2204 | 116.4082 | 149.3924 | 190.0919 | 221.0345 | 256.7882 | 0.8703%
2226 | 13-80 | -80.1537 | 12.8303 | 1319.2116 | 116.4781 | 149.495 | 190.3204 | 221.4476 | 257.4476 | 0.8735%
2227 | 13-80.5 | -80.4251 | 12.8303 | 1337.207 | 116.4423 | 149.5221 | 190.5071 | 221.8125 | 258.0526 | 0.8747%
2228 | 13-80.5 | -80.6964 | 12.8303 | 1355.2064 | 116.3274 | 149.4967 | 190.684 | 222.1774 | 258.6752 | 0.8746%
2229 | 13-81 | -80.9677 | 12.8303 | 1373.2096 | 116.0717 | 149.3506 | 190.7936 | 222.4742 | 259.2329 | 0.8719%
2230 | 13-81 | -81.239 | 12.8303 | 1391.2164 | 115.6833 | 149.0832 | 190.8228 | 222.6872 | 259.7028 | 0.8665%
2231 | 13-81.5 | -81.5104 | 12.8303 | 1409.2266 | 115.1956 | 148.7221 | 190.7829 | 222.8266 | 260.0914 | 0.8592%
2232 | 13-82 | -81.7817 | 12.8303 | 1427.2402 | 114.2796 | 147.8077 | 190.1649 | 222.2766 | 259.6031 | 0.8411%
2233 | 13-82 | -82.053 | 12.8303 | 1445.2569 | 112.9284 | 146.2518 | 188.856 | 220.9315 | 258.1002 | 0.8118%
2234 | 13-82.5 | -82.3243 | 12.8303 | 1463.2766 | 111.226 | 144.1388 | 186.8954 | 218.8617 | 255.6707 | 0.7741%
2235 | 13-82.5 | -82.5956 | 12.8303 | 1481.2992 | 109.3582 | 141.7725 | 184.6099 | 216.4097 | 252.7324 | 0.7337%
2236 | 13-83 | -82.867 | 12.8303 | 1499.3245 | 107.419 | 139.271 | 182.1256 | 213.7224 | 249.4815 | 0.6932%
2237 | 13-83 | -83.1383 | 12.8303 | 1517.3525 | 105.4401 | 136.6717 | 179.4819 | 210.8492 | 245.996 | 0.6533%
2238 | 13-83.5 | -83.4096 | 12.8303 | 1535.3829 | 103.343 | 133.8666 | 176.6053 | 207.6858 | 242.16 | 0.6126%
2239 | 13-83.5 | -83.6809 | 12.8303 | 1553.4158 | 101.1692 | 130.9052 | 173.494 | 204.3194 | 238.0959 | 0.5722%
2240 | 13-84 | -83.9522 | 12.8303 | 1571.4509 | 98.9597 | 127.8391 | 170.1766 | 200.8093 | 233.8862 | 0.533%
2241 | 13-84 | -84.2236 | 12.8303 | 1589.4882 | 96.7864 | 124.7811 | 166.817 | 197.2639 | 229.636 | 0.4962%
2242 | 13-84.5 | -84.4949 | 12.8303 | 1607.5276 | 94.7004 | 121.8023 | 163.5033 | 193.7578 | 225.4386 | 0.4623%
2243 | 13-85 | -84.7662 | 12.8303 | 1625.569 | 92.7099 | 118.9239 | 160.2839 | 190.3247 | 221.3394 | 0.4315%
2244 | 13-85 | -85.0375 | 12.8303 | 1643.6123 | 90.7636 | 116.0787 | 157.0738 | 186.8942 | 217.2197 | 0.4026%
2245 | 13-85.5 | -85.3089 | 12.8303 | 1661.6574 | 89.1839 | 113.7337 | 154.4075 | 184.0954 | 213.889 | 0.3802%
2246 | 13-85.5 | -85.5802 | 12.8303 | 1679.7042 | 88.0204 | 112.0201 | 152.4377 | 182.0838 | 211.54 | 0.3646%
2247 | 13-86 | -85.8515 | 12.8303 | 1697.7527 | 87.1897 | 110.8273 | 151.0427 | 180.698 | 209.9305 | 0.3541%
2248 | 13-86 | -86.1228 | 12.8303 | 1715.8027 | 86.523 | 109.8881 | 149.9697 | 179.6468 | 208.6888 | 0.3461%
2249 | 13-86.5 | -86.3941 | 12.8303 | 1733.8542 | 86.0076 | 109.1817 | 149.2271 | 178.913 | 207.776 | 0.3404%
2250 | 13-86.5 | -86.6655 | 12.8303 | 1751.9072 | 85.6911 | 108.7609 | 148.8836 | 178.5224 | 207.204 | 0.3372%
2251 | 13-87 | -86.9368 | 12.8303 | 1769.9614 | 85.7032 | 108.8066 | 149.0744 | 178.6214 | 207.1549 | 0.3377%
2252 | 13-87 | -87.2081 | 12.8303 | 1788.017 | 86.1137 | 109.3917 | 149.9019 | 179.2386 | 207.6545 | 0.3423%
2253 | 13-87.5 | -87.4794 | 12.8303 | 1806.0738 | 86.8704 | 110.4154 | 151.2418 | 180.1995 | 208.4518 | 0.3503%
2254 | 13-88 | -87.7507 | 12.8303 | 1824.1317 | 87.8854 | 111.7294 | 152.8447 | 181.3335 | 209.3827 | 0.3603%
2255 | 13-88 | -88.0221 | 12.8303 | 1842.1907 | 89.195 | 113.3876 | 154.7221 | 182.7039 | 210.5341 | 0.3733%
2256 | 13-88.5 | -88.2934 | 12.8303 | 1860.2508 | 90.8722 | 115.5087 | 156.9256 | 184.4236 | 212.0424 | 0.3903%
2257 | 13-88.5 | -88.5647 | 12.8303 | 1878.3119 | 92.9588 | 118.1938 | 159.5275 | 186.5594 | 214.0039 | 0.4129%
2258 | 13-89 | -88.836 | 12.8303 | 1896.3738 | 95.5012 | 121.5294 | 162.5231 | 189.1277 | 216.4366 | 0.4426%
2259 | 13-89 | -89.1074 | 12.8303 | 1914.4367 | 98.6047 | 125.5803 | 165.9573 | 192.1748 | 219.3929 | 0.482%
2260 | 13-89.5 | -89.3787 | 12.8303 | 1932.5003 | 102.5017 | 130.31 | 170.0369 | 195.939 | 223.2023 | 0.5363%
2261 | 13-89.5 | -89.65 | 12.8303 | 1950.5648 | 106.803 | 135.2984 | 174.3115 | 199.9168 | 227.277 | 0.6035%
2262 | 13-90 | -89.9213 | 12.8303 | 1968.6299 | 111.608 | 140.5378 | 178.7694 | 204.1391 | 231.669 | 0.6887%
2263 | 13-90 | -90.1926 | 12.8303 | 1986.6958 | 116.7999 | 146.0065 | 183.4054 | 208.6613 | 236.4543 | 0.7968%
2264 | 13-90.5 | -90.464 | 12.8303 | 2004.7622 | 122.2426 | 151.5266 | 188.0556 | 213.3109 | 241.4005 | 0.9314%
2265 | 13-90.5 | -90.7353 | 12.8303 | 2022.8293 | 127.6632 | 156.8384 | 192.4305 | 217.7454 | 246.0915 | 1.092%
2266 | 13-50 | -50.0371 | 13.1017 | 727.7921 | 121.4715 | 155.3267 | 193.3688 | 222.3584 | 255.6962 | 0.9878%
2267 | 13-50.5 | -50.3084 | 13.1017 | 710.0877 | 121.3843 | 155.4286 | 193.5641 | 222.6778 | 256.1726 | 0.9885%
2268 | 13-50.5 | -50.5797 | 13.1017 | 692.4069 | 121.2652 | 155.4964 | 193.7253 | 222.9495 | 256.5843 | 0.9883%
2269 | 13-51 | -50.851 | 13.1017 | 674.7514 | 121.132 | 155.5425 | 193.8621 | 223.184 | 256.9427 | 0.9876%
2270 | 13-51 | -51.1224 | 13.1017 | 657.1233 | 121.0087 | 155.5879 | 193.9921 | 223.4032 | 257.275 | 0.9869%
2271 | 13-51.5 | -51.3937 | 13.1017 | 639.525 | 120.8792 | 155.6113 | 194.0945 | 223.5787 | 257.5432 | 0.9858%
2272 | 13-51.5 | -51.665 | 13.1017 | 621.959 | 120.7626 | 155.6313 | 194.1948 | 223.7521 | 257.8095 | 0.9849%
2273 | 13-52 | -51.9363 | 13.1017 | 604.4281 | 120.6762 | 155.6627 | 194.313 | 223.9555 | 258.1212 | 0.9847%
2274 | 13-52 | -52.2077 | 13.1017 | 586.9355 | 120.59 | 155.6751 | 194.4063 | 224.1257 | 258.3899 | 0.9841%
2275 | 13-52.5 | -52.479 | 13.1017 | 569.4848 | 120.5332 | 155.6993 | 194.5065 | 224.3079 | 258.6767 | 0.9841%
2276 | 13-53 | -52.7503 | 13.1017 | 552.0799 | 120.5257 | 155.752 | 194.6331 | 224.5301 | 259.021 | 0.9853%
2277 | 13-53 | -53.0216 | 13.1017 | 534.7254 | 120.5273 | 155.7827 | 194.7253 | 224.704 | 259.2997 | 0.9862%
2278 | 13-53.5 | -53.2929 | 13.1017 | 517.4263 | 120.5627 | 155.8141 | 194.8146 | 224.8829 | 259.5939 | 0.9876%
2279 | 13-53.5 | -53.5643 | 13.1017 | 500.1885 | 120.6461 | 155.8578 | 194.9155 | 225.0904 | 259.9389 | 0.9899%
2280 | 13-54 | -53.8356 | 13.1017 | 483.0184 | 120.7457 | 155.892 | 195.0013 | 225.2829 | 260.2694 | 0.9923%
2281 | 13-54 | -54.1069 | 13.1017 | 465.9237 | 120.9013 | 155.9628 | 195.1221 | 225.5318 | 260.6838 | 0.996%
2282 | 13-54.5 | -54.3782 | 13.1017 | 448.9129 | 121.1284 | 156.084 | 195.2912 | 225.8551 | 261.2056 | 1.001%
2283 | 13-54.5 | -54.6495 | 13.1017 | 431.9961 | 121.3816 | 156.2114 | 195.4499 | 226.1584 | 261.6953 | 1.007%
2284 | 13-55 | -54.9209 | 13.1017 | 415.1846 | 121.6869 | 156.3699 | 195.6183 | 226.4664 | 262.1828 | 1.014%
2285 | 13-55 | -55.1922 | 13.1017 | 398.492 | 122.0548 | 156.5693 | 195.8018 | 226.782 | 262.6678 | 1.022%
2286 | 13-55.5 | -55.4635 | 13.1017 | 381.9336 | 122.4509 | 156.7858 | 195.9594 | 227.0358 | 263.0445 | 1.031%
2287 | 13-55.5 | -55.7348 | 13.1017 | 365.528 | 122.9225 | 157.0688 | 196.1525 | 227.3095 | 263.4197 | 1.042%
2288 | 13-56 | -56.0061 | 13.1017 | 349.2965 | 123.4886 | 157.4386 | 196.4082 | 227.6317 | 263.8235 | 1.055%
2289 | 13-56.5 | -56.2775 | 13.1017 | 333.2646 | 124.0984 | 157.8527 | 196.6947 | 227.9663 | 264.215 | 1.069%
2290 | 13-56.5 | -56.5488 | 13.1017 | 317.4628 | 124.809 | 158.3712 | 197.0859 | 228.4147 | 264.7293 | 1.087%
2291 | 13-57 | -56.8201 | 13.1017 | 301.9269 | 125.6228 | 158.9976 | 197.5846 | 228.9741 | 265.3567 | 1.109%
2292 | 13-57 | -57.0914 | 13.1017 | 286.7004 | 126.4558 | 159.6549 | 198.1052 | 229.5304 | 265.9475 | 1.132%
2293 | 13-57.5 | -57.3628 | 13.1017 | 271.8353 | 127.3447 | 160.3664 | 198.6771 | 230.1278 | 266.5643 | 1.157%
2294 | 13-57.5 | -57.6341 | 13.1017 | 257.3941 | 128.2718 | 161.1168 | 199.2841 | 230.745 | 267.1798 | 1.184%
2295 | 13-58 | -57.9054 | 13.1017 | 243.4524 | 129.1652 | 161.8434 | 199.8579 | 231.2985 | 267.6923 | 1.211%
2296 | 13-58 | -58.1767 | 13.1017 | 230.1009 | 130.0735 | 162.5936 | 200.4605 | 231.8827 | 268.2374 | 1.239%
2297 | 13-58.5 | -58.448 | 13.1017 | 217.4486 | 130.969 | 163.3452 | 201.0749 | 232.4791 | 268.7949 | 1.268%
2298 | 13-58.5 | -58.7194 | 13.1017 | 205.6244 | 131.7898 | 164.0439 | 201.6552 | 233.0406 | 269.3174 | 1.296%
2299 | 13-59 | -58.9907 | 13.1017 | 194.7793 | 132.5721 | 164.717 | 202.2471 | 233.64 | 269.9116 | 1.323%
2300 | 13-59.5 | -59.262 | 13.1017 | 185.0854 | 133.2803 | 165.3244 | 202.8047 | 234.2177 | 270.5017 | 1.349%
2301 | 13-59.5 | -59.5333 | 13.1017 | 176.7324 | 133.855 | 165.8079 | 203.2514 | 234.6743 | 270.96 | 1.37%
2302 | 13-60 | -59.8046 | 13.1017 | 169.9181 | 134.3479 | 166.2151 | 203.6269 | 235.0526 | 271.3329 | 1.388%
2303 | 13-60 | -60.076 | 13.1017 | 164.8334 | 134.7354 | 166.5309 | 203.9171 | 235.3391 | 271.6071 | 1.402%
2304 | 13-60.5 | -60.3473 | 13.1017 | 161.6418 | 134.9985 | 166.7432 | 204.1204 | 235.538 | 271.7949 | 1.412%
2305 | 13-60.5 | -60.6186 | 13.1017 | 160.456 | 135.2212 | 166.9317 | 204.328 | 235.7682 | 272.0495 | 1.421%
2306 | 13-61 | -60.8899 | 13.1017 | 161.3205 | 135.3769 | 167.0725 | 204.512 | 235.9953 | 272.3286 | 1.427%
2307 | 13-61 | -61.1613 | 13.1017 | 164.2029 | 135.449 | 167.1501 | 204.6543 | 236.1967 | 272.6042 | 1.43%
2308 | 13-61.5 | -61.4326 | 13.1017 | 168.9998 | 135.508 | 167.2298 | 204.8291 | 236.463 | 272.9863 | 1.433%
2309 | 13-61.5 | -61.7039 | 13.1017 | 175.5545 | 135.5243 | 167.2853 | 205.0002 | 236.7445 | 273.4085 | 1.434%
2310 | 13-62 | -61.9752 | 13.1017 | 183.6789 | 135.4907 | 167.3099 | 205.1499 | 237.011 | 273.825 | 1.434%
2311 | 13-62 | -62.2465 | 13.1017 | 193.1749 | 135.4639 | 167.3564 | 205.3306 | 237.321 | 274.3005 | 1.434%
2312 | 13-62.5 | -62.5179 | 13.1017 | 203.851 | 135.4205 | 167.399 | 205.505 | 237.6182 | 274.7552 | 1.434%
2313 | 13-63 | -62.7892 | 13.1017 | 215.5319 | 135.36 | 167.4358 | 205.6698 | 237.8957 | 275.1767 | 1.433%
2314 | 13-63 | -63.0605 | 13.1017 | 228.0632 | 135.3233 | 167.5091 | 205.8861 | 238.2401 | 275.6841 | 1.434%
2315 | 13-63.5 | -63.3318 | 13.1017 | 241.3124 | 135.288 | 167.5982 | 206.1311 | 238.6222 | 276.2404 | 1.435%
2316 | 13-63.5 | -63.6031 | 13.1017 | 255.1678 | 135.2478 | 167.6964 | 206.3916 | 239.0235 | 276.8199 | 1.435%
2317 | 13-64 | -63.8745 | 13.1017 | 269.5358 | 135.2175 | 167.8143 | 206.6732 | 239.4502 | 277.4303 | 1.437%
2318 | 13-64 | -64.1458 | 13.1017 | 284.3388 | 135.1644 | 167.9175 | 206.9264 | 239.8353 | 277.9823 | 1.437%
2319 | 13-64.5 | -64.4171 | 13.1017 | 299.5122 | 135.0928 | 168.0089 | 207.1517 | 240.1777 | 278.4733 | 1.437%
2320 | 13-64.5 | -64.6884 | 13.1017 | 315.0025 | 135.0331 | 168.1174 | 207.3862 | 240.5257 | 278.9648 | 1.437%
2321 | 13-65 | -64.9598 | 13.1017 | 330.7652 | 134.9481 | 168.1988 | 207.5732 | 240.7983 | 279.3455 | 1.437%
2322 | 13-65 | -65.2311 | 13.1017 | 346.763 | 134.8454 | 168.2555 | 207.7219 | 241.0083 | 279.6324 | 1.435%
2323 | 13-65.5 | -65.5024 | 13.1017 | 362.9649 | 134.747 | 168.3083 | 207.8653 | 241.2036 | 279.8922 | 1.434%
2324 | 13-66 | -65.7737 | 13.1017 | 379.3447 | 134.6143 | 168.3145 | 207.9532 | 241.3172 | 280.0371 | 1.431%
2325 | 13-66 | -66.045 | 13.1017 | 395.8803 | 134.4508 | 168.28 | 208.0045 | 241.3838 | 280.1223 | 1.427%
2326 | 13-66.5 | -66.3164 | 13.1017 | 412.553 | 134.2699 | 168.2219 | 208.049 | 241.4519 | 280.2202 | 1.422%
2327 | 13-66.5 | -66.5877 | 13.1017 | 429.3467 | 134.0092 | 168.0616 | 207.9938 | 241.3931 | 280.1578 | 1.413%
2328 | 13-67 | -66.859 | 13.1017 | 446.2478 | 133.6676 | 167.794 | 207.8334 | 241.2004 | 279.9266 | 1.402%
2329 | 13-67 | -67.1303 | 13.1017 | 463.2445 | 133.2552 | 167.4301 | 207.5609 | 240.895 | 279.5566 | 1.387%
2330 | 13-67.5 | -67.4016 | 13.1017 | 480.3266 | 132.7677 | 166.9823 | 207.1765 | 240.4437 | 278.9922 | 1.37%
2331 | 13-67.5 | -67.673 | 13.1017 | 497.4854 | 132.2319 | 166.4798 | 206.7264 | 239.9035 | 278.3089 | 1.351%
2332 | 13-68 | -67.9443 | 13.1017 | 514.713 | 131.6636 | 165.9404 | 206.2358 | 239.3088 | 277.5531 | 1.33%
2333 | 13-68 | -68.2156 | 13.1017 | 532.0028 | 131.079 | 165.3978 | 205.7446 | 238.6744 | 276.7347 | 1.31%
2334 | 13-68.5 | -68.4869 | 13.1017 | 549.349 | 130.5148 | 164.8995 | 205.2954 | 238.0846 | 275.9709 | 1.292%
2335 | 13-69 | -68.7583 | 13.1017 | 566.7463 | 129.9878 | 164.4667 | 204.9089 | 237.5794 | 275.3192 | 1.275%
2336 | 13-69 | -69.0296 | 13.1017 | 584.1901 | 129.3691 | 163.8959 | 204.3904 | 236.8924 | 274.4237 | 1.254%
2337 | 13-69.5 | -69.3009 | 13.1017 | 601.6763 | 128.6885 | 163.2183 | 203.7757 | 236.0714 | 273.3474 | 1.232%
2338 | 13-69.5 | -69.5722 | 13.1017 | 619.2014 | 127.9627 | 162.4529 | 203.0826 | 235.1394 | 272.1194 | 1.207%
2339 | 13-70 | -69.8435 | 13.1017 | 636.7621 | 127.2135 | 161.6412 | 202.3076 | 234.079 | 270.7042 | 1.182%
2340 | 13-70 | -70.1149 | 13.1017 | 654.3555 | 126.502 | 160.8605 | 201.5185 | 233.0159 | 269.2732 | 1.159%
2341 | 13-70.5 | -70.3862 | 13.1017 | 671.9791 | 125.848 | 160.1366 | 200.7325 | 231.9904 | 267.8826 | 1.137%
2342 | 13-70.5 | -70.6575 | 13.1017 | 689.6304 | 125.3196 | 159.6018 | 200.1348 | 231.1434 | 266.7108 | 1.12%
2343 | 13-71 | -70.9288 | 13.1017 | 707.3074 | 124.9193 | 159.2429 | 199.7062 | 230.5077 | 265.8155 | 1.108%
2344 | 13-71 | -71.2001 | 13.1017 | 725.0082 | 124.6355 | 159.0452 | 199.4321 | 230.0708 | 265.1851 | 1.1%
2345 | 13-71.5 | -71.4715 | 13.1017 | 742.7311 | 124.3722 | 158.8876 | 199.2023 | 229.6725 | 264.6076 | 1.093%
2346 | 13-71.5 | -71.7428 | 13.1017 | 760.4744 | 124.1125 | 158.7358 | 198.9575 | 229.2943 | 264.069 | 1.086%
2347 | 13-72 | -72.0141 | 13.1017 | 778.2368 | 123.8424 | 158.5667 | 198.6917 | 228.9076 | 263.531 | 1.079%
2348 | 13-72.5 | -72.2854 | 13.1017 | 796.017 | 123.5033 | 158.2942 | 198.3265 | 228.3937 | 262.8317 | 1.069%
2349 | 13-72.5 | -72.5568 | 13.1017 | 813.8138 | 123.2255 | 158.1225 | 198.0563 | 228.0199 | 262.3294 | 1.061%
2350 | 13-73 | -72.8281 | 13.1017 | 831.6261 | 123.0072 | 158.0492 | 197.878 | 227.7843 | 262.0232 | 1.056%
2351 | 13-73 | -73.0994 | 13.1017 | 849.4528 | 122.8206 | 158.0388 | 197.7513 | 227.6325 | 261.8417 | 1.052%
2352 | 13-73.5 | -73.3707 | 13.1017 | 867.2932 | 122.6495 | 158.0546 | 197.6803 | 227.5825 | 261.8211 | 1.049%
2353 | 13-73.5 | -73.642 | 13.1017 | 885.1462 | 122.4909 | 158.0928 | 197.6777 | 227.6198 | 261.9391 | 1.047%
2354 | 13-74 | -73.9134 | 13.1017 | 903.0112 | 122.3271 | 158.132 | 197.7247 | 227.6981 | 262.1277 | 1.045%
2355 | 13-74 | -74.1847 | 13.1017 | 920.8875 | 122.0978 | 158.0431 | 197.6582 | 227.6763 | 262.2076 | 1.041%
2356 | 13-74.5 | -74.456 | 13.1017 | 938.7743 | 121.7914 | 157.8108 | 197.4685 | 227.5113 | 262.1131 | 1.033%
2357 | 13-74.5 | -74.7273 | 13.1017 | 956.671 | 121.3837 | 157.406 | 197.1057 | 227.1241 | 261.7259 | 1.022%
2358 | 13-75 | -74.9986 | 13.1017 | 974.5772 | 120.9791 | 156.9561 | 196.682 | 226.6796 | 261.2649 | 1.011%
2359 | 13-75.5 | -75.27 | 13.1017 | 992.4921 | 120.577 | 156.4612 | 196.2124 | 226.1742 | 260.7239 | 0.9987%
2360 | 13-75.5 | -75.5413 | 13.1017 | 1010.4155 | 120.177 | 155.9293 | 195.7037 | 225.6155 | 260.1122 | 0.9866%
2361 | 13-76 | -75.8126 | 13.1017 | 1028.3467 | 119.8462 | 155.4516 | 195.2415 | 225.1229 | 259.591 | 0.9762%
2362 | 13-76 | -76.0839 | 13.1017 | 1046.2853 | 119.5715 | 155.0141 | 194.8135 | 224.6782 | 259.1349 | 0.9672%
2363 | 13-76.5 | -76.3553 | 13.1017 | 1064.2311 | 119.336 | 154.6013 | 194.4082 | 224.2644 | 258.7198 | 0.9591%
2364 | 13-76.5 | -76.6266 | 13.1017 | 1082.1835 | 119.1761 | 154.2553 | 194.067 | 223.9355 | 258.4151 | 0.953%
2365 | 13-77 | -76.8979 | 13.1017 | 1100.1422 | 119.0721 | 153.9595 | 193.7666 | 223.6513 | 258.1593 | 0.9482%
2366 | 13-77 | -77.1692 | 13.1017 | 1118.1069 | 119.0074 | 153.7028 | 193.4902 | 223.3819 | 257.9048 | 0.9443%
2367 | 13-77.5 | -77.4405 | 13.1017 | 1136.0774 | 119.0126 | 153.5142 | 193.2681 | 223.1727 | 257.7137 | 0.9421%
2368 | 13-77.5 | -77.7119 | 13.1017 | 1154.0532 | 119.0646 | 153.3804 | 193.0928 | 223.0133 | 257.5742 | 0.9411%
2369 | 13-78 | -77.9832 | 13.1017 | 1172.0341 | 119.1581 | 153.3052 | 192.9839 | 222.9383 | 257.5416 | 0.9414%
2370 | 13-78.5 | -78.2545 | 13.1017 | 1190.02 | 119.3426 | 153.3426 | 193.0122 | 223.0534 | 257.7666 | 0.9446%
2371 | 13-78.5 | -78.5258 | 13.1017 | 1208.0104 | 119.5654 | 153.4432 | 193.1322 | 223.2966 | 258.1675 | 0.9492%
2372 | 13-79 | -78.7971 | 13.1017 | 1226.0052 | 119.7942 | 153.574 | 193.3131 | 223.63 | 258.6964 | 0.9546%
2373 | 13-79 | -79.0685 | 13.1017 | 1244.0043 | 120.0494 | 153.7514 | 193.5692 | 224.0759 | 259.385 | 0.9611%
2374 | 13-79.5 | -79.3398 | 13.1017 | 1262.0073 | 120.2732 | 153.9234 | 193.8469 | 224.5569 | 260.1265 | 0.9673%
2375 | 13-79.5 | -79.6111 | 13.1017 | 1280.014 | 120.4521 | 154.0788 | 194.1293 | 225.0469 | 260.8824 | 0.9728%
2376 | 13-80 | -79.8824 | 13.1017 | 1298.0244 | 120.6182 | 154.2491 | 194.4435 | 225.5827 | 261.7022 | 0.9784%
2377 | 13-80 | -80.1537 | 13.1017 | 1316.0382 | 120.6923 | 154.3588 | 194.7158 | 226.067 | 262.4593 | 0.982%
2378 | 13-80.5 | -80.4251 | 13.1017 | 1334.0553 | 120.6606 | 154.3928 | 194.9372 | 226.495 | 263.1544 | 0.9834%
2379 | 13-80.5 | -80.6964 | 13.1017 | 1352.0755 | 120.5496 | 154.3726 | 195.1378 | 226.9145 | 263.8588 | 0.9831%
2380 | 13-81 | -80.9677 | 13.1017 | 1370.0986 | 120.2977 | 154.2327 | 195.2627 | 227.2554 | 264.4863 | 0.9797%
2381 | 13-81 | -81.239 | 13.1017 | 1388.1246 | 119.9125 | 153.9739 | 195.3038 | 227.5058 | 265.018 | 0.9732%
2382 | 13-81.5 | -81.5104 | 13.1017 | 1406.1532 | 119.4264 | 153.6232 | 195.2751 | 227.6795 | 265.4657 | 0.9646%
2383 | 13-82 | -81.7817 | 13.1017 | 1424.1844 | 118.4855 | 152.7153 | 194.6712 | 227.145 | 265.0137 | 0.9434%
2384 | 13-82 | -82.053 | 13.1017 | 1442.2181 | 117.0733 | 151.1554 | 193.3771 | 225.7961 | 263.5247 | 0.9094%
2385 | 13-82.5 | -82.3243 | 13.1017 | 1460.254 | 115.2727 | 148.993 | 191.4267 | 223.7057 | 261.0909 | 0.8654%
2386 | 13-82.5 | -82.5956 | 13.1017 | 1478.2922 | 113.2891 | 146.5601 | 189.1504 | 221.2309 | 258.1451 | 0.8185%
2387 | 13-83 | -82.867 | 13.1017 | 1496.3325 | 111.2197 | 143.9785 | 186.6738 | 218.5228 | 254.8843 | 0.7715%
2388 | 13-83 | -83.1383 | 13.1017 | 1514.3748 | 109.0969 | 141.2863 | 184.0355 | 215.6288 | 251.3837 | 0.7254%
2389 | 13-83.5 | -83.4096 | 13.1017 | 1532.4189 | 106.837 | 138.3658 | 181.1564 | 212.4359 | 247.5125 | 0.6785%
2390 | 13-83.5 | -83.6809 | 13.1017 | 1550.4649 | 104.4868 | 135.2692 | 178.0361 | 209.0319 | 243.3936 | 0.6321%
2391 | 13-84 | -83.9522 | 13.1017 | 1568.5126 | 102.0891 | 132.0494 | 174.7032 | 205.4758 | 239.1098 | 0.5871%
2392 | 13-84 | -84.2236 | 13.1017 | 1586.562 | 99.7158 | 128.8185 | 171.3097 | 201.857 | 234.7518 | 0.545%
2393 | 13-84.5 | -84.4949 | 13.1017 | 1604.6129 | 97.4201 | 125.648 | 167.9415 | 198.2502 | 230.4145 | 0.5062%
2394 | 13-85 | -84.7662 | 13.1017 | 1622.6653 | 95.2141 | 122.5627 | 164.6481 | 194.6902 | 226.1446 | 0.4709%
2395 | 13-85 | -85.0375 | 13.1017 | 1640.7191 | 93.0386 | 119.4818 | 161.3399 | 191.1001 | 221.8037 | 0.4377%
2396 | 13-85.5 | -85.3089 | 13.1017 | 1658.7742 | 91.2428 | 116.8825 | 158.5318 | 188.1258 | 218.2227 | 0.4116%
2397 | 13-85.5 | -85.5802 | 13.1017 | 1676.8306 | 89.8886 | 114.9064 | 156.3805 | 185.9249 | 215.6006 | 0.3929%
2398 | 13-86 | -85.8515 | 13.1017 | 1694.8882 | 88.9392 | 113.5485 | 154.891 | 184.4186 | 213.8052 | 0.3805%
2399 | 13-86 | -86.1228 | 13.1017 | 1712.947 | 88.2049 | 112.5135 | 153.7635 | 183.2919 | 212.4446 | 0.3713%
2400 | 13-86.5 | -86.3941 | 13.1017 | 1731.0068 | 87.6617 | 111.7656 | 152.9928 | 182.5067 | 211.4641 | 0.3649%
2401 | 13-86.5 | -86.6655 | 13.1017 | 1749.0676 | 87.3019 | 111.2742 | 152.5785 | 182.0029 | 210.7726 | 0.3608%
2402 | 13-87 | -86.9368 | 13.1017 | 1767.1293 | 87.2571 | 111.228 | 152.6573 | 181.9474 | 210.57 | 0.3604%
2403 | 13-87 | -87.2081 | 13.1017 | 1785.192 | 87.5907 | 111.6965 | 153.3288 | 182.3765 | 210.8894 | 0.3642%
2404 | 13-87.5 | -87.4794 | 13.1017 | 1803.2555 | 88.2504 | 112.5803 | 154.4755 | 183.1235 | 211.4872 | 0.3712%
2405 | 13-88 | -87.7507 | 13.1017 | 1821.3198 | 89.1536 | 113.7419 | 155.875 | 184.0496 | 212.2278 | 0.3803%
2406 | 13-88 | -88.0221 | 13.1017 | 1839.3848 | 90.3375 | 115.238 | 157.5399 | 185.223 | 213.2025 | 0.3924%
2407 | 13-88.5 | -88.2934 | 13.1017 | 1857.4505 | 91.8787 | 117.1924 | 159.5216 | 186.7596 | 214.5503 | 0.4086%
2408 | 13-88.5 | -88.5647 | 13.1017 | 1875.5169 | 93.8351 | 119.7284 | 161.91 | 188.731 | 216.3821 | 0.4306%
2409 | 13-89 | -88.836 | 13.1017 | 1893.5838 | 96.2524 | 122.9303 | 164.7208 | 191.15 | 218.71 | 0.46%
2410 | 13-89 | -89.1074 | 13.1017 | 1911.6514 | 99.2313 | 126.8549 | 167.9948 | 194.0594 | 221.5798 | 0.4992%
2411 | 13-89.5 | -89.3787 | 13.1017 | 1929.7194 | 102.9571 | 131.3907 | 171.8158 | 197.6121 | 225.2081 | 0.5523%
2412 | 13-89.5 | -89.65 | 13.1017 | 1947.7879 | 107.0584 | 136.1394 | 175.7934 | 201.3325 | 229.0341 | 0.6173%
2413 | 13-90 | -89.9213 | 13.1017 | 1965.8568 | 111.646 | 141.1086 | 179.9335 | 205.275 | 233.1335 | 0.6988%
2414 | 13-90 | -90.1926 | 13.1017 | 1983.9262 | 116.6533 | 146.3542 | 184.2974 | 209.5798 | 237.6832 | 0.8028%
2415 | 13-90.5 | -90.464 | 13.1017 | 2001.9959 | 121.9507 | 151.7056 | 188.7323 | 214.0709 | 242.4597 | 0.9328%
2416 | 13-90.5 | -90.7353 | 13.1017 | 2020.0659 | 127.282 | 156.9082 | 192.9678 | 218.4208 | 247.0668 | 1.088%
2417 | 13-50 | -50.0371 | 13.373 | 723.4805 | 124.5921 | 158.6913 | 195.8609 | 225.0906 | 258.6849 | 1.077%
2418 | 13-50.5 | -50.3084 | 13.373 | 705.6893 | 124.514 | 158.8043 | 196.0665 | 225.4227 | 259.1768 | 1.078%
2419 | 13-50.5 | -50.5797 | 13.373 | 687.9166 | 124.4041 | 158.8878 | 196.2424 | 225.7136 | 259.613 | 1.077%
2420 | 13-51 | -50.851 | 13.373 | 670.164 | 124.282 | 158.9554 | 196.4008 | 225.9778 | 260.011 | 1.077%
2421 | 13-51 | -51.1224 | 13.373 | 652.4333 | 124.173 | 159.0281 | 196.5616 | 226.2402 | 260.4019 | 1.077%
2422 | 13-51.5 | -51.3937 | 13.373 | 634.7261 | 124.0578 | 159.0812 | 196.6978 | 226.4637 | 260.7359 | 1.076%
2423 | 13-51.5 | -51.665 | 13.373 | 617.0446 | 123.9554 | 159.1304 | 196.8334 | 226.6872 | 261.0708 | 1.075%
2424 | 13-52 | -51.9363 | 13.373 | 599.3912 | 123.8829 | 159.1894 | 196.9877 | 226.9418 | 261.4524 | 1.075%
2425 | 13-52 | -52.2077 | 13.373 | 581.7682 | 123.8082 | 159.2264 | 197.1132 | 227.1577 | 261.7833 | 1.075%
2426 | 13-52.5 | -52.479 | 13.373 | 564.1787 | 123.761 | 159.2707 | 197.2418 | 227.3801 | 262.1251 | 1.075%
2427 | 13-53 | -52.7503 | 13.373 | 546.626 | 123.7617 | 159.3387 | 197.3931 | 227.6378 | 262.5183 | 1.077%
2428 | 13-53 | -53.0216 | 13.373 | 529.1136 | 123.768 | 159.3806 | 197.5062 | 227.8431 | 262.8416 | 1.078%
2429 | 13-53.5 | -53.2929 | 13.373 | 511.6457 | 123.8063 | 159.42 | 197.6145 | 228.0504 | 263.1761 | 1.08%
2430 | 13-53.5 | -53.5643 | 13.373 | 494.2272 | 123.8908 | 159.4684 | 197.7332 | 228.2839 | 263.5571 | 1.082%
2431 | 13-54 | -53.8356 | 13.373 | 476.8633 | 123.9882 | 159.5021 | 197.83 | 228.4906 | 263.9057 | 1.085%
2432 | 13-54 | -54.1069 | 13.373 | 459.5605 | 124.1376 | 159.5649 | 197.9547 | 228.7407 | 264.3174 | 1.089%
2433 | 13-54.5 | -54.3782 | 13.373 | 442.3257 | 124.3528 | 159.6701 | 198.1212 | 229.0529 | 264.817 | 1.094%
2434 | 13-54.5 | -54.6495 | 13.373 | 425.1675 | 124.5913 | 159.7787 | 198.2747 | 229.3404 | 265.2768 | 1.1%
2435 | 13-55 | -54.9209 | 13.373 | 408.0953 | 124.8808 | 159.9183 | 198.4412 | 229.6363 | 265.7388 | 1.107%
2436 | 13-55 | -55.1922 | 13.373 | 391.1205 | 125.231 | 160.099 | 198.6264 | 229.9442 | 266.2037 | 1.116%
2437 | 13-55.5 | -55.4635 | 13.373 | 374.2565 | 125.6056 | 160.2952 | 198.7811 | 230.1823 | 266.5477 | 1.125%
2438 | 13-55.5 | -55.7348 | 13.373 | 357.5189 | 126.0545 | 160.5574 | 198.9718 | 230.4392 | 266.8872 | 1.136%
2439 | 13-56 | -56.0061 | 13.373 | 340.9262 | 126.5981 | 160.9072 | 199.2265 | 230.7453 | 267.255 | 1.15%
2440 | 13-56.5 | -56.2775 | 13.373 | 324.5009 | 127.1882 | 161.3053 | 199.5163 | 231.0701 | 267.6193 | 1.166%
2441 | 13-56.5 | -56.5488 | 13.373 | 308.2697 | 127.8841 | 161.8108 | 199.9159 | 231.5146 | 268.1134 | 1.186%
2442 | 13-57 | -56.8201 | 13.373 | 292.2649 | 128.69 | 162.4276 | 200.4277 | 232.0759 | 268.7278 | 1.209%
2443 | 13-57 | -57.0914 | 13.373 | 276.5259 | 129.5224 | 163.0798 | 200.9643 | 232.6385 | 269.3117 | 1.235%
2444 | 13-57.5 | -57.3628 | 13.373 | 261.1007 | 130.4195 | 163.7914 | 201.5596 | 233.2542 | 269.94 | 1.263%
2445 | 13-57.5 | -57.6341 | 13.373 | 246.0485 | 131.3649 | 164.548 | 202.197 | 233.9015 | 270.5846 | 1.294%
2446 | 13-58 | -57.9054 | 13.373 | 231.442 | 132.2873 | 165.289 | 202.8085 | 234.497 | 271.144 | 1.325%
2447 | 13-58 | -58.1767 | 13.373 | 217.3711 | 133.2329 | 166.0557 | 203.4511 | 235.1268 | 271.7412 | 1.358%
2448 | 13-58.5 | -58.448 | 13.373 | 203.9468 | 134.1735 | 166.8258 | 204.106 | 235.77 | 272.3528 | 1.392%
2449 | 13-58.5 | -58.7194 | 13.373 | 191.3052 | 135.0449 | 167.5452 | 204.7257 | 236.377 | 272.928 | 1.425%
2450 | 13-59 | -58.9907 | 13.373 | 179.6117 | 135.8852 | 168.2428 | 205.3633 | 237.032 | 273.59 | 1.457%
2451 | 13-59.5 | -59.262 | 13.373 | 169.0631 | 136.6578 | 168.8783 | 205.9711 | 237.6724 | 274.2581 | 1.488%
2452 | 13-59.5 | -59.5333 | 13.373 | 159.8862 | 137.3012 | 169.3931 | 206.4689 | 238.1926 | 274.7952 | 1.514%
2453 | 13-60 | -59.8046 | 13.373 | 152.3292 | 137.8646 | 169.8312 | 206.8923 | 238.6287 | 275.2375 | 1.536%
2454 | 13-60 | -60.076 | 13.373 | 146.6427 | 138.3235 | 170.178 | 207.2275 | 238.9679 | 275.5735 | 1.555%
2455 | 13-60.5 | -60.3473 | 13.373 | 143.05 | 138.658 | 170.4228 | 207.4736 | 239.2166 | 275.8192 | 1.569%
2456 | 13-60.5 | -60.6186 | 13.373 | 141.7104 | 138.9528 | 170.6449 | 207.7233 | 239.4947 | 276.1283 | 1.582%
2457 | 13-61 | -60.8899 | 13.373 | 142.6874 | 139.1806 | 170.821 | 207.9482 | 239.7668 | 276.4565 | 1.591%
2458 | 13-61 | -61.1613 | 13.373 | 145.9344 | 139.3236 | 170.9355 | 208.1288 | 240.0079 | 276.7725 | 1.597%
2459 | 13-61.5 | -61.4326 | 13.373 | 151.3054 | 139.4523 | 171.0513 | 208.3386 | 240.3078 | 277.1853 | 1.603%
2460 | 13-61.5 | -61.7039 | 13.373 | 158.5848 | 139.535 | 171.142 | 208.5404 | 240.616 | 277.6281 | 1.607%
2461 | 13-62 | -61.9752 | 13.373 | 167.5238 | 139.5635 | 171.2007 | 208.7161 | 240.9023 | 278.0551 | 1.609%
2462 | 13-62 | -62.2465 | 13.373 | 177.8725 | 139.5981 | 171.2808 | 208.921 | 241.2289 | 278.5367 | 1.611%
2463 | 13-62.5 | -62.5179 | 13.373 | 189.4 | 139.6142 | 171.3575 | 209.1177 | 241.5408 | 278.9951 | 1.612%
2464 | 13-63 | -62.7892 | 13.373 | 201.9043 | 139.611 | 171.4292 | 209.3045 | 241.8342 | 279.4238 | 1.613%
2465 | 13-63 | -63.0605 | 13.373 | 215.2154 | 139.6305 | 171.5384 | 209.5453 | 242.2006 | 279.9492 | 1.615%
2466 | 13-63.5 | -63.3318 | 13.373 | 229.1926 | 139.6486 | 171.6641 | 209.8171 | 242.6118 | 280.5365 | 1.618%
2467 | 13-63.5 | -63.6031 | 13.373 | 243.7213 | 139.6577 | 171.798 | 210.1055 | 243.0475 | 281.1584 | 1.62%
2468 | 13-64 | -63.8745 | 13.373 | 258.7087 | 139.673 | 171.9492 | 210.4147 | 243.5111 | 281.817 | 1.623%
2469 | 13-64 | -64.1458 | 13.373 | 274.0795 | 139.6595 | 172.0812 | 210.6896 | 243.926 | 282.4089 | 1.624%
2470 | 13-64.5 | -64.4171 | 13.373 | 289.7726 | 139.6207 | 172.1959 | 210.9288 | 244.2881 | 282.9266 | 1.625%
2471 | 13-64.5 | -64.6884 | 13.373 | 305.7385 | 139.5888 | 172.3229 | 211.1713 | 244.6483 | 283.4356 | 1.626%
2472 | 13-65 | -64.9598 | 13.373 | 321.9364 | 139.5274 | 172.4218 | 211.3649 | 244.9336 | 283.8369 | 1.625%
2473 | 13-65 | -65.2311 | 13.373 | 338.3331 | 139.4466 | 172.4984 | 211.5227 | 245.1626 | 284.1556 | 1.624%
2474 | 13-65.5 | -65.5024 | 13.373 | 354.901 | 139.3711 | 172.5746 | 211.6797 | 245.3854 | 284.4609 | 1.623%
2475 | 13-66 | -65.7737 | 13.373 | 371.6172 | 139.2611 | 172.6072 | 211.7848 | 245.5345 | 284.6652 | 1.62%
2476 | 13-66 | -66.045 | 13.373 | 388.4625 | 139.1211 | 172.6016 | 211.8565 | 245.6437 | 284.8218 | 1.616%
2477 | 13-66.5 | -66.3164 | 13.373 | 405.4208 | 138.9657 | 172.5748 | 211.9246 | 245.7603 | 285.0005 | 1.611%
2478 | 13-66.5 | -66.5877 | 13.373 | 422.4784 | 138.7441 | 172.4718 | 211.9159 | 245.781 | 285.06 | 1.603%
2479 | 13-67 | -66.859 | 13.373 | 439.6239 | 138.4599 | 172.2936 | 211.8304 | 245.7044 | 284.9971 | 1.593%
2480 | 13-67 | -67.1303 | 13.373 | 456.8472 | 138.1242 | 172.0506 | 211.6825 | 245.5506 | 284.8396 | 1.58%
2481 | 13-67.5 | -67.4016 | 13.373 | 474.1398 | 137.7142 | 171.727 | 211.4263 | 245.2474 | 284.481 | 1.563%
2482 | 13-67.5 | -67.673 | 13.373 | 491.4945 | 137.2558 | 171.3493 | 211.1042 | 244.8538 | 284.0013 | 1.545%
2483 | 13-68 | -67.9443 | 13.373 | 508.9048 | 136.7661 | 170.9366 | 210.7442 | 244.4093 | 283.4547 | 1.526%
2484 | 13-68 | -68.2156 | 13.373 | 526.3653 | 136.2417 | 170.496 | 210.3402 | 243.8982 | 282.8126 | 1.506%
2485 | 13-68.5 | -68.4869 | 13.373 | 543.8709 | 135.7166 | 170.0672 | 209.9428 | 243.3929 | 282.1751 | 1.486%
2486 | 13-69 | -68.7583 | 13.373 | 561.4176 | 135.2074 | 169.6691 | 209.5772 | 242.9301 | 281.5936 | 1.467%
2487 | 13-69 | -69.0296 | 13.373 | 579.0016 | 134.603 | 169.1299 | 209.0714 | 242.2723 | 280.7488 | 1.444%
2488 | 13-69.5 | -69.3009 | 13.373 | 596.6195 | 133.9358 | 168.4836 | 208.4641 | 241.4699 | 279.7056 | 1.419%
2489 | 13-69.5 | -69.5722 | 13.373 | 614.2683 | 133.2233 | 167.7496 | 207.7741 | 240.5469 | 278.4944 | 1.392%
2490 | 13-70 | -69.8435 | 13.373 | 631.9455 | 132.4992 | 166.9915 | 207.0163 | 239.5085 | 277.107 | 1.364%
2491 | 13-70 | -70.1149 | 13.373 | 649.6488 | 131.8125 | 166.2621 | 206.2559 | 238.4561 | 275.6841 | 1.338%
2492 | 13-70.5 | -70.3862 | 13.373 | 667.376 | 131.1792 | 165.5798 | 205.5083 | 237.4231 | 274.2736 | 1.314%
2493 | 13-70.5 | -70.6575 | 13.373 | 685.1252 | 130.6466 | 165.0466 | 204.8831 | 236.5161 | 273.0125 | 1.295%
2494 | 13-71 | -70.9288 | 13.373 | 702.8948 | 130.2361 | 164.6783 | 204.4078 | 235.8084 | 272.0117 | 1.28%
2495 | 13-71 | -71.2001 | 13.373 | 720.6833 | 129.9375 | 164.4632 | 204.0733 | 235.2925 | 271.2663 | 1.271%
2496 | 13-71.5 | -71.4715 | 13.373 | 738.4892 | 129.6409 | 164.2606 | 203.7406 | 234.7823 | 270.5317 | 1.261%
2497 | 13-71.5 | -71.7428 | 13.373 | 756.3112 | 129.3481 | 164.0621 | 203.413 | 234.2896 | 269.8312 | 1.251%
2498 | 13-72 | -72.0141 | 13.373 | 774.1483 | 129.0497 | 163.8523 | 203.0757 | 233.794 | 269.1371 | 1.242%
2499 | 13-72.5 | -72.2854 | 13.373 | 791.9994 | 128.7008 | 163.5712 | 202.6639 | 233.2027 | 268.3212 | 1.23%
2500 | 13-72.5 | -72.5568 | 13.373 | 809.8636 | 128.4139 | 163.3912 | 202.3493 | 232.7543 | 267.7057 | 1.221%
2501 | 13-73 | -72.8281 | 13.373 | 827.7399 | 128.1846 | 163.3075 | 202.1269 | 232.4442 | 267.2864 | 1.215%
2502 | 13-73 | -73.0994 | 13.373 | 845.6277 | 127.9808 | 163.2822 | 201.9536 | 232.215 | 266.9884 | 1.209%
2503 | 13-73.5 | -73.3707 | 13.373 | 863.526 | 127.7735 | 163.2557 | 201.8154 | 232.063 | 266.8217 | 1.204%
2504 | 13-73.5 | -73.642 | 13.373 | 881.4344 | 127.5582 | 163.2241 | 201.7084 | 231.9735 | 266.7644 | 1.199%
2505 | 13-74 | -73.9134 | 13.373 | 899.3521 | 127.3165 | 163.167 | 201.6108 | 231.9024 | 266.7528 | 1.193%
2506 | 13-74 | -74.1847 | 13.373 | 917.2787 | 127.0085 | 162.9862 | 201.415 | 231.7454 | 266.6518 | 1.185%
2507 | 13-74.5 | -74.456 | 13.373 | 935.2134 | 126.6215 | 162.6658 | 201.1109 | 231.458 | 266.3943 | 1.173%
2508 | 13-74.5 | -74.7273 | 13.373 | 953.156 | 126.1323 | 162.1794 | 200.6502 | 230.9606 | 265.8605 | 1.158%
2509 | 13-75 | -74.9986 | 13.373 | 971.1058 | 125.6594 | 161.6734 | 200.1753 | 230.4446 | 265.3024 | 1.142%
2510 | 13-75.5 | -75.27 | 13.373 | 989.0625 | 125.2017 | 161.1478 | 199.6822 | 229.9031 | 264.7098 | 1.127%
2511 | 13-75.5 | -75.5413 | 13.373 | 1007.0258 | 124.756 | 160.6061 | 199.1705 | 229.3339 | 264.0777 | 1.112%
2512 | 13-76 | -75.8126 | 13.373 | 1024.9951 | 124.3761 | 160.1141 | 198.7069 | 228.8312 | 263.5349 | 1.1%
2513 | 13-76 | -76.0839 | 13.373 | 1042.9702 | 124.05 | 159.6595 | 198.28 | 228.3789 | 263.0598 | 1.088%
2514 | 13-76.5 | -76.3553 | 13.373 | 1060.9509 | 123.7623 | 159.2287 | 197.8793 | 227.9626 | 262.6328 | 1.078%
2515 | 13-76.5 | -76.6266 | 13.373 | 1078.9366 | 123.5526 | 158.8649 | 197.5486 | 227.6393 | 262.3269 | 1.07%
2516 | 13-77 | -76.8979 | 13.373 | 1096.9273 | 123.4023 | 158.5538 | 197.265 | 227.3695 | 262.0819 | 1.064%
2517 | 13-77 | -77.1692 | 13.373 | 1114.9226 | 123.2968 | 158.2867 | 197.0129 | 227.1246 | 261.8519 | 1.059%
2518 | 13-77.5 | -77.4405 | 13.373 | 1132.9222 | 123.2676 | 158.0924 | 196.8247 | 226.9487 | 261.6962 | 1.056%
2519 | 13-77.5 | -77.7119 | 13.373 | 1150.9261 | 123.2921 | 157.9571 | 196.6884 | 226.828 | 261.5985 | 1.055%
2520 | 13-78 | -77.9832 | 13.373 | 1168.9338 | 123.3652 | 157.8837 | 196.6212 | 226.7953 | 261.6119 | 1.055%
2521 | 13-78.5 | -78.2545 | 13.373 | 1186.9453 | 123.5363 | 157.925 | 196.6953 | 226.9594 | 261.8915 | 1.059%
2522 | 13-78.5 | -78.5258 | 13.373 | 1204.9603 | 123.7508 | 158.0304 | 196.8602 | 227.252 | 262.3471 | 1.064%
2523 | 13-79 | -78.7971 | 13.373 | 1222.9787 | 123.9754 | 158.1665 | 197.0847 | 227.6339 | 262.9294 | 1.071%
2524 | 13-79 | -79.0685 | 13.373 | 1241.0002 | 124.2308 | 158.3499 | 197.3873 | 228.1325 | 263.6772 | 1.078%
2525 | 13-79.5 | -79.3398 | 13.373 | 1259.0248 | 124.4601 | 158.5317 | 197.7144 | 228.6725 | 264.4884 | 1.085%
2526 | 13-79.5 | -79.6111 | 13.373 | 1277.0522 | 124.6492 | 158.7003 | 198.0484 | 229.2275 | 265.3249 | 1.092%
2527 | 13-80 | -79.8824 | 13.373 | 1295.0824 | 124.8293 | 158.8851 | 198.4154 | 229.8317 | 266.2318 | 1.098%
2528 | 13-80 | -80.1537 | 13.373 | 1313.1151 | 124.9193 | 159.0111 | 198.7383 | 230.3843 | 267.0786 | 1.103%
2529 | 13-80.5 | -80.4251 | 13.373 | 1331.1503 | 124.904 | 159.0619 | 199.0056 | 230.8775 | 267.8626 | 1.104%
2530 | 13-80.5 | -80.6964 | 13.373 | 1349.1878 | 124.8092 | 159.0563 | 199.2453 | 231.3566 | 268.6514 | 1.104%
2531 | 13-81 | -80.9677 | 13.373 | 1367.2276 | 124.5718 | 158.9311 | 199.3991 | 231.7479 | 269.3528 | 1.1%
2532 | 13-81 | -81.239 | 13.373 | 1385.2694 | 124.1984 | 158.6877 | 199.4617 | 232.0409 | 269.9491 | 1.093%
2533 | 13-81.5 | -81.5104 | 13.373 | 1403.3132 | 123.7197 | 158.3518 | 199.4497 | 232.2513 | 270.4547 | 1.082%
2534 | 13-82 | -81.7817 | 13.373 | 1421.3589 | 122.7593 | 157.4568 | 198.8671 | 231.7381 | 270.0429 | 1.058%
2535 | 13-82 | -82.053 | 13.373 | 1439.4064 | 121.2931 | 155.9033 | 197.6025 | 230.3979 | 268.5814 | 1.018%
2536 | 13-82.5 | -82.3243 | 13.373 | 1457.4556 | 119.4028 | 153.7197 | 195.6829 | 228.3067 | 266.168 | 0.9672%
2537 | 13-82.5 | -82.5956 | 13.373 | 1475.5064 | 117.3143 | 151.252 | 193.4399 | 225.8337 | 263.2519 | 0.913%
2538 | 13-83 | -82.867 | 13.373 | 1493.5587 | 115.1276 | 148.6257 | 190.9984 | 223.129 | 260.0264 | 0.8589%
2539 | 13-83 | -83.1383 | 13.373 | 1511.6125 | 112.8762 | 145.8789 | 188.396 | 220.243 | 256.5611 | 0.8059%
2540 | 13-83.5 | -83.4096 | 13.373 | 1529.6676 | 110.4717 | 142.8866 | 185.5441 | 217.048 | 252.704 | 0.7522%
2541 | 13-83.5 | -83.6809 | 13.373 | 1547.7241 | 107.9659 | 139.7027 | 182.4445 | 213.6319 | 248.5782 | 0.6991%
2542 | 13-84 | -83.9522 | 13.373 | 1565.7817 | 105.4033 | 136.3818 | 179.1268 | 210.0544 | 244.2683 | 0.6479%
2543 | 13-84 | -84.2236 | 13.373 | 1583.8405 | 102.8519 | 133.03 | 175.7325 | 206.3905 | 239.852 | 0.5998%
2544 | 13-84.5 | -84.4949 | 13.373 | 1601.9004 | 100.3678 | 129.7191 | 172.3484 | 202.7167 | 235.4281 | 0.5557%
2545 | 13-85 | -84.7662 | 13.373 | 1619.9613 | 97.9662 | 126.4766 | 169.0252 | 199.0688 | 231.045 | 0.5154%
2546 | 13-85 | -85.0375 | 13.373 | 1638.0232 | 95.5719 | 123.1962 | 165.6531 | 195.344 | 226.5244 | 0.4774%
2547 | 13-85.5 | -85.3089 | 13.373 | 1656.086 | 93.5586 | 120.3604 | 162.7389 | 192.1978 | 222.7104 | 0.4471%
2548 | 13-85.5 | -85.5802 | 13.373 | 1674.1496 | 92.0025 | 118.1247 | 160.4204 | 189.7951 | 219.813 | 0.4248%
2549 | 13-86 | -85.8515 | 13.373 | 1692.2141 | 90.9616 | 116.6505 | 158.8859 | 188.2243 | 217.9162 | 0.4106%
2550 | 13-86 | -86.1228 | 13.373 | 1710.2792 | 90.2306 | 115.6409 | 157.8096 | 187.1589 | 216.6195 | 0.4011%
2551 | 13-86.5 | -86.3941 | 13.373 | 1728.3451 | 89.7719 | 115.0185 | 157.1678 | 186.5366 | 215.8453 | 0.3955%
2552 | 13-86.5 | -86.6655 | 13.373 | 1746.4116 | 89.4253 | 114.5577 | 156.7729 | 186.0507 | 215.1924 | 0.3914%
2553 | 13-87 | -86.9368 | 13.373 | 1764.4787 | 89.3295 | 114.4401 | 156.7698 | 185.8957 | 214.8945 | 0.3902%
2554 | 13-87 | -87.2081 | 13.373 | 1782.5464 | 89.5542 | 114.7527 | 157.2691 | 186.1337 | 215.0182 | 0.3928%
2555 | 13-87.5 | -87.4794 | 13.373 | 1800.6145 | 90.0832 | 115.4554 | 158.2078 | 186.67 | 215.411 | 0.3987%
2556 | 13-88 | -87.7507 | 13.373 | 1818.6832 | 90.8426 | 116.4268 | 159.3881 | 187.3926 | 215.963 | 0.4068%
2557 | 13-88 | -88.0221 | 13.373 | 1836.7522 | 91.8694 | 117.7235 | 160.82 | 188.3703 | 216.7649 | 0.4178%
2558 | 13-88.5 | -88.2934 | 13.373 | 1854.8216 | 93.239 | 119.4673 | 162.5542 | 189.7136 | 217.9463 | 0.4331%
2559 | 13-88.5 | -88.5647 | 13.373 | 1872.8914 | 95.032 | 121.8137 | 164.7131 | 191.5177 | 219.6511 | 0.4544%
2560 | 13-89 | -88.836 | 13.373 | 1890.9615 | 97.2913 | 124.8409 | 167.308 | 193.7891 | 221.881 | 0.4834%
2561 | 13-89 | -89.1074 | 13.373 | 1909.0319 | 100.1049 | 128.5847 | 170.3895 | 196.5548 | 224.6597 | 0.5223%
2562 | 13-89.5 | -89.3787 | 13.373 | 1927.1025 | 103.5594 | 132.7787 | 173.8613 | 199.7975 | 227.9863 | 0.573%
2563 | 13-89.5 | -89.65 | 13.373 | 1945.1732 | 107.3031 | 137.0465 | 177.3838 | 203.0737 | 231.3329 | 0.6328%
2564 | 13-90 | -89.9213 | 13.373 | 1963.2442 | 111.4628 | 141.455 | 180.9895 | 206.4716 | 234.8106 | 0.7059%
2565 | 13-90 | -90.1926 | 13.373 | 1981.3153 | 116.117 | 146.2623 | 184.9246 | 210.3699 | 238.9048 | 0.8007%
2566 | 13-90.5 | -90.464 | 13.373 | 1999.3865 | 121.1388 | 151.3216 | 189.0467 | 214.5907 | 243.3933 | 0.9209%
2567 | 13-90.5 | -90.7353 | 13.373 | 2017.4578 | 126.2858 | 156.3562 | 193.0958 | 218.8097 | 247.8813 | 1.066%
2568 | 14-50 | -50.0371 | 13.6443 | 719.6264 | 127.6672 | 161.8552 | 198.284 | 227.7427 | 261.5806 | 1.173%
2569 | 14-50.5 | -50.3084 | 13.6443 | 701.7591 | 127.6018 | 161.9776 | 198.4999 | 228.0884 | 262.0899 | 1.174%
2570 | 14-50.5 | -50.5797 | 13.6443 | 683.906 | 127.5035 | 162.0738 | 198.6883 | 228.3963 | 262.5487 | 1.174%
2571 | 14-51 | -50.851 | 13.6443 | 666.0682 | 127.3945 | 162.1593 | 198.8654 | 228.6866 | 262.9821 | 1.173%
2572 | 14-51 | -51.1224 | 13.6443 | 648.247 | 127.3018 | 162.2562 | 199.0542 | 228.9891 | 263.4281 | 1.173%
2573 | 14-51.5 | -51.3937 | 13.6443 | 630.4438 | 127.2027 | 162.3364 | 199.2225 | 229.2595 | 263.8272 | 1.173%
2574 | 14-51.5 | -51.665 | 13.6443 | 612.6604 | 127.1164 | 162.4139 | 199.3938 | 229.5356 | 264.2358 | 1.173%
2575 | 14-52 | -51.9363 | 13.6443 | 594.8983 | 127.0608 | 162.5016 | 199.5876 | 229.8486 | 264.6996 | 1.173%
2576 | 14-52 | -52.2077 | 13.6443 | 577.1598 | 127.0011 | 162.5652 | 199.7497 | 230.1187 | 265.1066 | 1.174%
2577 | 14-52.5 | -52.479 | 13.6443 | 559.4469 | 126.9665 | 162.632 | 199.9109 | 230.3896 | 265.5169 | 1.174%
2578 | 14-53 | -52.7503 | 13.6443 | 541.7623 | 126.9769 | 162.7171 | 200.0911 | 230.6905 | 265.9714 | 1.176%
2579 | 14-53 | -53.0216 | 13.6443 | 524.1089 | 126.9871 | 162.7702 | 200.2266 | 230.931 | 266.3459 | 1.178%
2580 | 14-53.5 | -53.2929 | 13.6443 | 506.4898 | 127.0255 | 162.816 | 200.3535 | 231.1674 | 266.7225 | 1.179%
2581 | 14-53.5 | -53.5643 | 13.6443 | 488.909 | 127.1068 | 162.8663 | 200.4881 | 231.4248 | 267.1374 | 1.182%
2582 | 14-54 | -53.8356 | 13.6443 | 471.3706 | 127.1968 | 162.8966 | 200.5936 | 231.6431 | 267.5012 | 1.185%
2583 | 14-54 | -54.1069 | 13.6443 | 453.8797 | 127.3336 | 162.9489 | 200.7195 | 231.8921 | 267.9086 | 1.188%
2584 | 14-54.5 | -54.3782 | 13.6443 | 436.4419 | 127.5303 | 163.0358 | 200.8803 | 232.1911 | 268.3852 | 1.194%
2585 | 14-54.5 | -54.6495 | 13.6443 | 419.0639 | 127.7469 | 163.1226 | 201.0238 | 232.4583 | 268.8113 | 1.2%
2586 | 14-55 | -54.9209 | 13.6443 | 401.7536 | 128.0133 | 163.2401 | 201.1822 | 232.7355 | 269.2407 | 1.207%
2587 | 14-55 | -55.1922 | 13.6443 | 384.52 | 128.3387 | 163.398 | 201.3616 | 233.0269 | 269.6749 | 1.215%
2588 | 14-55.5 | -55.4635 | 13.6443 | 367.374 | 128.6836 | 163.5676 | 201.5031 | 233.2362 | 269.97 | 1.225%
2589 | 14-55.5 | -55.7348 | 13.6443 | 350.3285 | 129.1009 | 163.8017 | 201.6794 | 233.4619 | 270.2566 | 1.236%
2590 | 14-56 | -56.0061 | 13.6443 | 333.3989 | 129.6122 | 164.1228 | 201.9198 | 233.7361 | 270.5697 | 1.251%
2591 | 14-56.5 | -56.2775 | 13.6443 | 316.6038 | 130.1715 | 164.4942 | 202.1972 | 234.0317 | 270.883 | 1.267%
2592 | 14-56.5 | -56.5488 | 13.6443 | 299.9659 | 130.8417 | 164.9755 | 202.5883 | 234.4519 | 271.3325 | 1.288%
2593 | 14-57 | -56.8201 | 13.6443 | 283.5129 | 131.6287 | 165.5716 | 203.0959 | 234.9946 | 271.9093 | 1.314%
2594 | 14-57 | -57.0914 | 13.6443 | 267.2789 | 132.4517 | 166.2088 | 203.6332 | 235.5456 | 272.4657 | 1.342%
2595 | 14-57.5 | -57.3628 | 13.6443 | 251.3064 | 133.3502 | 166.9117 | 204.2377 | 236.1628 | 273.0851 | 1.373%
2596 | 14-57.5 | -57.6341 | 13.6443 | 235.6486 | 134.3084 | 167.666 | 204.8926 | 236.8243 | 273.7394 | 1.407%
2597 | 14-58 | -57.9054 | 13.6443 | 220.3727 | 135.2557 | 168.4129 | 205.53 | 237.4469 | 274.3271 | 1.443%
2598 | 14-58 | -58.1767 | 13.6443 | 205.5637 | 136.2352 | 169.1888 | 206.2033 | 238.1113 | 274.9633 | 1.48%
2599 | 14-58.5 | -58.448 | 13.6443 | 191.3302 | 137.2185 | 169.9713 | 206.892 | 238.7935 | 275.6202 | 1.519%
2600 | 14-58.5 | -58.7194 | 13.6443 | 177.8105 | 138.1398 | 170.7067 | 207.5461 | 239.4402 | 276.2411 | 1.557%
2601 | 14-59 | -58.9907 | 13.6443 | 165.1799 | 139.0401 | 171.4269 | 208.228 | 240.149 | 276.9688 | 1.596%
2602 | 14-59.5 | -59.262 | 13.6443 | 153.6579 | 139.8821 | 172.0921 | 208.889 | 240.856 | 277.7198 | 1.632%
2603 | 14-59.5 | -59.5333 | 13.6443 | 143.5118 | 140.6021 | 172.6433 | 209.4468 | 241.4524 | 278.353 | 1.664%
2604 | 14-60 | -59.8046 | 13.6443 | 135.0519 | 141.2469 | 173.1217 | 209.9344 | 241.9698 | 278.8974 | 1.693%
2605 | 14-60 | -60.076 | 13.6443 | 128.6116 | 141.7913 | 173.5123 | 210.3361 | 242.3926 | 279.338 | 1.718%
2606 | 14-60.5 | -60.3473 | 13.6443 | 124.5046 | 142.213 | 173.8037 | 210.648 | 242.7238 | 279.6863 | 1.737%
2607 | 14-60.5 | -60.6186 | 13.6443 | 122.965 | 142.5928 | 174.0723 | 210.9616 | 243.0805 | 280.0919 | 1.755%
2608 | 14-61 | -60.8899 | 13.6443 | 124.0883 | 142.9024 | 174.2952 | 211.247 | 243.4252 | 280.507 | 1.769%
2609 | 14-61 | -61.1613 | 13.6443 | 127.8044 | 143.1231 | 174.456 | 211.4828 | 243.7298 | 280.8957 | 1.779%
2610 | 14-61.5 | -61.4326 | 13.6443 | 133.8975 | 143.3253 | 174.6163 | 211.7426 | 244.0839 | 281.3672 | 1.789%
2611 | 14-61.5 | -61.7039 | 13.6443 | 142.0621 | 143.4761 | 174.7493 | 211.9877 | 244.4359 | 281.8531 | 1.796%
2612 | 14-62 | -61.9752 | 13.6443 | 151.9648 | 143.5672 | 174.848 | 212.1997 | 244.7551 | 282.3077 | 1.8%
2613 | 14-62 | -62.2465 | 13.6443 | 163.2895 | 143.6614 | 174.966 | 212.4366 | 245.1086 | 282.8083 | 1.805%
2614 | 14-62.5 | -62.5179 | 13.6443 | 175.7615 | 143.733 | 175.0785 | 212.6613 | 245.4428 | 283.2807 | 1.809%
2615 | 14-63 | -62.7892 | 13.6443 | 189.1542 | 143.7813 | 175.1843 | 212.8727 | 245.7557 | 283.7216 | 1.812%
2616 | 14-63 | -63.0605 | 13.6443 | 203.2855 | 143.8493 | 175.3256 | 213.1363 | 246.1412 | 284.2603 | 1.816%
2617 | 14-63.5 | -63.3318 | 13.6443 | 218.0119 | 143.9111 | 175.4807 | 213.4285 | 246.5711 | 284.8637 | 1.82%
2618 | 14-63.5 | -63.6031 | 13.6443 | 233.2206 | 143.9586 | 175.641 | 213.7356 | 247.0271 | 285.5072 | 1.824%
2619 | 14-64 | -63.8745 | 13.6443 | 248.8232 | 144.0077 | 175.816 | 214.0642 | 247.5147 | 286.1954 | 1.828%
2620 | 14-64 | -64.1458 | 13.6443 | 264.7501 | 144.0237 | 175.9667 | 214.3524 | 247.9469 | 286.8095 | 1.83%
2621 | 14-64.5 | -64.4171 | 13.6443 | 280.9461 | 144.0103 | 176.0943 | 214.5974 | 248.3169 | 287.3377 | 1.831%
2622 | 14-64.5 | -64.6884 | 13.6443 | 297.3671 | 144 | 176.2294 | 214.8409 | 248.6797 | 287.8511 | 1.832%
2623 | 14-65 | -64.9598 | 13.6443 | 313.978 | 143.958 | 176.3344 | 215.0321 | 248.9649 | 288.2552 | 1.832%
2624 | 14-65 | -65.2311 | 13.6443 | 330.7499 | 143.896 | 176.417 | 215.187 | 249.1954 | 288.5813 | 1.831%
2625 | 14-65.5 | -65.5024 | 13.6443 | 347.6597 | 143.8394 | 176.5006 | 215.3435 | 249.4252 | 288.9035 | 1.83%
2626 | 14-66 | -65.7737 | 13.6443 | 364.6881 | 143.7496 | 176.5444 | 215.4531 | 249.5913 | 289.1412 | 1.828%
2627 | 14-66 | -66.045 | 13.6443 | 381.8192 | 143.632 | 176.5548 | 215.5352 | 249.7276 | 289.3467 | 1.823%
2628 | 14-66.5 | -66.3164 | 13.6443 | 399.0398 | 143.5016 | 176.5487 | 215.6198 | 249.8805 | 289.5873 | 1.819%
2629 | 14-66.5 | -66.5877 | 13.6443 | 416.3388 | 143.3134 | 176.4834 | 215.6415 | 249.9561 | 289.7335 | 1.811%
2630 | 14-67 | -66.859 | 13.6443 | 433.7066 | 143.073 | 176.3637 | 215.6029 | 249.9555 | 289.7837 | 1.8%
2631 | 14-67 | -67.1303 | 13.6443 | 451.1355 | 142.7927 | 176.2006 | 215.5191 | 249.8987 | 289.7646 | 1.788%
2632 | 14-67.5 | -67.4016 | 13.6443 | 468.6185 | 142.4391 | 175.9601 | 215.3255 | 249.6886 | 289.5378 | 1.772%
2633 | 14-67.5 | -67.673 | 13.6443 | 486.1497 | 142.0377 | 175.6686 | 215.0678 | 249.3906 | 289.193 | 1.755%
2634 | 14-68 | -67.9443 | 13.6443 | 503.7242 | 141.6068 | 175.3461 | 214.7775 | 249.0495 | 288.7924 | 1.736%
2635 | 14-68 | -68.2156 | 13.6443 | 521.3375 | 141.1291 | 174.9815 | 214.4306 | 248.6278 | 288.2805 | 1.715%
2636 | 14-68.5 | -68.4869 | 13.6443 | 538.9858 | 140.6359 | 174.6095 | 214.0747 | 248.1919 | 287.7484 | 1.694%
2637 | 14-69 | -68.7583 | 13.6443 | 556.6657 | 140.1442 | 174.2477 | 213.7336 | 247.7764 | 287.2434 | 1.673%
2638 | 14-69 | -69.0296 | 13.6443 | 574.3743 | 139.5635 | 173.7586 | 213.2583 | 247.1714 | 286.4798 | 1.648%
2639 | 14-69.5 | -69.3009 | 13.6443 | 592.109 | 138.9265 | 173.1755 | 212.686 | 246.4244 | 285.5179 | 1.621%
2640 | 14-69.5 | -69.5722 | 13.6443 | 609.8674 | 138.2512 | 172.517 | 212.0353 | 245.5589 | 284.3868 | 1.592%
2641 | 14-70 | -69.8435 | 13.6443 | 627.6477 | 137.5683 | 171.8436 | 211.3192 | 244.5769 | 283.0741 | 1.563%
2642 | 14-70 | -70.1149 | 13.6443 | 645.4478 | 136.9216 | 171.1957 | 210.6009 | 243.5715 | 281.7101 | 1.536%
2643 | 14-70.5 | -70.3862 | 13.6443 | 663.2663 | 136.3258 | 170.587 | 209.9001 | 242.573 | 280.3391 | 1.511%
2644 | 14-70.5 | -70.6575 | 13.6443 | 681.1015 | 135.804 | 170.0844 | 209.2644 | 241.6463 | 279.0464 | 1.489%
2645 | 14-71 | -70.9288 | 13.6443 | 698.9523 | 135.3894 | 169.7216 | 208.7578 | 240.8902 | 277.976 | 1.473%
2646 | 14-71 | -71.2001 | 13.6443 | 716.8175 | 135.074 | 169.4906 | 208.375 | 240.3027 | 277.1296 | 1.461%
2647 | 14-71.5 | -71.4715 | 13.6443 | 734.6959 | 134.7473 | 169.2534 | 207.9768 | 239.6972 | 276.2622 | 1.449%
2648 | 14-71.5 | -71.7428 | 13.6443 | 752.5866 | 134.4258 | 169.0196 | 207.5842 | 239.1074 | 275.4243 | 1.437%
2649 | 14-72 | -72.0141 | 13.6443 | 770.4887 | 134.1033 | 168.7791 | 207.1864 | 238.5189 | 274.5963 | 1.425%
2650 | 14-72.5 | -72.2854 | 13.6443 | 788.4015 | 133.7432 | 168.4887 | 206.7301 | 237.8546 | 273.6709 | 1.411%
2651 | 14-72.5 | -72.5568 | 13.6443 | 806.3241 | 133.4381 | 168.2865 | 206.3641 | 237.3245 | 272.9355 | 1.4%
2652 | 14-73 | -72.8281 | 13.6443 | 824.2559 | 133.1815 | 168.1656 | 206.0813 | 236.9215 | 272.3823 | 1.392%
2653 | 14-73 | -73.0994 | 13.6443 | 842.1964 | 132.937 | 168.0867 | 205.8358 | 236.5844 | 271.9313 | 1.384%
2654 | 14-73.5 | -73.3707 | 13.6443 | 860.1448 | 132.6783 | 167.9926 | 205.6159 | 236.3131 | 271.5983 | 1.376%
2655 | 14-73.5 | -73.642 | 13.6443 | 878.1008 | 132.3996 | 167.8781 | 205.4112 | 236.0913 | 271.3594 | 1.367%
2656 | 14-74 | -73.9134 | 13.6443 | 896.0639 | 132.0818 | 167.7232 | 205.1927 | 235.8751 | 271.1518 | 1.357%
2657 | 14-74 | -74.1847 | 13.6443 | 914.0335 | 131.7084 | 167.4645 | 204.9156 | 235.6033 | 270.8941 | 1.344%
2658 | 14-74.5 | -74.456 | 13.6443 | 932.0093 | 131.2656 | 167.0864 | 204.5523 | 235.2309 | 270.519 | 1.328%
2659 | 14-74.5 | -74.7273 | 13.6443 | 949.9909 | 130.7291 | 166.5627 | 204.0527 | 234.6762 | 269.9049 | 1.308%
2660 | 14-75 | -74.9986 | 13.6443 | 967.978 | 130.2171 | 166.0367 | 203.5598 | 234.1317 | 269.305 | 1.29%
2661 | 14-75.5 | -75.27 | 13.6443 | 985.9703 | 129.7269 | 165.5072 | 203.0667 | 233.586 | 268.7025 | 1.272%
2662 | 14-75.5 | -75.5413 | 13.6443 | 1003.9674 | 129.2525 | 164.9733 | 202.5658 | 233.0262 | 268.0778 | 1.254%
2663 | 14-76 | -75.8126 | 13.6443 | 1021.969 | 128.8395 | 164.4843 | 202.1135 | 232.5322 | 267.5402 | 1.239%
2664 | 14-76 | -76.0839 | 13.6443 | 1039.9749 | 128.4766 | 164.029 | 201.6976 | 232.0874 | 267.0676 | 1.225%
2665 | 14-76.5 | -76.3553 | 13.6443 | 1057.9849 | 128.1499 | 163.5953 | 201.3072 | 231.6767 | 266.6397 | 1.213%
2666 | 14-76.5 | -76.6266 | 13.6443 | 1075.9987 | 127.9027 | 163.2272 | 200.989 | 231.3609 | 266.3344 | 1.203%
2667 | 14-77 | -76.8979 | 13.6443 | 1094.0162 | 127.7172 | 162.9117 | 200.7204 | 231.1018 | 266.0938 | 1.195%
2668 | 14-77 | -77.1692 | 13.6443 | 1112.037 | 127.5798 | 162.6423 | 200.4869 | 230.8725 | 265.8751 | 1.189%
2669 | 14-77.5 | -77.4405 | 13.6443 | 1130.061 | 127.5233 | 162.4483 | 200.3219 | 230.7185 | 265.739 | 1.186%
2670 | 14-77.5 | -77.7119 | 13.6443 | 1148.0881 | 127.5259 | 162.3162 | 200.2119 | 230.6237 | 265.666 | 1.184%
2671 | 14-78 | -77.9832 | 13.6443 | 1166.1181 | 127.5837 | 162.2487 | 200.1735 | 230.6196 | 265.7071 | 1.184%
2672 | 14-78.5 | -78.2545 | 13.6443 | 1184.1507 | 127.7469 | 162.2973 | 200.2802 | 230.8165 | 266.019 | 1.189%
2673 | 14-78.5 | -78.5258 | 13.6443 | 1202.186 | 127.9582 | 162.4098 | 200.4761 | 231.1392 | 266.5025 | 1.195%
2674 | 14-79 | -78.7971 | 13.6443 | 1220.2236 | 128.1833 | 162.5528 | 200.7294 | 231.5477 | 267.1077 | 1.202%
2675 | 14-79 | -79.0685 | 13.6443 | 1238.2636 | 128.4446 | 162.7445 | 201.0637 | 232.0768 | 267.8835 | 1.21%
2676 | 14-79.5 | -79.3398 | 13.6443 | 1256.3057 | 128.6864 | 162.939 | 201.4266 | 232.6543 | 268.733 | 1.219%
2677 | 14-79.5 | -79.6111 | 13.6443 | 1274.3499 | 128.8942 | 163.1252 | 201.8018 | 233.2566 | 269.6237 | 1.226%
2678 | 14-80 | -79.8824 | 13.6443 | 1292.3961 | 129.0982 | 163.3306 | 202.2166 | 233.9197 | 270.6025 | 1.234%
2679 | 14-80 | -80.1537 | 13.6443 | 1310.444 | 129.2154 | 163.4808 | 202.5898 | 234.5377 | 271.5329 | 1.24%
2680 | 14-80.5 | -80.4251 | 13.6443 | 1328.4937 | 129.2288 | 163.5574 | 202.9069 | 235.0983 | 272.4059 | 1.242%
2681 | 14-80.5 | -80.6964 | 13.6443 | 1346.545 | 129.1636 | 163.5779 | 203.195 | 235.6451 | 273.2859 | 1.242%
2682 | 14-81 | -80.9677 | 13.6443 | 1364.5979 | 128.9534 | 163.4793 | 203.3919 | 236.0981 | 274.0718 | 1.238%
2683 | 14-81 | -81.239 | 13.6443 | 1382.6523 | 128.6024 | 163.2623 | 203.4917 | 236.446 | 274.7449 | 1.229%
2684 | 14-81.5 | -81.5104 | 13.6443 | 1400.708 | 128.139 | 162.9508 | 203.511 | 236.7052 | 275.3211 | 1.217%
2685 | 14-82 | -81.7817 | 13.6443 | 1418.765 | 127.1661 | 162.0794 | 202.9519 | 236.2275 | 274.9653 | 1.189%
2686 | 14-82 | -82.053 | 13.6443 | 1436.8232 | 125.653 | 160.5453 | 201.7226 | 234.9134 | 273.552 | 1.143%
2687 | 14-82.5 | -82.3243 | 13.6443 | 1454.8826 | 123.6813 | 158.3722 | 199.8452 | 232.8428 | 271.1857 | 1.084%
2688 | 14-82.5 | -82.5956 | 13.6443 | 1472.943 | 121.4978 | 155.905 | 197.6522 | 230.398 | 268.3321 | 1.021%
2689 | 14-83 | -82.867 | 13.6443 | 1491.0045 | 119.2058 | 153.2722 | 195.2665 | 227.7274 | 265.1802 | 0.9592%
2690 | 14-83 | -83.1383 | 13.6443 | 1509.0669 | 116.839 | 150.5117 | 192.7233 | 224.8779 | 261.7938 | 0.8984%
2691 | 14-83.5 | -83.4096 | 13.6443 | 1527.1302 | 114.3047 | 147.4901 | 189.916 | 221.6987 | 257.9851 | 0.8369%
2692 | 14-83.5 | -83.6809 | 13.6443 | 1545.1943 | 111.6589 | 144.2635 | 186.8486 | 218.2797 | 253.8788 | 0.7763%
2693 | 14-84 | -83.9522 | 13.6443 | 1563.2593 | 108.9482 | 140.8881 | 183.5524 | 214.6843 | 249.5635 | 0.7179%
2694 | 14-84 | -84.2236 | 13.6443 | 1581.3249 | 106.2362 | 137.4642 | 180.1725 | 210.9881 | 245.1194 | 0.6631%
2695 | 14-84.5 | -84.4949 | 13.6443 | 1599.3912 | 103.5829 | 134.065 | 176.7986 | 207.2763 | 240.653 | 0.6129%
2696 | 14-85 | -84.7662 | 13.6443 | 1617.4581 | 101.0065 | 130.7201 | 173.4822 | 203.5865 | 236.2153 | 0.5672%
2697 | 14-85 | -85.0375 | 13.6443 | 1635.5256 | 98.4033 | 127.2774 | 170.065 | 199.7481 | 231.5472 | 0.5237%
2698 | 14-85.5 | -85.3089 | 13.6443 | 1653.5936 | 96.1697 | 124.2222 | 167.0555 | 196.4245 | 227.5036 | 0.4884%
2699 | 14-85.5 | -85.5802 | 13.6443 | 1671.6621 | 94.3979 | 121.7269 | 164.5743 | 193.7933 | 224.3103 | 0.4616%
2700 | 14-86 | -85.8515 | 13.6443 | 1689.7311 | 93.2961 | 120.1906 | 163.0411 | 192.2077 | 222.3899 | 0.4459%
2701 | 14-86 | -86.1228 | 13.6443 | 1707.8004 | 92.6544 | 119.2954 | 162.1284 | 191.346 | 221.3552 | 0.4372%
2702 | 14-86.5 | -86.3941 | 13.6443 | 1725.8701 | 92.4233 | 118.8904 | 161.7904 | 191.1212 | 221.1031 | 0.4342%
2703 | 14-86.5 | -86.6655 | 13.6443 | 1743.9401 | 92.1587 | 118.5298 | 161.5121 | 190.7932 | 220.6624 | 0.4309%
2704 | 14-87 | -86.9368 | 13.6443 | 1762.0104 | 92.0198 | 118.3641 | 161.4592 | 190.5957 | 220.3291 | 0.4292%
2705 | 14-87 | -87.2081 | 13.6443 | 1780.081 | 92.1002 | 118.4758 | 161.7684 | 190.6368 | 220.2346 | 0.4302%
2706 | 14-87.5 | -87.4794 | 13.6443 | 1798.1517 | 92.4634 | 118.953 | 162.4874 | 190.9669 | 220.4148 | 0.4346%
2707 | 14-88 | -87.7507 | 13.6443 | 1816.2227 | 93.043 | 119.6874 | 163.4262 | 191.483 | 220.766 | 0.4412%
2708 | 14-88 | -88.0221 | 13.6443 | 1834.2937 | 93.8734 | 120.7317 | 164.5868 | 192.2439 | 221.3703 | 0.4508%
2709 | 14-88.5 | -88.2934 | 13.6443 | 1852.3649 | 95.0222 | 122.1937 | 166.0227 | 193.3414 | 222.3299 | 0.4645%
2710 | 14-88.5 | -88.5647 | 13.6443 | 1870.4362 | 96.6047 | 124.2813 | 167.9085 | 194.9386 | 223.8657 | 0.4847%
2711 | 14-89 | -88.836 | 13.6443 | 1888.5075 | 98.6578 | 127.0616 | 170.2497 | 197.0323 | 225.9639 | 0.5129%
2712 | 14-89 | -89.1074 | 13.6443 | 1906.5788 | 101.2449 | 130.5307 | 173.081 | 199.6161 | 228.6056 | 0.5508%
2713 | 14-89.5 | -89.3787 | 13.6443 | 1924.6502 | 104.2906 | 134.1919 | 176.078 | 202.4064 | 231.4518 | 0.5969%
2714 | 14-89.5 | -89.65 | 13.6443 | 1942.7214 | 107.4652 | 137.7542 | 178.9424 | 204.993 | 234.0082 | 0.6475%
2715 | 14-90 | -89.9213 | 13.6443 | 1960.7927 | 110.9116 | 141.3742 | 181.7433 | 207.5047 | 236.4332 | 0.7063%
2716 | 14-90 | -90.1926 | 13.6443 | 1978.8638 | 114.9808 | 145.5295 | 185.0521 | 210.7511 | 239.7795 | 0.786%
2717 | 14-90.5 | -90.464 | 13.6443 | 1996.9348 | 119.5386 | 150.1203 | 188.7324 | 214.5484 | 243.81 | 0.8898%
2718 | 14-90.5 | -90.7353 | 13.6443 | 2015.0057 | 124.3522 | 154.8889 | 192.5211 | 218.5544 | 248.0999 | 1.018%
2719 | 14-50 | -50.0371 | 13.9156 | 716.2371 | 130.4864 | 164.6399 | 200.4494 | 230.0727 | 264.0765 | 1.269%
2720 | 14-50.5 | -50.3084 | 13.9156 | 698.3052 | 130.4357 | 164.7676 | 200.6718 | 230.427 | 264.5968 | 1.27%
2721 | 14-50.5 | -50.5797 | 13.9156 | 680.3834 | 130.3512 | 164.8722 | 200.8687 | 230.7468 | 265.0714 | 1.27%
2722 | 14-51 | -50.851 | 13.9156 | 662.4728 | 130.2576 | 164.9713 | 201.0603 | 231.0576 | 265.5326 | 1.269%
2723 | 14-51 | -51.1224 | 13.9156 | 644.5742 | 130.184 | 165.0885 | 201.2729 | 231.3938 | 266.0243 | 1.27%
2724 | 14-51.5 | -51.3937 | 13.9156 | 626.6888 | 130.1047 | 165.1936 | 201.4706 | 231.7059 | 266.4808 | 1.27%
2725 | 14-51.5 | -51.665 | 13.9156 | 608.8176 | 130.0386 | 165.2987 | 201.6759 | 232.0314 | 266.9579 | 1.27%
2726 | 14-52 | -51.9363 | 13.9156 | 590.9621 | 130.0038 | 165.4153 | 201.9083 | 232.4011 | 267.5008 | 1.272%
2727 | 14-52 | -52.2077 | 13.9156 | 573.1236 | 129.9629 | 165.5066 | 202.1071 | 232.7254 | 267.984 | 1.273%
2728 | 14-52.5 | -52.479 | 13.9156 | 555.304 | 129.9441 | 165.5971 | 202.3017 | 233.0458 | 268.464 | 1.274%
2729 | 14-53 | -52.7503 | 13.9156 | 537.505 | 129.9665 | 165.7008 | 202.5112 | 233.3905 | 268.9803 | 1.276%
2730 | 14-53 | -53.0216 | 13.9156 | 519.7288 | 129.9816 | 165.7657 | 202.6689 | 233.6654 | 269.4043 | 1.278%
2731 | 14-53.5 | -53.2929 | 13.9156 | 501.9779 | 130.0199 | 165.8178 | 202.8131 | 233.928 | 269.8185 | 1.28%
2732 | 14-53.5 | -53.5643 | 13.9156 | 484.2552 | 130.0971 | 165.8691 | 202.9614 | 234.205 | 270.2602 | 1.283%
2733 | 14-54 | -53.8356 | 13.9156 | 466.5637 | 130.1784 | 165.896 | 203.0753 | 234.4344 | 270.6382 | 1.285%
2734 | 14-54 | -54.1069 | 13.9156 | 448.9073 | 130.3015 | 165.9389 | 203.2036 | 234.6843 | 271.0444 | 1.289%
2735 | 14-54.5 | -54.3782 | 13.9156 | 431.2902 | 130.4786 | 166.0097 | 203.3604 | 234.9742 | 271.5049 | 1.294%
2736 | 14-54.5 | -54.6495 | 13.9156 | 413.7176 | 130.6713 | 166.0765 | 203.4948 | 235.2239 | 271.9027 | 1.299%
2737 | 14-55 | -54.9209 | 13.9156 | 396.1954 | 130.9114 | 166.1716 | 203.6436 | 235.482 | 272.3008 | 1.306%
2738 | 14-55 | -55.1922 | 13.9156 | 378.7306 | 131.2076 | 166.3048 | 203.813 | 235.7529 | 272.7008 | 1.315%
2739 | 14-55.5 | -55.4635 | 13.9156 | 361.3315 | 131.5174 | 166.4438 | 203.9351 | 235.9277 | 272.9417 | 1.324%
2740 | 14-55.5 | -55.7348 | 13.9156 | 344.0081 | 131.8963 | 166.6443 | 204.089 | 236.114 | 273.167 | 1.335%
2741 | 14-56 | -56.0061 | 13.9156 | 326.7726 | 132.3674 | 166.9292 | 204.3047 | 236.3454 | 273.4141 | 1.35%
2742 | 14-56.5 | -56.2775 | 13.9156 | 309.6396 | 132.8864 | 167.2645 | 204.5572 | 236.5987 | 273.6628 | 1.367%
2743 | 14-56.5 | -56.5488 | 13.9156 | 292.6272 | 133.5198 | 167.7104 | 204.9258 | 236.9801 | 274.0526 | 1.388%
2744 | 14-57 | -56.8201 | 13.9156 | 275.7576 | 134.2752 | 168.2728 | 205.4136 | 237.4883 | 274.5763 | 1.415%
2745 | 14-57 | -57.0914 | 13.9156 | 259.0588 | 135.0762 | 168.8828 | 205.938 | 238.0157 | 275.0953 | 1.445%
2746 | 14-57.5 | -57.3628 | 13.9156 | 242.5662 | 135.9631 | 169.5637 | 206.5373 | 238.6207 | 275.6935 | 1.478%
2747 | 14-57.5 | -57.6341 | 13.9156 | 226.3248 | 136.9204 | 170.3013 | 207.1944 | 239.281 | 276.3424 | 1.516%
2748 | 14-58 | -57.9054 | 13.9156 | 210.3929 | 137.8783 | 171.0388 | 207.8416 | 239.9137 | 276.9403 | 1.555%
2749 | 14-58 | -58.1767 | 13.9156 | 194.8464 | 138.8781 | 171.8092 | 208.5309 | 240.5967 | 277.5986 | 1.596%
2750 | 14-58.5 | -58.448 | 13.9156 | 179.7853 | 139.8915 | 172.5907 | 209.2402 | 241.3038 | 278.2857 | 1.64%
2751 | 14-58.5 | -58.7194 | 13.9156 | 165.3424 | 140.8524 | 173.3313 | 209.9182 | 241.9789 | 278.9406 | 1.683%
2752 | 14-59 | -58.9907 | 13.9156 | 151.6943 | 141.8049 | 174.066 | 210.636 | 242.7317 | 279.7222 | 1.727%
2753 | 14-59.5 | -59.262 | 13.9156 | 139.0753 | 142.7164 | 174.7591 | 211.3494 | 243.5045 | 280.5553 | 1.77%
2754 | 14-59.5 | -59.5333 | 13.9156 | 127.7906 | 143.5275 | 175.3601 | 211.9866 | 244.2013 | 281.3149 | 1.809%
2755 | 14-60 | -59.8046 | 13.9156 | 118.223 | 144.2778 | 175.9073 | 212.5773 | 244.8488 | 282.0225 | 1.846%
2756 | 14-60 | -60.076 | 13.9156 | 110.8181 | 144.9337 | 176.3764 | 213.0922 | 245.4144 | 282.6417 | 1.879%
2757 | 14-60.5 | -60.3473 | 13.9156 | 106.03 | 145.4601 | 176.7398 | 213.5046 | 245.8719 | 283.1482 | 1.905%
2758 | 14-60.5 | -60.6186 | 13.9156 | 104.22 | 145.9331 | 177.0685 | 213.9008 | 246.3317 | 283.6813 | 1.929%
2759 | 14-61 | -60.8899 | 13.9156 | 105.5414 | 146.3278 | 177.345 | 214.257 | 246.7625 | 284.201 | 1.949%
2760 | 14-61 | -61.1613 | 13.9156 | 109.8813 | 146.6304 | 177.5596 | 214.5587 | 247.1444 | 284.6804 | 1.965%
2761 | 14-61.5 | -61.4326 | 13.9156 | 116.9041 | 146.9104 | 177.7717 | 214.8791 | 247.567 | 285.2289 | 1.979%
2762 | 14-61.5 | -61.7039 | 13.9156 | 126.1624 | 147.1339 | 177.9545 | 215.1783 | 247.9767 | 285.7761 | 1.99%
2763 | 14-62 | -61.9752 | 13.9156 | 137.2045 | 147.2923 | 178.0999 | 215.4363 | 248.3416 | 286.2747 | 1.998%
2764 | 14-62 | -62.2465 | 13.9156 | 149.636 | 147.4489 | 178.26 | 215.7127 | 248.7317 | 286.8072 | 2.007%
2765 | 14-62.5 | -62.5179 | 13.9156 | 163.1396 | 147.5773 | 178.4104 | 215.9709 | 249.096 | 287.3041 | 2.014%
2766 | 14-63 | -62.7892 | 13.9156 | 177.4706 | 147.6709 | 178.5461 | 216.2055 | 249.4277 | 287.7575 | 2.019%
2767 | 14-63 | -63.0605 | 13.9156 | 192.4443 | 147.7671 | 178.7005 | 216.4718 | 249.8074 | 288.2792 | 2.025%
2768 | 14-63.5 | -63.3318 | 13.9156 | 207.9219 | 147.8447 | 178.852 | 216.7458 | 250.2078 | 288.8384 | 2.029%
2769 | 14-63.5 | -63.6031 | 13.9156 | 223.7988 | 147.9024 | 179.0013 | 217.0275 | 250.6277 | 289.4324 | 2.033%
2770 | 14-64 | -63.8745 | 13.9156 | 239.9958 | 147.9677 | 179.1733 | 217.3454 | 251.0998 | 290.0991 | 2.037%
2771 | 14-64 | -64.1458 | 13.9156 | 256.4522 | 148.005 | 179.3275 | 217.6323 | 251.5287 | 290.7071 | 2.04%
2772 | 14-64.5 | -64.4171 | 13.9156 | 273.1211 | 148.0136 | 179.4593 | 217.8773 | 251.8969 | 291.231 | 2.042%
2773 | 14-64.5 | -64.6884 | 13.9156 | 289.9658 | 148.0209 | 179.5933 | 218.1155 | 252.2516 | 291.7329 | 2.044%
2774 | 14-65 | -64.9598 | 13.9156 | 306.9574 | 147.9938 | 179.694 | 218.2966 | 252.5241 | 292.1208 | 2.043%
2775 | 14-65 | -65.2311 | 13.9156 | 324.0728 | 147.9451 | 179.7712 | 218.4397 | 252.7413 | 292.4319 | 2.042%
2776 | 14-65.5 | -65.5024 | 13.9156 | 341.2933 | 147.9012 | 179.8493 | 218.5854 | 252.9612 | 292.7455 | 2.041%
2777 | 14-66 | -65.7737 | 13.9156 | 358.6037 | 147.826 | 179.8928 | 218.6909 | 253.1293 | 292.9934 | 2.038%
2778 | 14-66 | -66.045 | 13.9156 | 375.9916 | 147.7259 | 179.9096 | 218.7769 | 253.2802 | 293.2275 | 2.034%
2779 | 14-66.5 | -66.3164 | 13.9156 | 393.4466 | 147.6163 | 179.9167 | 218.8732 | 253.4583 | 293.5109 | 2.029%
2780 | 14-66.5 | -66.5877 | 13.9156 | 410.9603 | 147.4525 | 179.8721 | 218.9113 | 253.5662 | 293.7096 | 2.021%
2781 | 14-67 | -66.859 | 13.9156 | 428.5255 | 147.241 | 179.7818 | 218.8942 | 253.6036 | 293.8192 | 2.01%
2782 | 14-67 | -67.1303 | 13.9156 | 446.1359 | 146.995 | 179.6571 | 218.8371 | 253.5903 | 293.865 | 1.998%
2783 | 14-67.5 | -67.4016 | 13.9156 | 463.7864 | 146.6768 | 179.4577 | 218.6682 | 253.4203 | 293.6977 | 1.982%
2784 | 14-67.5 | -67.673 | 13.9156 | 481.4726 | 146.3114 | 179.211 | 218.4377 | 253.1656 | 293.4169 | 1.964%
2785 | 14-68 | -67.9443 | 13.9156 | 499.1907 | 145.9183 | 178.9381 | 218.1799 | 252.8758 | 293.0916 | 1.944%
2786 | 14-68 | -68.2156 | 13.9156 | 516.9374 | 145.4739 | 178.6212 | 217.8644 | 252.5061 | 292.6582 | 1.923%
2787 | 14-68.5 | -68.4869 | 13.9156 | 534.7097 | 145.0087 | 178.2926 | 217.537 | 252.1202 | 292.2035 | 1.9%
2788 | 14-69 | -68.7583 | 13.9156 | 552.5053 | 144.5397 | 177.9687 | 217.2213 | 251.7511 | 291.772 | 1.878%
2789 | 14-69 | -69.0296 | 13.9156 | 570.3218 | 143.9983 | 177.5499 | 216.7932 | 251.2203 | 291.117 | 1.853%
2790 | 14-69.5 | -69.3009 | 13.9156 | 588.1574 | 143.4168 | 177.0657 | 216.286 | 250.5686 | 290.2882 | 1.825%
2791 | 14-69.5 | -69.5722 | 13.9156 | 606.0104 | 142.8121 | 176.5318 | 215.7163 | 249.8165 | 289.3109 | 1.796%
2792 | 14-70 | -69.8435 | 13.9156 | 623.8792 | 142.1957 | 175.9793 | 215.0725 | 248.9343 | 288.132 | 1.768%
2793 | 14-70 | -70.1149 | 13.9156 | 641.7625 | 141.6119 | 175.4483 | 214.4216 | 248.0199 | 286.8882 | 1.741%
2794 | 14-70.5 | -70.3862 | 13.9156 | 659.6591 | 141.0746 | 174.9504 | 213.7831 | 247.1036 | 285.6236 | 1.717%
2795 | 14-70.5 | -70.6575 | 13.9156 | 677.5679 | 140.5812 | 174.5123 | 213.168 | 246.2034 | 284.3647 | 1.695%
2796 | 14-71 | -70.9288 | 13.9156 | 695.4879 | 140.1692 | 174.1736 | 212.6481 | 245.4278 | 283.2669 | 1.677%
2797 | 14-71 | -71.2001 | 13.9156 | 713.4183 | 139.8349 | 173.93 | 212.2224 | 244.7798 | 282.3382 | 1.663%
2798 | 14-71.5 | -71.4715 | 13.9156 | 731.3583 | 139.4847 | 173.6734 | 211.774 | 244.1021 | 281.3712 | 1.649%
2799 | 14-71.5 | -71.7428 | 13.9156 | 749.3072 | 139.1416 | 173.4196 | 211.3307 | 243.4363 | 280.4254 | 1.635%
2800 | 14-72 | -72.0141 | 13.9156 | 767.2643 | 138.8004 | 173.1608 | 210.884 | 242.7717 | 279.4866 | 1.621%
2801 | 14-72.5 | -72.2854 | 13.9156 | 785.229 | 138.4268 | 172.8613 | 210.386 | 242.04 | 278.4615 | 1.605%
2802 | 14-72.5 | -72.5568 | 13.9156 | 803.2008 | 138.0918 | 172.6212 | 209.9594 | 241.4192 | 277.597 | 1.591%
2803 | 14-73 | -72.8281 | 13.9156 | 821.1792 | 137.7872 | 172.4329 | 209.5959 | 240.8994 | 276.882 | 1.579%
2804 | 14-73 | -73.0994 | 13.9156 | 839.1638 | 137.4745 | 172.2581 | 209.2478 | 240.4171 | 276.233 | 1.567%
2805 | 14-73.5 | -73.3707 | 13.9156 | 857.1541 | 137.1467 | 172.0686 | 208.9282 | 240.0048 | 275.7074 | 1.554%
2806 | 14-73.5 | -73.642 | 13.9156 | 875.1498 | 136.7966 | 171.8573 | 208.6251 | 239.6441 | 275.2792 | 1.54%
2807 | 14-74 | -73.9134 | 13.9156 | 893.1504 | 136.4041 | 171.6032 | 208.3081 | 239.2901 | 274.8846 | 1.525%
2808 | 14-74 | -74.1847 | 13.9156 | 911.1558 | 135.9786 | 171.2826 | 207.9693 | 238.9288 | 274.5024 | 1.508%
2809 | 14-74.5 | -74.456 | 13.9156 | 929.1656 | 135.5056 | 170.8809 | 207.5807 | 238.5152 | 274.0662 | 1.489%
2810 | 14-74.5 | -74.7273 | 13.9156 | 947.1795 | 134.9578 | 170.3701 | 207.0886 | 237.9642 | 273.4505 | 1.466%
2811 | 14-75 | -74.9986 | 13.9156 | 965.1972 | 134.436 | 169.8635 | 206.614 | 237.4396 | 272.8719 | 1.445%
2812 | 14-75.5 | -75.27 | 13.9156 | 983.2185 | 133.9363 | 169.3588 | 206.1472 | 236.9258 | 272.308 | 1.424%
2813 | 14-75.5 | -75.5413 | 13.9156 | 1001.2433 | 133.45 | 168.8519 | 205.6751 | 236.4015 | 271.7268 | 1.404%
2814 | 14-76 | -75.8126 | 13.9156 | 1019.2712 | 133.0211 | 168.385 | 205.2495 | 235.9389 | 271.226 | 1.387%
2815 | 14-76 | -76.0839 | 13.9156 | 1037.3022 | 132.6384 | 167.9476 | 204.8577 | 235.5203 | 270.7817 | 1.371%
2816 | 14-76.5 | -76.3553 | 13.9156 | 1055.3359 | 132.289 | 167.5287 | 204.4879 | 235.1292 | 270.3714 | 1.357%
2817 | 14-76.5 | -76.6266 | 13.9156 | 1073.3723 | 132.0185 | 167.1715 | 204.1886 | 234.8292 | 270.0774 | 1.345%
2818 | 14-77 | -76.8979 | 13.9156 | 1091.4112 | 131.81 | 166.8643 | 203.9377 | 234.5836 | 269.8443 | 1.336%
2819 | 14-77 | -77.1692 | 13.9156 | 1109.4525 | 131.6513 | 166.6021 | 203.7217 | 234.368 | 269.6341 | 1.329%
2820 | 14-77.5 | -77.4405 | 13.9156 | 1127.4959 | 131.5768 | 166.4159 | 203.5764 | 234.2307 | 269.5102 | 1.325%
2821 | 14-77.5 | -77.7119 | 13.9156 | 1145.5415 | 131.5655 | 166.2932 | 203.4877 | 234.1549 | 269.4529 | 1.323%
2822 | 14-78 | -77.9832 | 13.9156 | 1163.5889 | 131.6156 | 166.2374 | 203.473 | 234.1726 | 269.5126 | 1.323%
2823 | 14-78.5 | -78.2545 | 13.9156 | 1181.6383 | 131.7778 | 166.2979 | 203.6059 | 234.3937 | 269.8454 | 1.328%
2824 | 14-78.5 | -78.5258 | 13.9156 | 1199.6893 | 131.9927 | 166.4218 | 203.8264 | 234.7379 | 270.3457 | 1.335%
2825 | 14-79 | -78.7971 | 13.9156 | 1217.742 | 132.2257 | 166.5764 | 204.1025 | 235.165 | 270.9633 | 1.343%
2826 | 14-79 | -79.0685 | 13.9156 | 1235.7962 | 132.5012 | 166.7811 | 204.4621 | 235.7155 | 271.7547 | 1.353%
2827 | 14-79.5 | -79.3398 | 13.9156 | 1253.8518 | 132.7642 | 166.9927 | 204.8538 | 236.3195 | 272.6272 | 1.363%
2828 | 14-79.5 | -79.6111 | 13.9156 | 1271.9088 | 133.0001 | 167.201 | 205.2634 | 236.9573 | 273.5539 | 1.372%
2829 | 14-80 | -79.8824 | 13.9156 | 1289.967 | 133.2388 | 167.4322 | 205.7195 | 237.6673 | 274.5855 | 1.382%
2830 | 14-80 | -80.1537 | 13.9156 | 1308.0265 | 133.3952 | 167.6121 | 206.1382 | 238.3401 | 275.5814 | 1.389%
2831 | 14-80.5 | -80.4251 | 13.9156 | 1326.087 | 133.4501 | 167.7214 | 206.503 | 238.9602 | 276.5278 | 1.392%
2832 | 14-80.5 | -80.6964 | 13.9156 | 1344.1486 | 133.4279 | 167.7761 | 206.8401 | 239.569 | 277.4854 | 1.393%
2833 | 14-81 | -80.9677 | 13.9156 | 1362.2111 | 133.2597 | 167.7149 | 207.0851 | 240.0838 | 278.3492 | 1.389%
2834 | 14-81 | -81.239 | 13.9156 | 1380.2745 | 132.9464 | 167.5366 | 207.2305 | 240.4915 | 279.0988 | 1.38%
2835 | 14-81.5 | -81.5104 | 13.9156 | 1398.3388 | 132.5141 | 167.2625 | 207.2921 | 240.8077 | 279.75 | 1.367%
2836 | 14-82 | -81.7817 | 13.9156 | 1416.4039 | 131.5548 | 166.4375 | 206.7755 | 240.3899 | 279.4756 | 1.334%
2837 | 14-82 | -82.053 | 13.9156 | 1434.4697 | 130.0333 | 164.9573 | 205.6062 | 239.1442 | 278.1583 | 1.283%
2838 | 14-82.5 | -82.3243 | 13.9156 | 1452.5361 | 128.0293 | 162.84 | 203.812 | 237.1525 | 275.906 | 1.216%
2839 | 14-82.5 | -82.5956 | 13.9156 | 1470.6032 | 125.8027 | 160.4318 | 201.7162 | 234.7994 | 273.1876 | 1.145%
2840 | 14-83 | -82.867 | 13.9156 | 1488.6709 | 123.4585 | 157.8585 | 199.4375 | 232.2302 | 270.1869 | 1.074%
2841 | 14-83 | -83.1383 | 13.9156 | 1506.739 | 121.0307 | 155.1562 | 197.0083 | 229.4886 | 266.9629 | 1.006%
2842 | 14-83.5 | -83.4096 | 13.9156 | 1524.8077 | 118.4174 | 152.1777 | 194.2921 | 226.3897 | 263.278 | 0.9361%
2843 | 14-83.5 | -83.6809 | 13.9156 | 1542.8768 | 115.6784 | 148.9791 | 191.2921 | 223.0222 | 259.2534 | 0.8673%
2844 | 14-84 | -83.9522 | 13.9156 | 1560.9462 | 112.8624 | 145.6176 | 188.0417 | 219.4519 | 254.9802 | 0.801%
2845 | 14-84 | -84.2236 | 13.9156 | 1579.016 | 110.037 | 142.2072 | 184.7174 | 215.7836 | 250.5793 | 0.739%
2846 | 14-84.5 | -84.4949 | 13.9156 | 1597.0862 | 107.2655 | 138.8127 | 181.4106 | 212.1067 | 246.1623 | 0.6824%
2847 | 14-85 | -84.7662 | 13.9156 | 1615.1566 | 104.568 | 135.4645 | 178.1711 | 208.4623 | 241.78 | 0.631%
2848 | 14-85 | -85.0375 | 13.9156 | 1633.2272 | 101.8078 | 131.9565 | 174.7733 | 204.5911 | 237.0688 | 0.5815%
2849 | 14-85.5 | -85.3089 | 13.9156 | 1651.298 | 99.3931 | 128.7669 | 171.7214 | 201.155 | 232.877 | 0.5405%
2850 | 14-85.5 | -85.5802 | 13.9156 | 1669.369 | 97.4288 | 126.08 | 169.128 | 198.3401 | 229.4412 | 0.5088%
2851 | 14-86 | -85.8515 | 13.9156 | 1687.4401 | 96.2516 | 124.5018 | 167.5859 | 196.7253 | 227.4781 | 0.491%
2852 | 14-86 | -86.1228 | 13.9156 | 1705.5113 | 95.6472 | 123.6683 | 166.78 | 195.9963 | 226.615 | 0.4823%
2853 | 14-86.5 | -86.3941 | 13.9156 | 1723.5826 | 95.5513 | 123.3925 | 166.6461 | 196.0435 | 226.7228 | 0.4811%
2854 | 14-86.5 | -86.6655 | 13.9156 | 1741.654 | 95.2917 | 123.0514 | 166.4064 | 195.7791 | 226.3733 | 0.4778%
2855 | 14-87 | -86.9368 | 13.9156 | 1759.7253 | 95.0468 | 122.7669 | 166.2529 | 195.4774 | 225.9267 | 0.4748%
2856 | 14-87 | -87.2081 | 13.9156 | 1777.7966 | 94.9288 | 122.6166 | 166.3399 | 195.2806 | 225.5636 | 0.4733%
2857 | 14-87.5 | -87.4794 | 13.9156 | 1795.8679 | 95.0687 | 122.7996 | 166.8085 | 195.3646 | 225.4847 | 0.4752%
2858 | 14-88 | -87.7507 | 13.9156 | 1813.939 | 95.3992 | 123.2003 | 167.4462 | 195.6045 | 225.5515 | 0.4793%
2859 | 14-88 | -88.0221 | 13.9156 | 1832.0101 | 95.9525 | 123.8757 | 168.2597 | 196.0525 | 225.8373 | 0.486%
2860 | 14-88.5 | -88.2934 | 13.9156 | 1850.0811 | 96.7918 | 124.9244 | 169.3012 | 196.7883 | 226.4342 | 0.4965%
2861 | 14-88.5 | -88.5647 | 13.9156 | 1868.1519 | 98.0696 | 126.6122 | 170.817 | 198.0654 | 227.665 | 0.5138%
2862 | 14-89 | -88.836 | 13.9156 | 1886.2225 | 99.8138 | 128.9899 | 172.8066 | 199.8657 | 229.4987 | 0.5391%
2863 | 14-89 | -89.1074 | 13.9156 | 1904.2929 | 102.0559 | 132.0197 | 175.2763 | 202.145 | 231.8676 | 0.5737%
2864 | 14-89.5 | -89.3787 | 13.9156 | 1922.3632 | 104.5652 | 135.0328 | 177.719 | 204.3903 | 234.1374 | 0.6124%
2865 | 14-89.5 | -89.65 | 13.9156 | 1940.4331 | 107.0569 | 137.8257 | 179.882 | 206.2418 | 235.8695 | 0.6515%
2866 | 14-90 | -89.9213 | 13.9156 | 1958.5028 | 109.6898 | 140.6075 | 181.866 | 207.8658 | 237.268 | 0.6941%
2867 | 14-90 | -90.1926 | 13.9156 | 1976.5722 | 113.0751 | 144.0335 | 184.5042 | 210.4168 | 239.8401 | 0.7562%
2868 | 14-90.5 | -90.464 | 13.9156 | 1994.6413 | 117.0782 | 148.0595 | 187.6765 | 213.7201 | 243.3523 | 0.8407%
2869 | 14-90.5 | -90.7353 | 13.9156 | 2012.7101 | 121.4669 | 152.4566 | 191.1344 | 217.4374 | 247.3773 | 0.9478%
2870 | 14-50 | -50.0371 | 14.1869 | 713.3194 | 133.1421 | 167.1795 | 202.5039 | 232.296 | 266.4736 | 1.367%
2871 | 14-50.5 | -50.3084 | 14.1869 | 695.3346 | 133.1071 | 167.3079 | 202.7299 | 232.6552 | 267.0002 | 1.368%
2872 | 14-50.5 | -50.5797 | 14.1869 | 677.3566 | 133.0379 | 167.4159 | 202.9322 | 232.9828 | 267.4855 | 1.368%
2873 | 14-51 | -50.851 | 14.1869 | 659.3862 | 132.9617 | 167.5236 | 203.1348 | 233.3094 | 267.9684 | 1.368%
2874 | 14-51 | -51.1224 | 14.1869 | 641.4239 | 132.9096 | 167.6558 | 203.3672 | 233.6735 | 268.498 | 1.369%
2875 | 14-51.5 | -51.3937 | 14.1869 | 623.4704 | 132.8531 | 167.7809 | 203.5899 | 234.0213 | 269.0033 | 1.37%
2876 | 14-51.5 | -51.665 | 14.1869 | 605.5267 | 132.8102 | 167.909 | 203.8245 | 234.389 | 269.5387 | 1.371%
2877 | 14-52 | -51.9363 | 14.1869 | 587.5935 | 132.7986 | 168.0504 | 204.0905 | 234.8074 | 270.1493 | 1.373%
2878 | 14-52 | -52.2077 | 14.1869 | 569.6719 | 132.7782 | 168.1655 | 204.3208 | 235.1778 | 270.6967 | 1.374%
2879 | 14-52.5 | -52.479 | 14.1869 | 551.7631 | 132.7764 | 168.2763 | 204.5439 | 235.5401 | 271.2354 | 1.376%
2880 | 14-53 | -52.7503 | 14.1869 | 533.8684 | 132.8115 | 168.3954 | 204.7785 | 235.9219 | 271.8036 | 1.379%
2881 | 14-53 | -53.0216 | 14.1869 | 515.9893 | 132.8321 | 168.4702 | 204.9549 | 236.2248 | 272.2675 | 1.381%
2882 | 14-53.5 | -53.2929 | 14.1869 | 498.1275 | 132.8717 | 168.528 | 205.1141 | 236.5094 | 272.712 | 1.383%
2883 | 14-53.5 | -53.5643 | 14.1869 | 480.285 | 132.9467 | 168.5816 | 205.2757 | 236.8041 | 273.1768 | 1.386%
2884 | 14-54 | -53.8356 | 14.1869 | 462.4639 | 133.0214 | 168.6078 | 205.4002 | 237.0471 | 273.5718 | 1.388%
2885 | 14-54 | -54.1069 | 14.1869 | 444.667 | 133.1327 | 168.645 | 205.534 | 237.3025 | 273.9831 | 1.392%
2886 | 14-54.5 | -54.3782 | 14.1869 | 426.8973 | 133.2923 | 168.7044 | 205.6911 | 237.5893 | 274.4362 | 1.397%
2887 | 14-54.5 | -54.6495 | 14.1869 | 409.1582 | 133.4623 | 168.7553 | 205.8196 | 237.8271 | 274.8141 | 1.402%
2888 | 14-55 | -54.9209 | 14.1869 | 391.4542 | 133.6766 | 168.8314 | 205.9608 | 238.0705 | 275.1879 | 1.408%
2889 | 14-55 | -55.1922 | 14.1869 | 373.79 | 133.9431 | 168.9418 | 206.121 | 238.3239 | 275.5598 | 1.417%
2890 | 14-55.5 | -55.4635 | 14.1869 | 356.1718 | 134.2166 | 169.0515 | 206.2238 | 238.4665 | 275.752 | 1.425%
2891 | 14-55.5 | -55.7348 | 14.1869 | 338.6066 | 134.5557 | 169.2184 | 206.3544 | 238.6148 | 275.9206 | 1.436%
2892 | 14-56 | -56.0061 | 14.1869 | 321.1033 | 134.9842 | 169.4662 | 206.5433 | 238.8038 | 276.1053 | 1.451%
2893 | 14-56.5 | -56.2775 | 14.1869 | 303.6725 | 135.4592 | 169.7626 | 206.7665 | 239.0122 | 276.2892 | 1.468%
2894 | 14-56.5 | -56.5488 | 14.1869 | 286.3276 | 136.05 | 170.1678 | 207.1059 | 239.3496 | 276.6164 | 1.489%
2895 | 14-57 | -56.8201 | 14.1869 | 269.0852 | 136.7659 | 170.6882 | 207.5653 | 239.8162 | 277.0817 | 1.517%
2896 | 14-57 | -57.0914 | 14.1869 | 251.9662 | 137.5348 | 171.2605 | 208.0668 | 240.3114 | 277.5571 | 1.548%
2897 | 14-57.5 | -57.3628 | 14.1869 | 234.9979 | 138.3982 | 171.9072 | 208.6494 | 240.8935 | 278.1248 | 1.583%
2898 | 14-57.5 | -57.6341 | 14.1869 | 218.2152 | 139.3416 | 172.6141 | 209.2958 | 241.5397 | 278.7555 | 1.623%
2899 | 14-58 | -57.9054 | 14.1869 | 201.6646 | 140.2966 | 173.3274 | 209.9392 | 242.1677 | 279.3478 | 1.665%
2900 | 14-58 | -58.1767 | 14.1869 | 185.4084 | 141.304 | 174.0785 | 210.6316 | 242.855 | 280.0119 | 1.71%
2901 | 14-58.5 | -58.448 | 14.1869 | 169.5311 | 142.3362 | 174.8463 | 211.3498 | 243.5731 | 280.713 | 1.758%
2902 | 14-58.5 | -58.7194 | 14.1869 | 154.15 | 143.3275 | 175.5816 | 212.042 | 244.2645 | 281.3868 | 1.806%
2903 | 14-59 | -58.9907 | 14.1869 | 139.4295 | 144.3246 | 176.3219 | 212.7868 | 245.0498 | 282.2075 | 1.855%
2904 | 14-59.5 | -59.262 | 14.1869 | 125.6019 | 145.3053 | 177.0405 | 213.5515 | 245.8855 | 283.1179 | 1.905%
2905 | 14-59.5 | -59.5333 | 14.1869 | 112.9957 | 146.215 | 177.7054 | 214.2873 | 246.7052 | 284.0298 | 1.952%
2906 | 14-60 | -59.8046 | 14.1869 | 102.0644 | 147.0918 | 178.3525 | 215.023 | 247.5335 | 284.9617 | 1.999%
2907 | 14-60 | -60.076 | 14.1869 | 93.398 | 147.885 | 178.9371 | 215.7002 | 248.3015 | 285.8322 | 2.043%
2908 | 14-60.5 | -60.3473 | 14.1869 | 87.6708 | 148.5316 | 179.3967 | 216.2448 | 248.924 | 286.5432 | 2.078%
2909 | 14-60.5 | -60.6186 | 14.1869 | 85.4756 | 149.1033 | 179.7967 | 216.7377 | 249.5031 | 287.2231 | 2.11%
2910 | 14-61 | -60.8899 | 14.1869 | 87.08 | 149.5836 | 180.1315 | 217.1697 | 250.0257 | 287.8536 | 2.136%
2911 | 14-61 | -61.1613 | 14.1869 | 92.286 | 149.9699 | 180.406 | 217.5446 | 250.4936 | 288.4341 | 2.158%
2912 | 14-61.5 | -61.4326 | 14.1869 | 100.5356 | 150.3299 | 180.6769 | 217.9342 | 250.9955 | 289.0734 | 2.178%
2913 | 14-61.5 | -61.7039 | 14.1869 | 111.1533 | 150.6281 | 180.9163 | 218.2966 | 251.4749 | 289.6973 | 2.195%
2914 | 14-62 | -61.9752 | 14.1869 | 123.5299 | 150.8549 | 181.1143 | 218.609 | 251.8968 | 290.255 | 2.207%
2915 | 14-62 | -62.2465 | 14.1869 | 137.1901 | 151.0735 | 181.3203 | 218.9318 | 252.3332 | 290.8323 | 2.22%
2916 | 14-62.5 | -62.5179 | 14.1869 | 151.7878 | 151.2567 | 181.5106 | 219.2291 | 252.7353 | 291.3645 | 2.231%
2917 | 14-63 | -62.7892 | 14.1869 | 167.0774 | 151.3868 | 181.6718 | 219.485 | 253.0843 | 291.8292 | 2.239%
2918 | 14-63 | -63.0605 | 14.1869 | 182.8855 | 151.4952 | 181.8194 | 219.7315 | 253.4308 | 292.3008 | 2.245%
2919 | 14-63.5 | -63.3318 | 14.1869 | 199.0885 | 151.5602 | 181.931 | 219.9435 | 253.7465 | 292.7472 | 2.249%
2920 | 14-63.5 | -63.6031 | 14.1869 | 215.5974 | 151.5965 | 182.0283 | 220.1492 | 254.066 | 293.2104 | 2.25%
2921 | 14-64 | -63.8745 | 14.1869 | 232.347 | 151.6582 | 182.1704 | 220.424 | 254.4797 | 293.7996 | 2.254%
2922 | 14-64 | -64.1458 | 14.1869 | 249.2887 | 151.7082 | 182.3151 | 220.6962 | 254.886 | 294.3751 | 2.257%
2923 | 14-64.5 | -64.4171 | 14.1869 | 266.386 | 151.7361 | 182.4458 | 220.9386 | 255.2469 | 294.8856 | 2.259%
2924 | 14-64.5 | -64.6884 | 14.1869 | 283.6105 | 151.7577 | 182.5723 | 221.168 | 255.5876 | 295.3665 | 2.261%
2925 | 14-65 | -64.9598 | 14.1869 | 300.9406 | 151.7413 | 182.6615 | 221.3348 | 255.8399 | 295.7269 | 2.261%
2926 | 14-65 | -65.2311 | 14.1869 | 318.3588 | 151.7014 | 182.7255 | 221.4612 | 256.0355 | 296.0102 | 2.259%
2927 | 14-65.5 | -65.5024 | 14.1869 | 335.8515 | 151.6658 | 182.7906 | 221.5916 | 256.2372 | 296.3023 | 2.258%
2928 | 14-66 | -65.7737 | 14.1869 | 353.4075 | 151.6006 | 182.8261 | 221.6881 | 256.3982 | 296.5454 | 2.255%
2929 | 14-66 | -66.045 | 14.1869 | 371.0179 | 151.5136 | 182.842 | 221.7728 | 256.5531 | 296.7906 | 2.25%
2930 | 14-66.5 | -66.3164 | 14.1869 | 388.6753 | 151.4203 | 182.8551 | 221.8748 | 256.7447 | 297.0974 | 2.244%
2931 | 14-66.5 | -66.5877 | 14.1869 | 406.3734 | 151.2737 | 182.8197 | 221.9192 | 256.8672 | 297.3215 | 2.236%
2932 | 14-67 | -66.859 | 14.1869 | 424.1073 | 151.0805 | 182.7416 | 221.9083 | 256.9191 | 297.4563 | 2.225%
2933 | 14-67 | -67.1303 | 14.1869 | 441.8724 | 150.8545 | 182.6327 | 221.8583 | 256.9207 | 297.5271 | 2.212%
2934 | 14-67.5 | -67.4016 | 14.1869 | 459.6653 | 150.5573 | 182.4517 | 221.6948 | 256.7633 | 297.3819 | 2.195%
2935 | 14-67.5 | -67.673 | 14.1869 | 477.4827 | 150.2154 | 182.2273 | 221.4718 | 256.5243 | 297.1274 | 2.176%
2936 | 14-68 | -67.9443 | 14.1869 | 495.3221 | 149.8487 | 181.9815 | 221.2258 | 256.2564 | 296.8368 | 2.156%
2937 | 14-68 | -68.2156 | 14.1869 | 513.181 | 149.4321 | 181.6953 | 220.9247 | 255.9139 | 296.4471 | 2.133%
2938 | 14-68.5 | -68.4869 | 14.1869 | 531.0575 | 148.993 | 181.3988 | 220.6138 | 255.5593 | 296.0429 | 2.109%
2939 | 14-69 | -68.7583 | 14.1869 | 548.9498 | 148.5485 | 181.1076 | 220.3158 | 255.2247 | 295.6674 | 2.086%
2940 | 14-69 | -69.0296 | 14.1869 | 566.8565 | 148.048 | 180.754 | 219.9281 | 254.7578 | 295.1062 | 2.06%
2941 | 14-69.5 | -69.3009 | 14.1869 | 584.7761 | 147.5225 | 180.3636 | 219.4804 | 254.1942 | 294.4015 | 2.032%
2942 | 14-69.5 | -69.5722 | 14.1869 | 602.7076 | 146.9889 | 179.9496 | 218.9874 | 253.5517 | 293.5751 | 2.005%
2943 | 14-70 | -69.8435 | 14.1869 | 620.6497 | 146.4353 | 179.508 | 218.4078 | 252.7622 | 292.5243 | 1.978%
2944 | 14-70 | -70.1149 | 14.1869 | 638.6017 | 145.9097 | 179.0833 | 217.8163 | 251.9331 | 291.3982 | 1.952%
2945 | 14-70.5 | -70.3862 | 14.1869 | 656.5627 | 145.4264 | 178.6867 | 217.2334 | 251.096 | 290.2422 | 1.929%
2946 | 14-70.5 | -70.6575 | 14.1869 | 674.5319 | 144.96 | 178.3098 | 216.639 | 250.2279 | 289.03 | 1.907%
2947 | 14-71 | -70.9288 | 14.1869 | 692.5087 | 144.5496 | 177.993 | 216.1074 | 249.4402 | 287.9197 | 1.888%
2948 | 14-71 | -71.2001 | 14.1869 | 710.4924 | 144.1945 | 177.7356 | 215.6415 | 248.7403 | 286.9249 | 1.872%
2949 | 14-71.5 | -71.4715 | 14.1869 | 728.4826 | 143.8222 | 177.4646 | 215.1509 | 248.0055 | 285.8824 | 1.855%
2950 | 14-71.5 | -71.7428 | 14.1869 | 746.4788 | 143.4584 | 177.1973 | 214.6655 | 247.2794 | 284.8535 | 1.839%
2951 | 14-72 | -72.0141 | 14.1869 | 764.4804 | 143.0997 | 176.9266 | 214.1785 | 246.554 | 283.8281 | 1.823%
2952 | 14-72.5 | -72.2854 | 14.1869 | 782.4871 | 142.7102 | 176.6194 | 213.644 | 245.7662 | 282.722 | 1.805%
2953 | 14-72.5 | -72.5568 | 14.1869 | 800.4985 | 142.3436 | 176.3435 | 213.1637 | 245.0672 | 281.749 | 1.788%
2954 | 14-73 | -72.8281 | 14.1869 | 818.5143 | 141.9907 | 176.0906 | 212.7275 | 244.4451 | 280.8946 | 1.772%
2955 | 14-73 | -73.0994 | 14.1869 | 836.5342 | 141.6108 | 175.8241 | 212.2861 | 243.8331 | 280.0708 | 1.755%
2956 | 14-73.5 | -73.3707 | 14.1869 | 854.5579 | 141.2204 | 175.55 | 211.8824 | 243.3027 | 279.3849 | 1.738%
2957 | 14-73.5 | -73.642 | 14.1869 | 872.5851 | 140.8109 | 175.2598 | 211.503 | 242.8339 | 278.8087 | 1.719%
2958 | 14-74 | -73.9134 | 14.1869 | 890.6156 | 140.3612 | 174.9319 | 211.116 | 242.3802 | 278.2776 | 1.699%
2959 | 14-74 | -74.1847 | 14.1869 | 908.6492 | 139.9032 | 174.5771 | 210.7452 | 241.9695 | 277.8239 | 1.678%
2960 | 14-74.5 | -74.456 | 14.1869 | 926.6856 | 139.4217 | 174.1812 | 210.3614 | 241.5558 | 277.3808 | 1.656%
2961 | 14-74.5 | -74.7273 | 14.1869 | 944.7247 | 138.8852 | 173.7131 | 209.9058 | 241.048 | 276.8159 | 1.631%
2962 | 14-75 | -74.9986 | 14.1869 | 962.7663 | 138.3736 | 173.2506 | 209.4732 | 240.5757 | 276.3021 | 1.608%
2963 | 14-75.5 | -75.27 | 14.1869 | 980.8102 | 137.8811 | 172.7899 | 209.0513 | 240.1195 | 275.8112 | 1.586%
2964 | 14-75.5 | -75.5413 | 14.1869 | 998.8563 | 137.3972 | 172.3249 | 208.6217 | 239.6503 | 275.3005 | 1.564%
2965 | 14-76 | -75.8126 | 14.1869 | 1016.9044 | 136.9676 | 171.8951 | 208.235 | 239.2361 | 274.8596 | 1.545%
2966 | 14-76 | -76.0839 | 14.1869 | 1034.9544 | 136.5807 | 171.4906 | 207.8772 | 238.8575 | 274.4621 | 1.527%
2967 | 14-76.5 | -76.3553 | 14.1869 | 1053.0062 | 136.2236 | 171.1007 | 207.5351 | 238.4957 | 274.0825 | 1.511%
2968 | 14-76.5 | -76.6266 | 14.1869 | 1071.0597 | 135.944 | 170.7678 | 207.2595 | 238.2179 | 273.8082 | 1.498%
2969 | 14-77 | -76.8979 | 14.1869 | 1089.1147 | 135.7257 | 170.4809 | 207.0287 | 237.9889 | 273.5866 | 1.488%
2970 | 14-77 | -77.1692 | 14.1869 | 1107.1712 | 135.5578 | 170.236 | 206.8304 | 237.7868 | 273.3841 | 1.48%
2971 | 14-77.5 | -77.4405 | 14.1869 | 1125.229 | 135.4759 | 170.0654 | 206.702 | 237.6623 | 273.2672 | 1.475%
2972 | 14-77.5 | -77.7119 | 14.1869 | 1143.2881 | 135.4599 | 169.9574 | 206.6296 | 237.5984 | 273.2156 | 1.473%
2973 | 14-78 | -77.9832 | 14.1869 | 1161.3483 | 135.5094 | 169.9163 | 206.6312 | 237.6277 | 273.2807 | 1.474%
2974 | 14-78.5 | -78.2545 | 14.1869 | 1179.4097 | 135.6768 | 169.9903 | 206.7822 | 237.8621 | 273.62 | 1.48%
2975 | 14-78.5 | -78.5258 | 14.1869 | 1197.4721 | 135.9008 | 170.1266 | 207.0191 | 238.2163 | 274.1218 | 1.488%
2976 | 14-79 | -78.7971 | 14.1869 | 1215.5354 | 136.1476 | 170.2937 | 207.3099 | 238.6505 | 274.7362 | 1.497%
2977 | 14-79 | -79.0685 | 14.1869 | 1233.5996 | 136.4435 | 170.5124 | 207.6866 | 239.2105 | 275.5266 | 1.509%
2978 | 14-79.5 | -79.3398 | 14.1869 | 1251.6646 | 136.7341 | 170.7419 | 208.0983 | 239.8277 | 276.4026 | 1.521%
2979 | 14-79.5 | -79.6111 | 14.1869 | 1269.7303 | 137.0049 | 170.9727 | 208.5326 | 240.4855 | 277.3425 | 1.532%
2980 | 14-80 | -79.8824 | 14.1869 | 1287.7968 | 137.2862 | 171.2301 | 209.0202 | 241.2254 | 278.401 | 1.544%
2981 | 14-80 | -80.1537 | 14.1869 | 1305.8638 | 137.491 | 171.4412 | 209.4763 | 241.9377 | 279.4381 | 1.553%
2982 | 14-80.5 | -80.4251 | 14.1869 | 1323.9315 | 137.5981 | 171.5863 | 209.8833 | 242.6053 | 280.4376 | 1.558%
2983 | 14-80.5 | -80.6964 | 14.1869 | 1341.9997 | 137.6305 | 171.6804 | 210.2666 | 243.2675 | 281.4565 | 1.56%
2984 | 14-81 | -80.9677 | 14.1869 | 1360.0684 | 137.5171 | 171.6638 | 210.5603 | 243.8395 | 282.3872 | 1.556%
2985 | 14-81 | -81.239 | 14.1869 | 1378.1375 | 137.2568 | 171.5339 | 210.7555 | 244.3071 | 283.2083 | 1.547%
2986 | 14-81.5 | -81.5104 | 14.1869 | 1396.207 | 136.8731 | 171.31 | 210.8673 | 244.6855 | 283.9358 | 1.533%
2987 | 14-82 | -81.7817 | 14.1869 | 1414.2768 | 135.9597 | 170.5568 | 210.4155 | 244.3509 | 283.7669 | 1.498%
2988 | 14-82 | -82.053 | 14.1869 | 1432.347 | 134.4795 | 169.1711 | 209.3318 | 243.2178 | 282.5958 | 1.441%
2989 | 14-82.5 | -82.3243 | 14.1869 | 1450.4174 | 132.5086 | 167.1647 | 207.6667 | 241.3691 | 280.5323 | 1.367%
2990 | 14-82.5 | -82.5956 | 14.1869 | 1468.4881 | 130.3068 | 164.8735 | 205.7198 | 239.1765 | 278.0292 | 1.288%
2991 | 14-83 | -82.867 | 14.1869 | 1486.5589 | 127.9789 | 162.4189 | 203.6027 | 236.7803 | 275.2636 | 1.21%
2992 | 14-83 | -83.1383 | 14.1869 | 1504.6299 | 125.5587 | 159.8353 | 201.3454 | 234.2222 | 272.2914 | 1.134%
2993 | 14-83.5 | -83.4096 | 14.1869 | 1522.7011 | 122.9328 | 156.9586 | 198.778 | 231.2815 | 268.8246 | 1.056%
2994 | 14-83.5 | -83.6809 | 14.1869 | 1540.7723 | 120.1647 | 153.8448 | 195.9012 | 228.0424 | 264.9763 | 0.9784%
2995 | 14-84 | -83.9522 | 14.1869 | 1558.8436 | 117.3049 | 150.5513 | 192.7491 | 224.5713 | 260.8366 | 0.9035%
2996 | 14-84 | -84.2236 | 14.1869 | 1576.9149 | 114.428 | 147.2129 | 189.5378 | 221.0084 | 256.5757 | 0.8336%
2997 | 14-84.5 | -84.4949 | 14.1869 | 1594.9862 | 111.6001 | 143.8939 | 186.3596 | 217.4465 | 252.3094 | 0.77%
2998 | 14-85 | -84.7662 | 14.1869 | 1613.0575 | 108.8428 | 140.6238 | 183.2612 | 213.9254 | 248.0864 | 0.7124%
2999 | 14-85 | -85.0375 | 14.1869 | 1631.1288 | 105.9917 | 137.1622 | 179.9553 | 210.1149 | 243.4523 | 0.6563%
3000 | 14-85.5 | -85.3089 | 14.1869 | 1649.2 | 103.4537 | 133.958 | 176.9303 | 206.6582 | 239.2312 | 0.6093%
3001 | 14-85.5 | -85.5802 | 14.1869 | 1667.271 | 101.3406 | 131.1911 | 174.3002 | 203.7438 | 235.6634 | 0.572%
3002 | 14-86 | -85.8515 | 14.1869 | 1685.342 | 100.0648 | 129.5783 | 172.7363 | 202.0795 | 233.6361 | 0.5511%
3003 | 14-86 | -86.1228 | 14.1869 | 1703.4128 | 99.4114 | 128.7399 | 171.9464 | 201.3658 | 232.7974 | 0.5412%
3004 | 14-86.5 | -86.3941 | 14.1869 | 1721.4834 | 99.3042 | 128.4802 | 171.8564 | 201.4792 | 233.0015 | 0.5401%
3005 | 14-86.5 | -86.6655 | 14.1869 | 1739.5538 | 98.9384 | 128.071 | 171.5343 | 201.1278 | 232.554 | 0.5352%
3006 | 14-87 | -86.9368 | 14.1869 | 1757.6239 | 98.5075 | 127.6007 | 171.1991 | 200.6227 | 231.8704 | 0.5293%
3007 | 14-87 | -87.2081 | 14.1869 | 1775.6939 | 98.1316 | 127.1548 | 171.0138 | 200.1261 | 231.1608 | 0.524%
3008 | 14-87.5 | -87.4794 | 14.1869 | 1793.7635 | 97.9849 | 127.0027 | 171.1781 | 199.8932 | 230.731 | 0.5222%
3009 | 14-88 | -87.7507 | 14.1869 | 1811.8329 | 97.9949 | 127.0126 | 171.4493 | 199.7685 | 230.3974 | 0.5222%
3010 | 14-88 | -88.0221 | 14.1869 | 1829.902 | 98.1937 | 127.2413 | 171.8419 | 199.8016 | 230.2298 | 0.5245%
3011 | 14-88.5 | -88.2934 | 14.1869 | 1847.9707 | 98.6478 | 127.7927 | 172.4161 | 200.0814 | 230.3335 | 0.5301%
3012 | 14-88.5 | -88.5647 | 14.1869 | 1866.0391 | 99.5403 | 128.968 | 173.4825 | 200.9323 | 231.1194 | 0.5429%
3013 | 14-89 | -88.836 | 14.1869 | 1884.1072 | 100.8904 | 130.8133 | 175.0352 | 202.326 | 232.5414 | 0.5635%
3014 | 14-89 | -89.1074 | 14.1869 | 1902.1748 | 102.7015 | 133.2722 | 177.0554 | 204.1846 | 234.4879 | 0.5925%
3015 | 14-89.5 | -89.3787 | 14.1869 | 1920.242 | 104.6463 | 135.5997 | 178.9294 | 205.8622 | 236.1518 | 0.6228%
3016 | 14-89.5 | -89.65 | 14.1869 | 1938.3088 | 106.4816 | 137.6499 | 180.4447 | 207.0438 | 237.1456 | 0.6506%
3017 | 14-90 | -89.9213 | 14.1869 | 1956.3752 | 108.367 | 139.644 | 181.7168 | 207.9131 | 237.6958 | 0.6789%
3018 | 14-90 | -90.1926 | 14.1869 | 1974.4411 | 111.0828 | 142.3464 | 183.7347 | 209.8301 | 239.5786 | 0.7253%
3019 | 14-90.5 | -90.464 | 14.1869 | 1992.5066 | 114.5069 | 145.7823 | 186.4036 | 212.6418 | 242.5833 | 0.7922%
3020 | 14-90.5 | -90.7353 | 14.1869 | 2010.5715 | 118.423 | 149.7473 | 189.5044 | 216.0361 | 246.3098 | 0.8797%
3021 | 14-50 | -50.0371 | 14.4583 | 710.8789 | 135.7255 | 169.5751 | 204.5738 | 234.5845 | 269.0003 | 1.471%
3022 | 14-50.5 | -50.3084 | 14.4583 | 692.8535 | 135.7068 | 169.6995 | 204.8023 | 234.9479 | 269.5331 | 1.472%
3023 | 14-50.5 | -50.5797 | 14.4583 | 674.8322 | 135.6539 | 169.8062 | 205.0082 | 235.2814 | 270.027 | 1.472%
3024 | 14-51 | -50.851 | 14.4583 | 656.8155 | 135.5967 | 169.9172 | 205.2196 | 235.621 | 270.5281 | 1.472%
3025 | 14-51 | -51.1224 | 14.4583 | 638.8036 | 135.5681 | 170.0582 | 205.4686 | 236.009 | 271.0906 | 1.474%
3026 | 14-51.5 | -51.3937 | 14.4583 | 620.7972 | 135.5364 | 170.1963 | 205.7115 | 236.3859 | 271.6359 | 1.475%
3027 | 14-51.5 | -51.665 | 14.4583 | 602.7966 | 135.5183 | 170.3401 | 205.9694 | 236.7869 | 272.2171 | 1.477%
3028 | 14-52 | -51.9363 | 14.4583 | 584.8024 | 135.5312 | 170.4995 | 206.2619 | 237.243 | 272.8793 | 1.48%
3029 | 14-52 | -52.2077 | 14.4583 | 566.8154 | 135.5317 | 170.6312 | 206.5155 | 237.6463 | 273.4718 | 1.482%
3030 | 14-52.5 | -52.479 | 14.4583 | 548.8361 | 135.5465 | 170.7554 | 206.759 | 238.0377 | 274.0503 | 1.484%
3031 | 14-53 | -52.7503 | 14.4583 | 530.8655 | 135.5941 | 170.8838 | 207.0118 | 238.4456 | 274.6543 | 1.488%
3032 | 14-53 | -53.0216 | 14.4583 | 512.9044 | 135.6209 | 170.9648 | 207.2017 | 238.7679 | 275.145 | 1.49%
3033 | 14-53.5 | -53.2929 | 14.4583 | 494.954 | 135.6639 | 171.0278 | 207.3741 | 239.0705 | 275.6134 | 1.492%
3034 | 14-53.5 | -53.5643 | 14.4583 | 477.0155 | 135.7409 | 171.0868 | 207.5509 | 239.3844 | 276.1022 | 1.495%
3035 | 14-54 | -53.8356 | 14.4583 | 459.0903 | 135.8133 | 171.1171 | 207.69 | 239.6459 | 276.5203 | 1.497%
3036 | 14-54 | -54.1069 | 14.4583 | 441.18 | 135.9172 | 171.1544 | 207.8345 | 239.9138 | 276.9461 | 1.501%
3037 | 14-54.5 | -54.3782 | 14.4583 | 423.2866 | 136.0634 | 171.2088 | 207.9975 | 240.2058 | 277.403 | 1.505%
3038 | 14-54.5 | -54.6495 | 14.4583 | 405.4123 | 136.2138 | 171.2499 | 208.1254 | 240.4395 | 277.7723 | 1.51%
3039 | 14-55 | -54.9209 | 14.4583 | 387.5598 | 136.4046 | 171.3125 | 208.2641 | 240.6767 | 278.135 | 1.516%
3040 | 14-55 | -55.1922 | 14.4583 | 369.7323 | 136.6437 | 171.4058 | 208.4202 | 240.9221 | 278.4937 | 1.524%
3041 | 14-55.5 | -55.4635 | 14.4583 | 351.9336 | 136.883 | 171.491 | 208.5086 | 241.042 | 278.6529 | 1.532%
3042 | 14-55.5 | -55.7348 | 14.4583 | 334.1684 | 137.1842 | 171.6291 | 208.6204 | 241.1618 | 278.7806 | 1.543%
3043 | 14-56 | -56.0061 | 14.4583 | 316.4423 | 137.5717 | 171.8433 | 208.7863 | 241.3172 | 278.9184 | 1.557%
3044 | 14-56.5 | -56.2775 | 14.4583 | 298.7623 | 138.0029 | 172.1024 | 208.9813 | 241.4856 | 279.0475 | 1.574%
3045 | 14-56.5 | -56.5488 | 14.4583 | 281.1372 | 138.5491 | 172.4652 | 209.2895 | 241.7799 | 279.3166 | 1.596%
3046 | 14-57 | -56.8201 | 14.4583 | 263.5779 | 139.2209 | 172.9384 | 209.7154 | 242.2016 | 279.7229 | 1.624%
3047 | 14-57 | -57.0914 | 14.4583 | 246.0986 | 139.949 | 173.4632 | 210.185 | 242.6565 | 280.1476 | 1.655%
3048 | 14-57.5 | -57.3628 | 14.4583 | 228.7177 | 140.7786 | 174.0631 | 210.7401 | 243.2048 | 280.674 | 1.691%
3049 | 14-57.5 | -57.6341 | 14.4583 | 211.4594 | 141.6964 | 174.7254 | 211.3638 | 243.824 | 281.2729 | 1.733%
3050 | 14-58 | -57.9054 | 14.4583 | 194.3565 | 142.6372 | 175.4007 | 211.9911 | 244.4333 | 281.8436 | 1.777%
3051 | 14-58 | -58.1767 | 14.4583 | 177.4538 | 143.6423 | 176.1197 | 212.6753 | 245.1111 | 282.4968 | 1.825%
3052 | 14-58.5 | -58.448 | 14.4583 | 160.8147 | 144.6849 | 176.8625 | 213.3921 | 245.8271 | 283.1948 | 1.877%
3053 | 14-58.5 | -58.7194 | 14.4583 | 144.5302 | 145.6995 | 177.5822 | 214.0889 | 246.5215 | 283.8697 | 1.93%
3054 | 14-59 | -58.9907 | 14.4583 | 128.7349 | 146.7357 | 178.3192 | 214.8522 | 247.327 | 284.7123 | 1.984%
3055 | 14-59.5 | -59.262 | 14.4583 | 113.6331 | 147.7774 | 179.0602 | 215.6663 | 248.2213 | 285.6922 | 2.041%
3056 | 14-59.5 | -59.5333 | 14.4583 | 99.541 | 148.7901 | 179.8015 | 216.5187 | 249.1833 | 286.7775 | 2.098%
3057 | 14-60 | -59.8046 | 14.4583 | 86.9507 | 149.8113 | 180.5786 | 217.4398 | 250.2405 | 287.9907 | 2.157%
3058 | 14-60 | -60.076 | 14.4583 | 76.6066 | 150.7636 | 181.3137 | 218.3265 | 251.2677 | 289.1806 | 2.213%
3059 | 14-60.5 | -60.3473 | 14.4583 | 69.5186 | 151.5416 | 181.8913 | 219.0314 | 252.0877 | 290.1342 | 2.26%
3060 | 14-60.5 | -60.6186 | 14.4583 | 66.7324 | 152.2133 | 182.3719 | 219.6319 | 252.7977 | 290.973 | 2.3%
3061 | 14-61 | -60.8899 | 14.4583 | 68.7729 | 152.776 | 182.7688 | 220.1425 | 253.4136 | 291.7143 | 2.335%
3062 | 14-61 | -61.1613 | 14.4583 | 75.2485 | 153.2442 | 183.1095 | 220.5957 | 253.9726 | 292.4007 | 2.363%
3063 | 14-61.5 | -61.4326 | 14.4583 | 85.1533 | 153.6823 | 183.4458 | 221.0613 | 254.5615 | 293.1396 | 2.39%
3064 | 14-61.5 | -61.7039 | 14.4583 | 97.4471 | 154.0526 | 183.7479 | 221.4938 | 255.1194 | 293.8511 | 2.413%
3065 | 14-62 | -61.9752 | 14.4583 | 111.3414 | 154.3437 | 184.003 | 221.8669 | 255.6064 | 294.4782 | 2.431%
3066 | 14-62 | -62.2465 | 14.4583 | 126.3091 | 154.6189 | 184.2583 | 222.2416 | 256.0966 | 295.1105 | 2.448%
3067 | 14-62.5 | -62.5179 | 14.4583 | 142.0112 | 154.8499 | 184.4905 | 222.5825 | 256.5426 | 295.686 | 2.463%
3068 | 14-63 | -62.7892 | 14.4583 | 158.2292 | 155.0123 | 184.6736 | 222.8568 | 256.9055 | 296.1582 | 2.474%
3069 | 14-63 | -63.0605 | 14.4583 | 174.8195 | 155.1169 | 184.7955 | 223.0613 | 257.1913 | 296.5457 | 2.48%
3070 | 14-63.5 | -63.3318 | 14.4583 | 191.6854 | 155.1409 | 184.8325 | 223.167 | 257.3666 | 296.8093 | 2.481%
3071 | 14-63.5 | -63.6031 | 14.4583 | 208.7602 | 155.1245 | 184.8385 | 223.2455 | 257.5194 | 297.0574 | 2.478%
3072 | 14-64 | -63.8745 | 14.4583 | 225.9965 | 155.1629 | 184.9258 | 223.4449 | 257.8315 | 297.5126 | 2.48%
3073 | 14-64 | -64.1458 | 14.4583 | 243.36 | 155.2175 | 185.0505 | 223.6902 | 258.1974 | 298.0305 | 2.483%
3074 | 14-64.5 | -64.4171 | 14.4583 | 260.8251 | 155.2625 | 185.177 | 223.9291 | 258.5483 | 298.5224 | 2.485%
3075 | 14-64.5 | -64.6884 | 14.4583 | 278.3729 | 155.2952 | 185.2918 | 224.149 | 258.8732 | 298.9796 | 2.487%
3076 | 14-65 | -64.9598 | 14.4583 | 295.9885 | 155.2857 | 185.364 | 224.2999 | 259.103 | 299.3091 | 2.487%
3077 | 14-65 | -65.2311 | 14.4583 | 313.6605 | 155.2507 | 185.4091 | 224.4077 | 259.2741 | 299.5605 | 2.484%
3078 | 14-65.5 | -65.5024 | 14.4583 | 331.3798 | 155.2197 | 185.4564 | 224.5222 | 259.4564 | 299.8289 | 2.482%
3079 | 14-66 | -65.7737 | 14.4583 | 349.1393 | 155.1606 | 185.4787 | 224.6069 | 259.6048 | 300.0587 | 2.478%
3080 | 14-66 | -66.045 | 14.4583 | 366.9331 | 155.0822 | 185.4873 | 224.685 | 259.7541 | 300.2997 | 2.473%
3081 | 14-66.5 | -66.3164 | 14.4583 | 384.7563 | 155.0001 | 185.4989 | 224.7858 | 259.9467 | 300.6102 | 2.467%
3082 | 14-66.5 | -66.5877 | 14.4583 | 402.6051 | 154.8654 | 185.4648 | 224.8282 | 260.069 | 300.8366 | 2.458%
3083 | 14-67 | -66.859 | 14.4583 | 420.4761 | 154.6852 | 185.391 | 224.8154 | 260.1214 | 300.975 | 2.446%
3084 | 14-67 | -67.1303 | 14.4583 | 438.3667 | 154.474 | 185.2907 | 224.7657 | 260.1268 | 301.0542 | 2.432%
3085 | 14-67.5 | -67.4016 | 14.4583 | 456.2745 | 154.1926 | 185.121 | 224.6019 | 259.9736 | 300.9189 | 2.414%
3086 | 14-67.5 | -67.673 | 14.4583 | 474.1975 | 153.8686 | 184.9122 | 224.3799 | 259.7405 | 300.6768 | 2.394%
3087 | 14-68 | -67.9443 | 14.4583 | 492.134 | 153.5229 | 184.6866 | 224.1376 | 259.482 | 300.4029 | 2.373%
3088 | 14-68 | -68.2156 | 14.4583 | 510.0826 | 153.1294 | 184.4236 | 223.841 | 259.1509 | 300.0337 | 2.349%
3089 | 14-68.5 | -68.4869 | 14.4583 | 528.0421 | 152.7137 | 184.1509 | 223.5352 | 258.81 | 299.6544 | 2.324%
3090 | 14-69 | -68.7583 | 14.4583 | 546.0113 | 152.2922 | 183.8827 | 223.2427 | 258.491 | 299.3077 | 2.299%
3091 | 14-69 | -69.0296 | 14.4583 | 563.9892 | 151.8252 | 183.5703 | 222.8715 | 258.0549 | 298.7955 | 2.273%
3092 | 14-69.5 | -69.3009 | 14.4583 | 581.9751 | 151.3399 | 183.2371 | 222.4514 | 257.5374 | 298.1606 | 2.245%
3093 | 14-69.5 | -69.5722 | 14.4583 | 599.9682 | 150.8531 | 182.8947 | 221.9966 | 256.9562 | 297.4246 | 2.219%
3094 | 14-70 | -69.8435 | 14.4583 | 617.9678 | 150.3377 | 182.5159 | 221.4442 | 256.2144 | 296.4478 | 2.191%
3095 | 14-70 | -70.1149 | 14.4583 | 635.9734 | 149.8446 | 182.1488 | 220.876 | 255.4284 | 295.39 | 2.165%
3096 | 14-70.5 | -70.3862 | 14.4583 | 653.9844 | 149.3887 | 181.805 | 220.314 | 254.631 | 294.298 | 2.142%
3097 | 14-70.5 | -70.6575 | 14.4583 | 672.0004 | 148.9316 | 181.455 | 219.7175 | 253.7714 | 293.1081 | 2.119%
3098 | 14-71 | -70.9288 | 14.4583 | 690.021 | 148.5144 | 181.1407 | 219.164 | 252.9641 | 291.9818 | 2.099%
3099 | 14-71 | -71.2001 | 14.4583 | 708.0458 | 148.139 | 180.8645 | 218.6594 | 252.2201 | 290.9368 | 2.08%
3100 | 14-71.5 | -71.4715 | 14.4583 | 726.0744 | 147.7472 | 180.5762 | 218.1296 | 251.4379 | 289.8373 | 2.061%
3101 | 14-71.5 | -71.7428 | 14.4583 | 744.1065 | 147.3663 | 180.2948 | 217.6074 | 250.6642 | 288.7477 | 2.043%
3102 | 14-72 | -72.0141 | 14.4583 | 762.1419 | 146.9941 | 180.0142 | 217.0876 | 249.8935 | 287.6617 | 2.025%
3103 | 14-72.5 | -72.2854 | 14.4583 | 780.1804 | 146.5908 | 179.7019 | 216.5248 | 249.0657 | 286.5009 | 2.005%
3104 | 14-72.5 | -72.5568 | 14.4583 | 798.2216 | 146.2001 | 179.4066 | 216.0101 | 248.3189 | 285.4634 | 1.986%
3105 | 14-73 | -72.8281 | 14.4583 | 816.2654 | 145.8151 | 179.1193 | 215.532 | 247.6389 | 284.5314 | 1.967%
3106 | 14-73 | -73.0994 | 14.4583 | 834.3115 | 145.3932 | 178.8038 | 215.0374 | 246.9536 | 283.6091 | 1.946%
3107 | 14-73.5 | -73.3707 | 14.4583 | 852.3599 | 144.9668 | 178.489 | 214.5912 | 246.3627 | 282.8402 | 1.924%
3108 | 14-73.5 | -73.642 | 14.4583 | 870.4103 | 144.5269 | 178.1661 | 214.1787 | 245.8448 | 282.1951 | 1.902%
3109 | 14-74 | -73.9134 | 14.4583 | 888.4626 | 144.0517 | 177.8136 | 213.7672 | 245.3527 | 281.6078 | 1.878%
3110 | 14-74 | -74.1847 | 14.4583 | 906.5166 | 143.5867 | 177.4631 | 213.4013 | 244.9427 | 281.1494 | 1.854%
3111 | 14-74.5 | -74.456 | 14.4583 | 924.5723 | 143.1153 | 177.0993 | 213.0494 | 244.5663 | 280.7498 | 1.831%
3112 | 14-74.5 | -74.7273 | 14.4583 | 942.6294 | 142.6017 | 176.6871 | 212.6459 | 244.1238 | 280.2661 | 1.805%
3113 | 14-75 | -74.9986 | 14.4583 | 960.6879 | 142.112 | 176.2816 | 212.2695 | 243.7236 | 279.8438 | 1.78%
3114 | 14-75.5 | -75.27 | 14.4583 | 978.7478 | 141.6382 | 175.8771 | 211.9045 | 243.3416 | 279.4481 | 1.757%
3115 | 14-75.5 | -75.5413 | 14.4583 | 996.8088 | 141.1675 | 175.4646 | 211.5272 | 242.9406 | 279.025 | 1.734%
3116 | 14-76 | -75.8126 | 14.4583 | 1014.8709 | 140.7491 | 175.0832 | 211.188 | 242.5865 | 278.6594 | 1.713%
3117 | 14-76 | -76.0839 | 14.4583 | 1032.934 | 140.3708 | 174.7227 | 210.8707 | 242.2563 | 278.3198 | 1.695%
3118 | 14-76.5 | -76.3553 | 14.4583 | 1050.998 | 140.0189 | 174.3727 | 210.5602 | 241.9286 | 277.9767 | 1.677%
3119 | 14-76.5 | -76.6266 | 14.4583 | 1069.0629 | 139.743 | 174.0753 | 210.3109 | 241.6761 | 277.7257 | 1.663%
3120 | 14-77 | -76.8979 | 14.4583 | 1087.1286 | 139.5278 | 173.8196 | 210.1017 | 241.4652 | 277.5172 | 1.652%
3121 | 14-77 | -77.1692 | 14.4583 | 1105.195 | 139.363 | 173.6023 | 209.921 | 241.2762 | 277.3213 | 1.644%
3122 | 14-77.5 | -77.4405 | 14.4583 | 1123.2621 | 139.2847 | 173.4547 | 209.8074 | 241.1611 | 277.2065 | 1.639%
3123 | 14-77.5 | -77.7119 | 14.4583 | 1141.3297 | 139.2728 | 173.3652 | 209.7455 | 241.1011 | 277.1501 | 1.637%
3124 | 14-78 | -77.9832 | 14.4583 | 1159.3979 | 139.3285 | 173.3394 | 209.7546 | 241.1301 | 277.2044 | 1.638%
3125 | 14-78.5 | -78.2545 | 14.4583 | 1177.4666 | 139.506 | 173.4258 | 209.9142 | 241.3649 | 277.5333 | 1.645%
3126 | 14-78.5 | -78.5258 | 14.4583 | 1195.5358 | 139.7436 | 173.5723 | 210.1576 | 241.7158 | 278.0187 | 1.655%
3127 | 14-79 | -78.7971 | 14.4583 | 1213.6053 | 140.0084 | 173.7497 | 210.4533 | 242.1431 | 278.6106 | 1.666%
3128 | 14-79 | -79.0685 | 14.4583 | 1231.6752 | 140.3296 | 173.9806 | 210.8374 | 242.6984 | 279.3805 | 1.68%
3129 | 14-79.5 | -79.3398 | 14.4583 | 1249.7454 | 140.6528 | 174.2261 | 211.2589 | 243.3133 | 280.2381 | 1.694%
3130 | 14-79.5 | -79.6111 | 14.4583 | 1267.8159 | 140.963 | 174.4771 | 211.7073 | 243.9742 | 281.1663 | 1.707%
3131 | 14-80 | -79.8824 | 14.4583 | 1285.8866 | 141.2897 | 174.7586 | 212.2155 | 244.7261 | 282.2249 | 1.722%
3132 | 14-80 | -80.1537 | 14.4583 | 1303.9574 | 141.5466 | 175.0001 | 212.6999 | 245.462 | 283.2787 | 1.734%
3133 | 14-80.5 | -80.4251 | 14.4583 | 1322.0285 | 141.7112 | 175.1821 | 213.1429 | 246.1648 | 284.3113 | 1.741%
3134 | 14-80.5 | -80.6964 | 14.4583 | 1340.0996 | 141.8045 | 175.3189 | 213.5692 | 246.872 | 285.3767 | 1.745%
3135 | 14-81 | -80.9677 | 14.4583 | 1358.1709 | 141.7556 | 175.3518 | 213.9101 | 247.495 | 286.3619 | 1.743%
3136 | 14-81 | -81.239 | 14.4583 | 1376.2422 | 141.5616 | 175.2778 | 214.1567 | 248.0199 | 287.2465 | 1.734%
3137 | 14-81.5 | -81.5104 | 14.4583 | 1394.3135 | 141.2425 | 175.1145 | 214.3248 | 248.4635 | 288.0492 | 1.72%
3138 | 14-82 | -81.7817 | 14.4583 | 1412.3848 | 140.4061 | 174.4566 | 213.9579 | 248.2329 | 288.0071 | 1.683%
3139 | 14-82 | -82.053 | 14.4583 | 1430.4561 | 139.0167 | 173.2044 | 212.9964 | 247.2546 | 287.0303 | 1.622%
3140 | 14-82.5 | -82.3243 | 14.4583 | 1448.5274 | 137.1458 | 171.3628 | 211.5019 | 245.6128 | 285.2317 | 1.542%
3141 | 14-82.5 | -82.5956 | 14.4583 | 1466.5985 | 135.0393 | 169.2457 | 209.75 | 243.6487 | 283.025 | 1.457%
3142 | 14-83 | -82.867 | 14.4583 | 1484.6696 | 132.799 | 166.9679 | 207.8432 | 241.4957 | 280.5784 | 1.372%
3143 | 14-83 | -83.1383 | 14.4583 | 1502.7405 | 130.46 | 164.5628 | 205.8097 | 239.1951 | 277.9473 | 1.289%
3144 | 14-83.5 | -83.4096 | 14.4583 | 1520.8112 | 127.8984 | 161.851 | 203.4508 | 236.4959 | 274.8018 | 1.203%
3145 | 14-83.5 | -83.6809 | 14.4583 | 1538.8818 | 125.1786 | 158.8871 | 200.7631 | 233.4755 | 271.2438 | 1.117%
3146 | 14-84 | -83.9522 | 14.4583 | 1556.9522 | 122.3521 | 155.7282 | 197.7806 | 230.1994 | 267.3611 | 1.033%
3147 | 14-84 | -84.2236 | 14.4583 | 1575.0223 | 119.4977 | 152.5246 | 194.7477 | 226.8307 | 263.3548 | 0.9546%
3148 | 14-84.5 | -84.4949 | 14.4583 | 1593.0922 | 116.6821 | 149.34 | 191.7583 | 223.4663 | 259.3469 | 0.8832%
3149 | 14-85 | -84.7662 | 14.4583 | 1611.1619 | 113.9284 | 146.2033 | 188.8558 | 220.1441 | 255.3842 | 0.8186%
3150 | 14-85 | -85.0375 | 14.4583 | 1629.2312 | 111.0593 | 142.8533 | 185.7133 | 216.4913 | 250.9559 | 0.7553%
3151 | 14-85.5 | -85.3089 | 14.4583 | 1647.3003 | 108.4672 | 139.7091 | 182.7934 | 213.1196 | 246.8465 | 0.7014%
3152 | 14-85.5 | -85.5802 | 14.4583 | 1665.369 | 106.264 | 136.947 | 180.2063 | 210.2135 | 243.2918 | 0.6579%
3153 | 14-86 | -85.8515 | 14.4583 | 1683.4373 | 104.868 | 135.292 | 178.619 | 208.4901 | 241.1943 | 0.6327%
3154 | 14-86 | -86.1228 | 14.4583 | 1701.5054 | 104.0766 | 134.3845 | 177.7603 | 207.6805 | 240.2419 | 0.6196%
3155 | 14-86.5 | -86.3941 | 14.4583 | 1719.573 | 103.811 | 134.0287 | 177.5583 | 207.6614 | 240.2904 | 0.616%
3156 | 14-86.5 | -86.6655 | 14.4583 | 1737.6403 | 103.2235 | 133.4513 | 177.0361 | 207.0763 | 239.5615 | 0.6072%
3157 | 14-87 | -86.9368 | 14.4583 | 1755.7071 | 102.5179 | 132.7273 | 176.4337 | 206.2643 | 238.5112 | 0.5963%
3158 | 14-87 | -87.2081 | 14.4583 | 1773.7735 | 101.815 | 131.9476 | 175.9145 | 205.3943 | 237.3615 | 0.5855%
3159 | 14-87.5 | -87.4794 | 14.4583 | 1791.8394 | 101.3055 | 131.4099 | 175.7 | 204.752 | 236.4591 | 0.578%
3160 | 14-88 | -87.7507 | 14.4583 | 1809.9049 | 100.9143 | 130.9707 | 175.5327 | 204.162 | 235.5915 | 0.5719%
3161 | 14-88 | -88.0221 | 14.4583 | 1827.97 | 100.6755 | 130.6902 | 175.4308 | 203.677 | 234.8321 | 0.5677%
3162 | 14-88.5 | -88.2934 | 14.4583 | 1846.0345 | 100.6674 | 130.6908 | 175.4746 | 203.4106 | 234.3192 | 0.5667%
3163 | 14-88.5 | -88.5647 | 14.4583 | 1864.0985 | 101.0889 | 131.2928 | 176.0141 | 203.7277 | 234.5149 | 0.573%
3164 | 14-89 | -88.836 | 14.4583 | 1882.162 | 101.9505 | 132.5276 | 177.0379 | 204.5907 | 235.36 | 0.5869%
3165 | 14-89 | -89.1074 | 14.4583 | 1900.2249 | 103.2315 | 134.3218 | 178.506 | 205.8928 | 236.7054 | 0.6083%
3166 | 14-89.5 | -89.3787 | 14.4583 | 1918.2873 | 104.5785 | 135.9531 | 179.7934 | 206.9748 | 237.7255 | 0.6293%
3167 | 14-89.5 | -89.65 | 14.4583 | 1936.3492 | 105.7847 | 137.2981 | 180.718 | 207.5524 | 238.0655 | 0.6466%
3168 | 14-90 | -89.9213 | 14.4583 | 1954.4104 | 106.9877 | 138.5625 | 181.3818 | 207.7906 | 237.9292 | 0.6627%
3169 | 14-90 | -90.1926 | 14.4583 | 1972.4711 | 109.0493 | 140.5627 | 182.824 | 209.1217 | 239.1887 | 0.6952%
3170 | 14-90.5 | -90.464 | 14.4583 | 1990.5311 | 111.8702 | 143.3807 | 184.9846 | 211.4282 | 241.675 | 0.7461%
3171 | 14-90.5 | -90.7353 | 14.4583 | 2008.5906 | 115.2646 | 146.8484 | 187.6904 | 214.4456 | 245.0415 | 0.8155%
3172 | 15-50 | -50.0371 | 14.7296 | 708.9206 | 138.0887 | 171.6917 | 206.4886 | 236.6981 | 271.3297 | 1.573%
3173 | 15-50.5 | -50.3084 | 14.7296 | 690.8673 | 138.0851 | 171.8066 | 206.7187 | 237.0654 | 271.8692 | 1.574%
3174 | 15-50.5 | -50.5797 | 14.7296 | 672.8159 | 138.0471 | 171.9053 | 206.9257 | 237.4023 | 272.3694 | 1.575%
3175 | 15-51 | -50.851 | 14.7296 | 654.7668 | 138.0064 | 172.011 | 207.1405 | 237.7483 | 272.8805 | 1.575%
3176 | 15-51 | -51.1224 | 14.7296 | 636.7201 | 137.9973 | 172.1495 | 207.3966 | 238.1476 | 273.4596 | 1.577%
3177 | 15-51.5 | -51.3937 | 14.7296 | 618.6761 | 137.9851 | 172.2876 | 207.6475 | 238.5368 | 274.0227 | 1.578%
3178 | 15-51.5 | -51.665 | 14.7296 | 600.635 | 137.9865 | 172.4339 | 207.9145 | 238.9511 | 274.6221 | 1.58%
3179 | 15-52 | -51.9363 | 14.7296 | 582.5972 | 138.0185 | 172.5983 | 208.218 | 239.4217 | 275.3033 | 1.584%
3180 | 15-52 | -52.2077 | 14.7296 | 564.563 | 138.0343 | 172.7345 | 208.4801 | 239.836 | 275.9096 | 1.586%
3181 | 15-52.5 | -52.479 | 14.7296 | 546.5327 | 138.0601 | 172.8604 | 208.7296 | 240.2352 | 276.4979 | 1.589%
3182 | 15-53 | -52.7503 | 14.7296 | 528.5069 | 138.114 | 172.9869 | 208.9863 | 240.6481 | 277.1083 | 1.592%
3183 | 15-53 | -53.0216 | 14.7296 | 510.486 | 138.1426 | 173.0658 | 209.1786 | 240.9738 | 277.6036 | 1.594%
3184 | 15-53.5 | -53.2929 | 14.7296 | 492.4706 | 138.1857 | 173.1284 | 209.3554 | 241.2819 | 278.0788 | 1.596%
3185 | 15-53.5 | -53.5643 | 14.7296 | 474.4613 | 138.2625 | 173.1898 | 209.5404 | 241.6053 | 278.5783 | 1.599%
3186 | 15-54 | -53.8356 | 14.7296 | 456.4588 | 138.3321 | 173.224 | 209.6892 | 241.8784 | 279.0103 | 1.602%
3187 | 15-54 | -54.1069 | 14.7296 | 438.4642 | 138.4298 | 173.2635 | 209.8423 | 242.1558 | 279.4463 | 1.605%
3188 | 15-54.5 | -54.3782 | 14.7296 | 420.4783 | 138.566 | 173.3174 | 210.012 | 242.4538 | 279.9081 | 1.61%
3189 | 15-54.5 | -54.6495 | 14.7296 | 402.5025 | 138.7019 | 173.3554 | 210.1443 | 242.6913 | 280.2802 | 1.614%
3190 | 15-55 | -54.9209 | 14.7296 | 384.5381 | 138.8759 | 173.4128 | 210.2887 | 242.9351 | 280.6506 | 1.62%
3191 | 15-55 | -55.1922 | 14.7296 | 366.5868 | 139.0953 | 173.4983 | 210.4516 | 243.19 | 281.022 | 1.628%
3192 | 15-55.5 | -55.4635 | 14.7296 | 348.6507 | 139.3088 | 173.5692 | 210.5401 | 243.3113 | 281.1841 | 1.636%
3193 | 15-55.5 | -55.7348 | 14.7296 | 330.7324 | 139.581 | 173.6886 | 210.6487 | 243.4288 | 281.3108 | 1.646%
3194 | 15-56 | -56.0061 | 14.7296 | 312.8348 | 139.936 | 173.8778 | 210.8069 | 243.5769 | 281.4421 | 1.66%
3195 | 15-56.5 | -56.2775 | 14.7296 | 294.9618 | 140.3308 | 174.1057 | 210.986 | 243.7272 | 281.5505 | 1.677%
3196 | 15-56.5 | -56.5488 | 14.7296 | 277.1181 | 140.8363 | 174.4271 | 211.269 | 243.9909 | 281.7825 | 1.698%
3197 | 15-57 | -56.8201 | 14.7296 | 259.31 | 141.4638 | 174.8487 | 211.6614 | 244.3715 | 282.1386 | 1.726%
3198 | 15-57 | -57.0914 | 14.7296 | 241.5452 | 142.1484 | 175.3194 | 212.0961 | 244.7851 | 282.5148 | 1.757%
3199 | 15-57.5 | -57.3628 | 14.7296 | 223.8341 | 142.9377 | 175.8653 | 212.6171 | 245.2942 | 282.9962 | 1.794%
3200 | 15-57.5 | -57.6341 | 14.7296 | 206.1905 | 143.8203 | 176.4755 | 213.2088 | 245.8777 | 283.555 | 1.837%
3201 | 15-58 | -57.9054 | 14.7296 | 188.6335 | 144.7359 | 177.1048 | 213.8106 | 246.4589 | 284.0952 | 1.882%
3202 | 15-58 | -58.1767 | 14.7296 | 171.1897 | 145.7264 | 177.784 | 214.4751 | 247.1141 | 284.7228 | 1.933%
3203 | 15-58.5 | -58.448 | 14.7296 | 153.8977 | 146.7658 | 178.4937 | 215.1771 | 247.8118 | 285.3981 | 1.987%
3204 | 15-58.5 | -58.7194 | 14.7296 | 136.815 | 147.7892 | 179.1878 | 215.8635 | 248.4906 | 286.0508 | 2.043%
3205 | 15-59 | -58.9907 | 14.7296 | 120.0311 | 148.8494 | 179.9107 | 216.6275 | 249.2926 | 286.8846 | 2.102%
3206 | 15-59.5 | -59.262 | 14.7296 | 103.6912 | 149.9332 | 180.6594 | 217.4665 | 250.2121 | 287.8897 | 2.165%
3207 | 15-59.5 | -59.5333 | 14.7296 | 88.0429 | 151.0226 | 181.4516 | 218.3956 | 251.2632 | 289.0782 | 2.229%
3208 | 15-60 | -59.8046 | 14.7296 | 73.5291 | 152.1547 | 182.323 | 219.4496 | 252.4803 | 290.4836 | 2.299%
3209 | 15-60 | -60.076 | 14.7296 | 60.9655 | 153.2333 | 183.1734 | 220.4927 | 253.6975 | 291.9037 | 2.368%
3210 | 15-60.5 | -60.3473 | 14.7296 | 51.7915 | 154.1217 | 183.8484 | 221.3233 | 254.6688 | 293.0392 | 2.425%
3211 | 15-60.5 | -60.6186 | 14.7296 | 47.9918 | 154.8833 | 184.4016 | 222.0127 | 255.4825 | 293.9989 | 2.474%
3212 | 15-61 | -60.8899 | 14.7296 | 50.7875 | 155.5253 | 184.8586 | 222.5931 | 256.1766 | 294.8279 | 2.516%
3213 | 15-61 | -61.1613 | 14.7296 | 59.2522 | 156.0746 | 185.2629 | 223.1188 | 256.8153 | 295.6018 | 2.553%
3214 | 15-61.5 | -61.4326 | 14.7296 | 71.3973 | 156.5899 | 185.6622 | 223.6549 | 257.4807 | 296.4233 | 2.587%
3215 | 15-61.5 | -61.7039 | 14.7296 | 85.6715 | 157.0316 | 186.0247 | 224.1537 | 258.1093 | 297.2097 | 2.617%
3216 | 15-62 | -61.9752 | 14.7296 | 101.1778 | 157.3861 | 186.3346 | 224.5858 | 258.658 | 297.9006 | 2.641%
3217 | 15-62 | -62.2465 | 14.7296 | 117.429 | 157.7164 | 186.6394 | 225.0128 | 259.2019 | 298.5873 | 2.664%
3218 | 15-62.5 | -62.5179 | 14.7296 | 134.1546 | 157.994 | 186.9153 | 225.3996 | 259.6949 | 299.2099 | 2.684%
3219 | 15-63 | -62.7892 | 14.7296 | 151.1973 | 158.1917 | 187.127 | 225.7013 | 260.0829 | 299.7039 | 2.698%
3220 | 15-63 | -63.0605 | 14.7296 | 168.4609 | 158.3045 | 187.244 | 225.8887 | 260.3394 | 300.0463 | 2.705%
3221 | 15-63.5 | -63.3318 | 14.7296 | 185.8838 | 158.3085 | 187.2402 | 225.9285 | 260.424 | 300.1885 | 2.704%
3222 | 15-63.5 | -63.6031 | 14.7296 | 203.425 | 158.2619 | 187.1921 | 225.9226 | 260.4628 | 300.2859 | 2.699%
3223 | 15-64 | -63.8745 | 14.7296 | 221.0563 | 158.2899 | 187.2511 | 226.0726 | 260.7048 | 300.6447 | 2.699%
3224 | 15-64 | -64.1458 | 14.7296 | 238.7578 | 158.3528 | 187.3716 | 226.303 | 261.0449 | 301.123 | 2.702%
3225 | 15-64.5 | -64.4171 | 14.7296 | 256.515 | 158.4133 | 187.5034 | 226.5428 | 261.392 | 301.6048 | 2.706%
3226 | 15-64.5 | -64.6884 | 14.7296 | 274.3169 | 158.4542 | 187.616 | 226.7564 | 261.7061 | 302.0455 | 2.708%
3227 | 15-65 | -64.9598 | 14.7296 | 292.1554 | 158.4483 | 187.6797 | 226.8941 | 261.9183 | 302.3518 | 2.707%
3228 | 15-65 | -65.2311 | 14.7296 | 310.0241 | 158.4149 | 187.7129 | 226.9857 | 262.0688 | 302.5774 | 2.704%
3229 | 15-65.5 | -65.5024 | 14.7296 | 327.9181 | 158.3851 | 187.7482 | 227.0847 | 262.2323 | 302.823 | 2.701%
3230 | 15-66 | -65.7737 | 14.7296 | 345.8334 | 158.3286 | 187.7589 | 227.1544 | 262.3625 | 303.0305 | 2.697%
3231 | 15-66 | -66.045 | 14.7296 | 363.7669 | 158.254 | 187.7574 | 227.218 | 262.4931 | 303.2476 | 2.691%
3232 | 15-66.5 | -66.3164 | 14.7296 | 381.7159 | 158.1774 | 187.7612 | 227.3054 | 262.6664 | 303.5314 | 2.684%
3233 | 15-66.5 | -66.5877 | 14.7296 | 399.6784 | 158.0491 | 187.7193 | 227.3344 | 262.7698 | 303.7316 | 2.674%
3234 | 15-67 | -66.859 | 14.7296 | 417.6526 | 157.8777 | 187.6391 | 227.3123 | 262.8097 | 303.8535 | 2.661%
3235 | 15-67 | -67.1303 | 14.7296 | 435.6369 | 157.6784 | 187.5353 | 227.2595 | 262.8126 | 303.9308 | 2.646%
3236 | 15-67.5 | -67.4016 | 14.7296 | 453.6303 | 157.4112 | 187.3636 | 227.0965 | 262.6637 | 303.8042 | 2.627%
3237 | 15-67.5 | -67.673 | 14.7296 | 471.6315 | 157.1051 | 187.1575 | 226.8786 | 262.4394 | 303.577 | 2.605%
3238 | 15-68 | -67.9443 | 14.7296 | 489.6398 | 156.7811 | 186.9394 | 226.6438 | 262.1937 | 303.3227 | 2.583%
3239 | 15-68 | -68.2156 | 14.7296 | 507.6543 | 156.4114 | 186.6855 | 226.3559 | 261.8781 | 302.9777 | 2.559%
3240 | 15-68.5 | -68.4869 | 14.7296 | 525.6744 | 156.0191 | 186.4214 | 226.0587 | 261.5544 | 302.6266 | 2.533%
3241 | 15-69 | -68.7583 | 14.7296 | 543.6995 | 155.6194 | 186.16 | 225.7741 | 261.2535 | 302.3115 | 2.506%
3242 | 15-69 | -69.0296 | 14.7296 | 561.7291 | 155.1745 | 185.8566 | 225.41 | 260.8356 | 301.832 | 2.478%
3243 | 15-69.5 | -69.3009 | 14.7296 | 579.7627 | 154.711 | 185.5345 | 224.9975 | 260.3394 | 301.2359 | 2.45%
3244 | 15-69.5 | -69.5722 | 14.7296 | 597.8 | 154.2431 | 185.2047 | 224.5517 | 259.7837 | 300.547 | 2.421%
3245 | 15-70 | -69.8435 | 14.7296 | 615.8405 | 153.7378 | 184.8315 | 224.0011 | 259.061 | 299.6122 | 2.392%
3246 | 15-70 | -70.1149 | 14.7296 | 633.8841 | 153.2475 | 184.4656 | 223.4291 | 258.2876 | 298.5885 | 2.364%
3247 | 15-70.5 | -70.3862 | 14.7296 | 651.9304 | 152.7882 | 184.1187 | 222.8579 | 257.4956 | 297.5212 | 2.339%
3248 | 15-70.5 | -70.6575 | 14.7296 | 669.9792 | 152.3195 | 183.7584 | 222.241 | 256.625 | 296.3334 | 2.314%
3249 | 15-71 | -70.9288 | 14.7296 | 688.0302 | 151.8843 | 183.428 | 221.659 | 255.794 | 295.1907 | 2.29%
3250 | 15-71 | -71.2001 | 14.7296 | 706.0832 | 151.4865 | 183.1293 | 221.1194 | 255.0158 | 294.1133 | 2.27%
3251 | 15-71.5 | -71.4715 | 14.7296 | 724.1382 | 151.0723 | 182.8197 | 220.5533 | 254.1954 | 292.9742 | 2.248%
3252 | 15-71.5 | -71.7428 | 14.7296 | 742.1948 | 150.6721 | 182.5215 | 219.9969 | 253.3827 | 291.8401 | 2.228%
3253 | 15-72 | -72.0141 | 14.7296 | 760.253 | 150.2844 | 182.2296 | 219.446 | 252.5736 | 290.7071 | 2.208%
3254 | 15-72.5 | -72.2854 | 14.7296 | 778.3127 | 149.8654 | 181.9103 | 218.8539 | 251.7078 | 289.4977 | 2.186%
3255 | 15-72.5 | -72.5568 | 14.7296 | 796.3736 | 149.4572 | 181.6078 | 218.3124 | 250.9249 | 288.4125 | 2.165%
3256 | 15-73 | -72.8281 | 14.7296 | 814.4357 | 149.0536 | 181.3136 | 217.8096 | 250.2104 | 287.4337 | 2.144%
3257 | 15-73 | -73.0994 | 14.7296 | 832.499 | 148.6144 | 180.9927 | 217.2915 | 249.4904 | 286.4628 | 2.121%
3258 | 15-73.5 | -73.3707 | 14.7296 | 850.5632 | 148.1783 | 180.6817 | 216.8314 | 248.8755 | 285.6571 | 2.097%
3259 | 15-73.5 | -73.642 | 14.7296 | 868.6282 | 147.736 | 180.3721 | 216.4143 | 248.3441 | 284.9869 | 2.073%
3260 | 15-74 | -73.9134 | 14.7296 | 886.6942 | 147.2654 | 180.044 | 216.0078 | 247.8497 | 284.3877 | 2.047%
3261 | 15-74 | -74.1847 | 14.7296 | 904.7608 | 146.8143 | 179.7313 | 215.6629 | 247.4584 | 283.9444 | 2.023%
3262 | 15-74.5 | -74.456 | 14.7296 | 922.8281 | 146.3646 | 179.4177 | 215.3464 | 247.1206 | 283.5864 | 1.998%
3263 | 15-74.5 | -74.7273 | 14.7296 | 940.896 | 145.878 | 179.0656 | 214.9891 | 246.7325 | 283.1666 | 1.972%
3264 | 15-75 | -74.9986 | 14.7296 | 958.9645 | 145.4164 | 178.7223 | 214.6648 | 246.3957 | 282.8212 | 1.947%
3265 | 15-75.5 | -75.27 | 14.7296 | 977.0335 | 144.9691 | 178.3802 | 214.3539 | 246.0807 | 282.508 | 1.923%
3266 | 15-75.5 | -75.5413 | 14.7296 | 995.1028 | 144.5209 | 178.0275 | 214.0276 | 245.743 | 282.163 | 1.899%
3267 | 15-76 | -75.8126 | 14.7296 | 1013.1726 | 144.1255 | 177.7036 | 213.7378 | 245.4491 | 281.8703 | 1.878%
3268 | 15-76 | -76.0839 | 14.7296 | 1031.2427 | 143.7698 | 177.399 | 213.4669 | 245.1736 | 281.5952 | 1.859%
3269 | 15-76.5 | -76.3553 | 14.7296 | 1049.3131 | 143.4398 | 177.1039 | 213.1981 | 244.8927 | 281.3046 | 1.841%
3270 | 15-76.5 | -76.6266 | 14.7296 | 1067.3837 | 143.1855 | 176.8582 | 212.987 | 244.6811 | 281.097 | 1.828%
3271 | 15-77 | -76.8979 | 14.7296 | 1085.4545 | 142.9915 | 176.6511 | 212.8128 | 244.5066 | 280.9259 | 1.817%
3272 | 15-77 | -77.1692 | 14.7296 | 1103.5255 | 142.8476 | 176.4781 | 212.6639 | 244.3507 | 280.764 | 1.809%
3273 | 15-77.5 | -77.4405 | 14.7296 | 1121.5966 | 142.7892 | 176.3678 | 212.5785 | 244.2647 | 280.679 | 1.805%
3274 | 15-77.5 | -77.7119 | 14.7296 | 1139.6679 | 142.7961 | 176.3088 | 212.54 | 244.2286 | 280.6464 | 1.804%
3275 | 15-78 | -77.9832 | 14.7296 | 1157.7392 | 142.8703 | 176.307 | 212.5683 | 244.2761 | 280.718 | 1.807%
3276 | 15-78.5 | -78.2545 | 14.7296 | 1175.8105 | 143.0675 | 176.4114 | 212.7451 | 244.5263 | 281.0596 | 1.815%
3277 | 15-78.5 | -78.5258 | 14.7296 | 1193.8818 | 143.3267 | 176.5726 | 213.0026 | 244.8876 | 281.5501 | 1.827%
3278 | 15-79 | -78.7971 | 14.7296 | 1211.9531 | 143.6175 | 176.7649 | 213.3112 | 245.3223 | 282.142 | 1.84%
3279 | 15-79 | -79.0685 | 14.7296 | 1230.0244 | 143.9688 | 177.013 | 213.7113 | 245.8875 | 282.9135 | 1.856%
3280 | 15-79.5 | -79.3398 | 14.7296 | 1248.0956 | 144.3272 | 177.2795 | 214.1509 | 246.5139 | 283.7734 | 1.873%
3281 | 15-79.5 | -79.6111 | 14.7296 | 1266.1666 | 144.678 | 177.5555 | 214.6204 | 247.1892 | 284.7067 | 1.89%
3282 | 15-80 | -79.8824 | 14.7296 | 1284.2376 | 145.0503 | 177.8644 | 215.154 | 247.9604 | 285.7761 | 1.908%
3283 | 15-80 | -80.1537 | 14.7296 | 1302.3084 | 145.3586 | 178.1388 | 215.6698 | 248.7242 | 286.8523 | 1.922%
3284 | 15-80.5 | -80.4251 | 14.7296 | 1320.379 | 145.5797 | 178.3606 | 216.1505 | 249.4639 | 287.9196 | 1.933%
3285 | 15-80.5 | -80.6964 | 14.7296 | 1338.4495 | 145.7331 | 178.5437 | 216.6206 | 250.2155 | 289.0291 | 1.94%
3286 | 15-81 | -80.9677 | 14.7296 | 1356.5197 | 145.749 | 178.6311 | 217.0102 | 250.8889 | 290.0654 | 1.939%
3287 | 15-81 | -81.239 | 14.7296 | 1374.5897 | 145.6239 | 178.62 | 217.3109 | 251.4708 | 291.0093 | 1.932%
3288 | 15-81.5 | -81.5104 | 14.7296 | 1392.6594 | 145.3761 | 178.5273 | 217.539 | 251.9793 | 291.8814 | 1.919%
3289 | 15-82 | -81.7817 | 14.7296 | 1410.7289 | 144.633 | 177.98 | 217.2637 | 251.8548 | 291.9621 | 1.881%
3290 | 15-82 | -82.053 | 14.7296 | 1428.7981 | 143.3608 | 176.8817 | 216.433 | 251.0349 | 291.1767 | 1.818%
3291 | 15-82.5 | -82.3243 | 14.7296 | 1446.8669 | 141.6229 | 175.2305 | 215.108 | 249.6041 | 289.6393 | 1.734%
3292 | 15-82.5 | -82.5956 | 14.7296 | 1464.9355 | 139.6486 | 173.3133 | 213.5424 | 247.8696 | 287.7211 | 1.643%
3293 | 15-83 | -82.867 | 14.7296 | 1483.0037 | 137.5346 | 171.238 | 211.8363 | 245.9585 | 285.5824 | 1.552%
3294 | 15-83 | -83.1383 | 14.7296 | 1501.0715 | 135.3156 | 169.0362 | 210.0166 | 243.9126 | 283.2791 | 1.463%
3295 | 15-83.5 | -83.4096 | 14.7296 | 1519.139 | 132.858 | 166.5177 | 207.8644 | 241.4604 | 280.4544 | 1.369%
3296 | 15-83.5 | -83.6809 | 14.7296 | 1537.2061 | 130.2269 | 163.7352 | 205.3722 | 238.6731 | 277.2 | 1.274%
3297 | 15-84 | -83.9522 | 14.7296 | 1555.2728 | 127.4741 | 160.7449 | 202.5729 | 235.6145 | 273.5997 | 1.181%
3298 | 15-84 | -84.2236 | 14.7296 | 1573.339 | 124.6808 | 157.7071 | 199.7301 | 232.4615 | 269.8742 | 1.094%
3299 | 15-84.5 | -84.4949 | 14.7296 | 1591.4049 | 121.9133 | 154.6845 | 196.9365 | 229.312 | 266.1476 | 1.015%
3300 | 15-85 | -84.7662 | 14.7296 | 1609.4702 | 119.1955 | 151.7044 | 194.2311 | 226.2015 | 262.4635 | 0.9423%
3301 | 15-85 | -85.0375 | 14.7296 | 1627.5351 | 116.3406 | 148.4928 | 191.2619 | 222.7287 | 258.2729 | 0.8709%
3302 | 15-85.5 | -85.3089 | 14.7296 | 1645.5996 | 113.721 | 145.4355 | 188.4631 | 219.4709 | 254.3164 | 0.8093%
3303 | 15-85.5 | -85.5802 | 14.7296 | 1663.6635 | 111.4463 | 142.7042 | 185.9408 | 216.608 | 250.8247 | 0.7587%
3304 | 15-86 | -85.8515 | 14.7296 | 1681.7269 | 109.9288 | 141.0145 | 184.3408 | 214.8374 | 248.6768 | 0.728%
3305 | 15-86 | -86.1228 | 14.7296 | 1699.7898 | 108.9848 | 140.0321 | 183.4112 | 213.9248 | 247.6051 | 0.7107%
3306 | 15-86.5 | -86.3941 | 14.7296 | 1717.8522 | 108.5347 | 139.563 | 183.0776 | 213.7495 | 247.4692 | 0.7036%
3307 | 15-86.5 | -86.6655 | 14.7296 | 1735.914 | 107.6932 | 138.7974 | 182.3343 | 212.9055 | 246.4288 | 0.6893%
3308 | 15-87 | -86.9368 | 14.7296 | 1753.9753 | 106.6749 | 137.79 | 181.436 | 211.7515 | 244.9675 | 0.6716%
3309 | 15-87 | -87.2081 | 14.7296 | 1772.036 | 105.6038 | 136.6413 | 180.5497 | 210.4658 | 243.3213 | 0.6531%
3310 | 15-87.5 | -87.4794 | 14.7296 | 1790.0961 | 104.698 | 135.6925 | 179.9389 | 209.3801 | 241.8985 | 0.6382%
3311 | 15-88 | -87.7507 | 14.7296 | 1808.1557 | 103.8811 | 134.7913 | 179.3282 | 208.306 | 240.4681 | 0.6245%
3312 | 15-88 | -88.0221 | 14.7296 | 1826.2146 | 103.1871 | 133.9986 | 178.7375 | 207.2969 | 239.1044 | 0.6124%
3313 | 15-88.5 | -88.2934 | 14.7296 | 1844.2729 | 102.6995 | 133.4454 | 178.2591 | 206.4797 | 237.963 | 0.6036%
3314 | 15-88.5 | -88.5647 | 14.7296 | 1862.3305 | 102.6258 | 133.4599 | 178.2656 | 206.243 | 237.5368 | 0.6023%
3315 | 15-89 | -88.836 | 14.7296 | 1880.3876 | 102.9662 | 134.0562 | 178.7396 | 206.539 | 237.7536 | 0.6084%
3316 | 15-89 | -89.1074 | 14.7296 | 1898.4439 | 103.6732 | 135.1492 | 179.6185 | 207.2323 | 238.4279 | 0.621%
3317 | 15-89.5 | -89.3787 | 14.7296 | 1916.4996 | 104.382 | 136.0502 | 180.295 | 207.6808 | 238.7569 | 0.6318%
3318 | 15-89.5 | -89.65 | 14.7296 | 1934.5546 | 104.927 | 136.6622 | 180.6193 | 207.6314 | 238.4174 | 0.6383%
3319 | 15-90 | -89.9213 | 14.7296 | 1952.6089 | 105.4277 | 137.1792 | 180.6812 | 207.2337 | 237.5957 | 0.6424%
3320 | 15-90 | -90.1926 | 14.7296 | 1970.6626 | 106.8204 | 138.459 | 181.5471 | 207.9726 | 238.2325 | 0.662%
3321 | 15-90.5 | -90.464 | 14.7296 | 1988.7155 | 109.0239 | 140.6414 | 183.198 | 209.764 | 240.1974 | 0.6984%
3322 | 15-90.5 | -90.7353 | 14.7296 | 2006.7677 | 111.8807 | 143.5916 | 185.5013 | 212.3904 | 243.196 | 0.7518%
3323 | 15-50 | -50.0371 | 15.0009 | 707.4486 | 140.3553 | 173.657 | 208.3628 | 238.7816 | 273.6436 | 1.677%
3324 | 15-50.5 | -50.3084 | 15.0009 | 689.3801 | 140.3697 | 173.7656 | 208.6025 | 239.1656 | 274.2086 | 1.679%
3325 | 15-50.5 | -50.5797 | 15.0009 | 671.3122 | 140.3478 | 173.8572 | 208.8167 | 239.5159 | 274.7302 | 1.68%
3326 | 15-51 | -50.851 | 15.0009 | 653.2449 | 140.3231 | 173.9556 | 209.0372 | 239.8735 | 275.2603 | 1.68%
3327 | 15-51 | -51.1224 | 15.0009 | 635.1784 | 140.3307 | 174.0864 | 209.2987 | 240.2838 | 275.8573 | 1.682%
3328 | 15-51.5 | -51.3937 | 15.0009 | 617.1128 | 140.3339 | 174.2164 | 209.552 | 240.6792 | 276.4313 | 1.684%
3329 | 15-51.5 | -51.665 | 15.0009 | 599.0481 | 140.3492 | 174.355 | 209.8193 | 241.0954 | 277.0349 | 1.686%
3330 | 15-52 | -51.9363 | 15.0009 | 580.9844 | 140.3942 | 174.5126 | 210.1223 | 241.5658 | 277.7159 | 1.69%
3331 | 15-52 | -52.2077 | 15.0009 | 562.922 | 140.419 | 174.6417 | 210.3815 | 241.9759 | 278.3166 | 1.692%
3332 | 15-52.5 | -52.479 | 15.0009 | 544.8609 | 140.4499 | 174.7588 | 210.6261 | 242.3683 | 278.8956 | 1.695%
3333 | 15-53 | -52.7503 | 15.0009 | 526.8013 | 140.5054 | 174.8747 | 210.8764 | 242.772 | 279.4933 | 1.698%
3334 | 15-53 | -53.0216 | 15.0009 | 508.7435 | 140.5321 | 174.9444 | 211.0621 | 243.0885 | 279.9761 | 1.7%
3335 | 15-53.5 | -53.2929 | 15.0009 | 490.6875 | 140.5721 | 175.001 | 211.2355 | 243.3915 | 280.4438 | 1.701%
3336 | 15-53.5 | -53.5643 | 15.0009 | 472.6338 | 140.6455 | 175.0601 | 211.4214 | 243.7149 | 280.9421 | 1.704%
3337 | 15-54 | -53.8356 | 15.0009 | 454.5825 | 140.7107 | 175.0952 | 211.5739 | 243.9913 | 281.3769 | 1.707%
3338 | 15-54 | -54.1069 | 15.0009 | 436.534 | 140.8028 | 175.1363 | 211.7321 | 244.2734 | 281.8168 | 1.71%
3339 | 15-54.5 | -54.3782 | 15.0009 | 418.4887 | 140.9323 | 175.192 | 211.9085 | 244.5773 | 282.2831 | 1.715%
3340 | 15-54.5 | -54.6495 | 15.0009 | 400.4471 | 141.0595 | 175.2322 | 212.0493 | 244.824 | 282.665 | 1.719%
3341 | 15-55 | -54.9209 | 15.0009 | 382.4097 | 141.2246 | 175.2924 | 212.2071 | 245.0851 | 283.0575 | 1.725%
3342 | 15-55 | -55.1922 | 15.0009 | 364.3771 | 141.4346 | 175.3803 | 212.3881 | 245.3653 | 283.4633 | 1.733%
3343 | 15-55.5 | -55.4635 | 15.0009 | 346.3502 | 141.6335 | 175.449 | 212.4922 | 245.5105 | 283.66 | 1.741%
3344 | 15-55.5 | -55.7348 | 15.0009 | 328.3299 | 141.8882 | 175.5608 | 212.6144 | 245.651 | 283.8215 | 1.751%
3345 | 15-56 | -56.0061 | 15.0009 | 310.3174 | 142.221 | 175.7337 | 212.7815 | 245.8179 | 283.9843 | 1.765%
3346 | 15-56.5 | -56.2775 | 15.0009 | 292.3141 | 142.5876 | 175.9363 | 212.9581 | 245.9715 | 284.1039 | 1.782%
3347 | 15-56.5 | -56.5488 | 15.0009 | 274.322 | 143.0583 | 176.2237 | 213.2254 | 246.2206 | 284.323 | 1.803%
3348 | 15-57 | -56.8201 | 15.0009 | 256.3434 | 143.6449 | 176.603 | 213.59 | 246.5703 | 284.645 | 1.831%
3349 | 15-57 | -57.0914 | 15.0009 | 238.3813 | 144.2882 | 177.0283 | 213.9928 | 246.9487 | 284.9821 | 1.862%
3350 | 15-57.5 | -57.3628 | 15.0009 | 220.4399 | 145.037 | 177.5276 | 214.4805 | 247.4211 | 285.4233 | 1.899%
3351 | 15-57.5 | -57.6341 | 15.0009 | 202.5247 | 145.882 | 178.0917 | 215.0394 | 247.9687 | 285.9433 | 1.942%
3352 | 15-58 | -57.9054 | 15.0009 | 184.6433 | 146.7676 | 178.6795 | 215.6125 | 248.5191 | 286.4507 | 1.988%
3353 | 15-58 | -58.1767 | 15.0009 | 166.8066 | 147.7369 | 179.3218 | 216.2517 | 249.146 | 287.0464 | 2.041%
3354 | 15-58.5 | -58.448 | 15.0009 | 149.0308 | 148.7644 | 179.9995 | 216.9314 | 249.8165 | 287.689 | 2.098%
3355 | 15-58.5 | -58.7194 | 15.0009 | 131.3406 | 149.7852 | 180.6671 | 217.5967 | 250.467 | 288.3043 | 2.156%
3356 | 15-59 | -58.9907 | 15.0009 | 113.7759 | 150.8535 | 181.3733 | 218.3473 | 251.2477 | 289.1067 | 2.219%
3357 | 15-59.5 | -59.262 | 15.0009 | 96.4054 | 151.9591 | 182.122 | 219.1878 | 252.1616 | 290.0969 | 2.286%
3358 | 15-59.5 | -59.5333 | 15.0009 | 79.3567 | 153.0934 | 182.9435 | 220.1484 | 253.2422 | 291.3116 | 2.358%
3359 | 15-60 | -59.8046 | 15.0009 | 62.8923 | 154.2946 | 183.8741 | 221.271 | 254.5359 | 292.8025 | 2.436%
3360 | 15-60 | -60.076 | 15.0009 | 47.6221 | 155.4565 | 184.7981 | 222.4024 | 255.8544 | 294.339 | 2.515%
3361 | 15-60.5 | -60.3473 | 15.0009 | 35.1388 | 156.4259 | 185.5401 | 223.3114 | 256.914 | 295.5739 | 2.581%
3362 | 15-60.5 | -60.6186 | 15.0009 | 29.2588 | 157.2596 | 186.149 | 224.0616 | 257.7922 | 296.6016 | 2.639%
3363 | 15-61 | -60.8899 | 15.0009 | 33.6434 | 157.9702 | 186.6576 | 224.6951 | 258.5396 | 297.4827 | 2.689%
3364 | 15-61 | -61.1613 | 15.0009 | 45.4109 | 158.5905 | 187.1176 | 225.2777 | 259.2351 | 298.3119 | 2.734%
3365 | 15-61.5 | -61.4326 | 15.0009 | 60.3894 | 159.1739 | 187.573 | 225.8706 | 259.9564 | 299.1869 | 2.776%
3366 | 15-61.5 | -61.7039 | 15.0009 | 76.7207 | 159.6786 | 187.9901 | 226.4247 | 260.6393 | 300.0252 | 2.813%
3367 | 15-62 | -61.9752 | 15.0009 | 93.7002 | 160.0894 | 188.3514 | 226.909 | 261.2397 | 300.7658 | 2.843%
3368 | 15-62 | -62.2465 | 15.0009 | 111.0307 | 160.4694 | 188.7048 | 227.3865 | 261.8348 | 301.5033 | 2.872%
3369 | 15-62.5 | -62.5179 | 15.0009 | 128.5705 | 160.7922 | 189.0249 | 227.8201 | 262.3758 | 302.1744 | 2.896%
3370 | 15-63 | -62.7892 | 15.0009 | 146.2442 | 161.0276 | 189.2713 | 228.1573 | 262.7993 | 302.7028 | 2.915%
3371 | 15-63 | -63.0605 | 15.0009 | 164.0085 | 161.1629 | 189.4049 | 228.3568 | 263.0628 | 303.0453 | 2.924%
3372 | 15-63.5 | -63.3318 | 15.0009 | 181.8368 | 161.173 | 189.3972 | 228.3806 | 263.1192 | 303.1437 | 2.924%
3373 | 15-63.5 | -63.6031 | 15.0009 | 199.712 | 161.1251 | 189.3358 | 228.3457 | 263.1132 | 303.1763 | 2.918%
3374 | 15-64 | -63.8745 | 15.0009 | 217.6225 | 161.1602 | 189.3929 | 228.4826 | 263.3305 | 303.4956 | 2.919%
3375 | 15-64 | -64.1458 | 15.0009 | 235.5602 | 161.2378 | 189.5213 | 228.7157 | 263.6676 | 303.9633 | 2.923%
3376 | 15-64.5 | -64.4171 | 15.0009 | 253.5193 | 161.3137 | 189.6628 | 228.9636 | 264.0208 | 304.4485 | 2.928%
3377 | 15-64.5 | -64.6884 | 15.0009 | 271.4955 | 161.3626 | 189.7769 | 229.1768 | 264.3327 | 304.8843 | 2.93%
3378 | 15-65 | -64.9598 | 15.0009 | 289.4857 | 161.3595 | 189.8351 | 229.3068 | 264.5348 | 305.1776 | 2.929%
3379 | 15-65 | -65.2311 | 15.0009 | 307.4874 | 161.326 | 189.8584 | 229.3851 | 264.6689 | 305.3828 | 2.926%
3380 | 15-65.5 | -65.5024 | 15.0009 | 325.4985 | 161.295 | 189.8821 | 229.4682 | 264.8125 | 305.6035 | 2.922%
3381 | 15-66 | -65.7737 | 15.0009 | 343.5177 | 161.2366 | 189.8789 | 229.518 | 264.9167 | 305.778 | 2.916%
3382 | 15-66 | -66.045 | 15.0009 | 361.5436 | 161.1604 | 189.863 | 229.5594 | 265.0175 | 305.9555 | 2.909%
3383 | 15-66.5 | -66.3164 | 15.0009 | 379.5754 | 161.0829 | 189.8538 | 229.6246 | 265.1595 | 306.1964 | 2.901%
3384 | 15-66.5 | -66.5877 | 15.0009 | 397.6121 | 160.9554 | 189.7993 | 229.6331 | 265.2343 | 306.3578 | 2.89%
3385 | 15-67 | -66.859 | 15.0009 | 415.6531 | 160.7876 | 189.7097 | 229.597 | 265.2559 | 306.4559 | 2.875%
3386 | 15-67 | -67.1303 | 15.0009 | 433.6978 | 160.5961 | 189.6009 | 229.54 | 265.2552 | 306.5304 | 2.859%
3387 | 15-67.5 | -67.4016 | 15.0009 | 451.7458 | 160.3404 | 189.4267 | 229.3788 | 265.1124 | 306.4156 | 2.839%
3388 | 15-67.5 | -67.673 | 15.0009 | 469.7967 | 160.0503 | 189.2214 | 229.1677 | 264.9011 | 306.2091 | 2.816%
3389 | 15-68 | -67.9443 | 15.0009 | 487.8501 | 159.7473 | 189.0081 | 228.9447 | 264.6741 | 305.9823 | 2.793%
3390 | 15-68 | -68.2156 | 15.0009 | 505.9057 | 159.3999 | 188.7584 | 228.6688 | 264.3785 | 305.6676 | 2.768%
3391 | 15-68.5 | -68.4869 | 15.0009 | 523.9633 | 159.0289 | 188.4962 | 228.3827 | 264.0752 | 305.3487 | 2.74%
3392 | 15-69 | -68.7583 | 15.0009 | 542.0226 | 158.6481 | 188.2343 | 228.1078 | 263.7946 | 305.0674 | 2.713%
3393 | 15-69 | -69.0296 | 15.0009 | 560.0834 | 158.2185 | 187.9249 | 227.7475 | 263.3908 | 304.6155 | 2.682%
3394 | 15-69.5 | -69.3009 | 15.0009 | 578.1457 | 157.7664 | 187.5921 | 227.3351 | 262.906 | 304.0459 | 2.651%
3395 | 15-69.5 | -69.5722 | 15.0009 | 596.2091 | 157.3056 | 187.2473 | 226.8868 | 262.3611 | 303.3851 | 2.621%
3396 | 15-70 | -69.8435 | 15.0009 | 614.2737 | 156.8003 | 186.8525 | 226.3278 | 261.6446 | 302.4757 | 2.588%
3397 | 15-70 | -70.1149 | 15.0009 | 632.3392 | 156.3017 | 186.4593 | 225.7407 | 260.8691 | 301.468 | 2.557%
3398 | 15-70.5 | -70.3862 | 15.0009 | 650.4056 | 155.8268 | 186.0802 | 225.1471 | 260.0659 | 300.4045 | 2.529%
3399 | 15-70.5 | -70.6575 | 15.0009 | 668.4727 | 155.338 | 185.6833 | 224.4991 | 259.1711 | 299.2024 | 2.5%
3400 | 15-71 | -70.9288 | 15.0009 | 686.5405 | 154.8791 | 185.3146 | 223.8816 | 258.3087 | 298.0346 | 2.473%
3401 | 15-71 | -71.2001 | 15.0009 | 704.6089 | 154.4554 | 184.977 | 223.3037 | 257.494 | 296.9241 | 2.449%
3402 | 15-71.5 | -71.4715 | 15.0009 | 722.6779 | 154.0146 | 184.6284 | 222.6973 | 256.6333 | 295.7457 | 2.424%
3403 | 15-71.5 | -71.7428 | 15.0009 | 740.7473 | 153.5913 | 184.2961 | 222.1041 | 255.7822 | 294.5721 | 2.401%
3404 | 15-72 | -72.0141 | 15.0009 | 758.8171 | 153.1846 | 183.9763 | 221.5205 | 254.9373 | 293.4 | 2.379%
3405 | 15-72.5 | -72.2854 | 15.0009 | 776.8872 | 152.7467 | 183.634 | 220.8964 | 254.034 | 292.1469 | 2.355%
3406 | 15-72.5 | -72.5568 | 15.0009 | 794.9576 | 152.3218 | 183.3157 | 220.328 | 253.2183 | 291.0218 | 2.332%
3407 | 15-73 | -72.8281 | 15.0009 | 813.0283 | 151.905 | 183.0132 | 219.8044 | 252.4767 | 290.0083 | 2.309%
3408 | 15-73 | -73.0994 | 15.0009 | 831.0992 | 151.457 | 182.6932 | 219.2723 | 251.7367 | 289.0098 | 2.284%
3409 | 15-73.5 | -73.3707 | 15.0009 | 849.1702 | 151.0203 | 182.3942 | 218.8084 | 251.1126 | 288.188 | 2.259%
3410 | 15-73.5 | -73.642 | 15.0009 | 867.2414 | 150.5865 | 182.1071 | 218.3971 | 250.5825 | 287.513 | 2.234%
3411 | 15-74 | -73.9134 | 15.0009 | 885.3126 | 150.1323 | 181.8127 | 218.0053 | 250.0991 | 286.9197 | 2.208%
3412 | 15-74 | -74.1847 | 15.0009 | 903.3839 | 149.7035 | 181.5433 | 217.6858 | 249.7329 | 286.5003 | 2.183%
3413 | 15-74.5 | -74.456 | 15.0009 | 921.4552 | 149.2812 | 181.2817 | 217.4049 | 249.4338 | 286.1844 | 2.159%
3414 | 15-74.5 | -74.7273 | 15.0009 | 939.5266 | 148.826 | 180.9897 | 217.092 | 249.0974 | 285.8248 | 2.133%
3415 | 15-75 | -74.9986 | 15.0009 | 957.5979 | 148.399 | 180.7133 | 216.8196 | 248.8232 | 285.5546 | 2.108%
3416 | 15-75.5 | -75.27 | 15.0009 | 975.6691 | 147.987 | 180.4417 | 216.5643 | 248.5759 | 285.3235 | 2.084%
3417 | 15-75.5 | -75.5413 | 15.0009 | 993.7403 | 147.5718 | 180.1584 | 216.2915 | 248.303 | 285.0567 | 2.061%
3418 | 15-76 | -75.8126 | 15.0009 | 1011.8113 | 147.2118 | 179.9033 | 216.0566 | 248.0755 | 284.8441 | 2.04%
3419 | 15-76 | -76.0839 | 15.0009 | 1029.8822 | 146.893 | 179.6669 | 215.8406 | 247.8659 | 284.6476 | 2.022%
3420 | 15-76.5 | -76.3553 | 15.0009 | 1047.953 | 146.6 | 179.4389 | 215.6243 | 247.6466 | 284.4295 | 2.006%
3421 | 15-76.5 | -76.6266 | 15.0009 | 1066.0236 | 146.382 | 179.2569 | 215.4625 | 247.4915 | 284.2865 | 1.993%
3422 | 15-77 | -76.8979 | 15.0009 | 1084.094 | 146.2233 | 179.109 | 215.3339 | 247.3686 | 284.1737 | 1.984%
3423 | 15-77 | -77.1692 | 15.0009 | 1102.1642 | 146.1131 | 178.9896 | 215.2266 | 247.2598 | 284.0651 | 1.977%
3424 | 15-77.5 | -77.4405 | 15.0009 | 1120.2341 | 146.0873 | 178.9251 | 215.1793 | 247.217 | 284.0292 | 1.975%
3425 | 15-77.5 | -77.7119 | 15.0009 | 1138.3038 | 146.1252 | 178.9043 | 215.1745 | 247.2191 | 284.0401 | 1.976%
3426 | 15-78 | -77.9832 | 15.0009 | 1156.3733 | 146.2283 | 178.9329 | 215.2314 | 247.2987 | 284.1476 | 1.98%
3427 | 15-78.5 | -78.2545 | 15.0009 | 1174.4425 | 146.452 | 179.0592 | 215.4323 | 247.5742 | 284.5155 | 1.991%
3428 | 15-78.5 | -78.5258 | 15.0009 | 1192.5114 | 146.7352 | 179.2371 | 215.7091 | 247.9533 | 285.0215 | 2.005%
3429 | 15-79 | -78.7971 | 15.0009 | 1210.5799 | 147.051 | 179.4454 | 216.0352 | 248.4019 | 285.6223 | 2.021%
3430 | 15-79 | -79.0685 | 15.0009 | 1228.6482 | 147.4305 | 179.7114 | 216.4555 | 248.9836 | 286.4046 | 2.04%
3431 | 15-79.5 | -79.3398 | 15.0009 | 1246.7161 | 147.821 | 179.999 | 216.9171 | 249.627 | 287.2747 | 2.06%
3432 | 15-79.5 | -79.6111 | 15.0009 | 1264.7837 | 148.2086 | 180.2996 | 217.4106 | 250.321 | 288.219 | 2.08%
3433 | 15-80 | -79.8824 | 15.0009 | 1282.8508 | 148.6218 | 180.6358 | 217.9721 | 251.1149 | 289.3035 | 2.101%
3434 | 15-80 | -80.1537 | 15.0009 | 1300.9177 | 148.9761 | 180.9428 | 218.52 | 251.907 | 290.402 | 2.119%
3435 | 15-80.5 | -80.4251 | 15.0009 | 1318.9841 | 149.2481 | 181.204 | 219.0375 | 252.6809 | 291.4993 | 2.133%
3436 | 15-80.5 | -80.6964 | 15.0009 | 1337.0501 | 149.4566 | 181.4334 | 219.5491 | 253.4722 | 292.645 | 2.143%
3437 | 15-81 | -80.9677 | 15.0009 | 1355.1157 | 149.5334 | 181.5771 | 219.986 | 254.192 | 293.7252 | 2.145%
3438 | 15-81 | -81.239 | 15.0009 | 1373.1808 | 149.4752 | 181.6328 | 220.341 | 254.8285 | 294.7226 | 2.14%
3439 | 15-81.5 | -81.5104 | 15.0009 | 1391.2455 | 149.2993 | 181.6167 | 220.6308 | 255.4009 | 295.6597 | 2.129%
3440 | 15-82 | -81.7817 | 15.0009 | 1409.3098 | 148.6548 | 181.1898 | 220.4496 | 255.3821 | 295.8589 | 2.091%
3441 | 15-82 | -82.053 | 15.0009 | 1427.3736 | 147.5112 | 180.259 | 219.7522 | 254.7195 | 295.2589 | 2.027%
3442 | 15-82.5 | -82.3243 | 15.0009 | 1445.4369 | 145.9263 | 178.8159 | 218.5992 | 253.498 | 293.9756 | 1.941%
3443 | 15-82.5 | -82.5956 | 15.0009 | 1463.4997 | 144.1093 | 177.1174 | 217.2155 | 251.9883 | 292.3343 | 1.847%
3444 | 15-83 | -82.867 | 15.0009 | 1481.562 | 142.1508 | 175.2638 | 215.6965 | 250.3118 | 290.4879 | 1.752%
3445 | 15-83 | -83.1383 | 15.0009 | 1499.6239 | 140.0836 | 173.2851 | 214.0735 | 248.5111 | 288.4936 | 1.657%
3446 | 15-83.5 | -83.4096 | 15.0009 | 1517.6851 | 137.7691 | 170.9895 | 212.1291 | 246.3096 | 285.9882 | 1.556%
3447 | 15-83.5 | -83.6809 | 15.0009 | 1535.7459 | 135.2711 | 168.4287 | 209.8544 | 243.7763 | 283.0586 | 1.454%
3448 | 15-84 | -83.9522 | 15.0009 | 1553.8061 | 132.6414 | 165.6575 | 207.2805 | 240.9744 | 279.7867 | 1.353%
3449 | 15-84 | -84.2236 | 15.0009 | 1571.8657 | 129.9535 | 162.8286 | 204.6583 | 238.0691 | 276.3795 | 1.257%
3450 | 15-84.5 | -84.4949 | 15.0009 | 1589.9248 | 127.2721 | 160.0012 | 202.0759 | 235.1549 | 272.9578 | 1.169%
3451 | 15-85 | -84.7662 | 15.0009 | 1607.9833 | 124.6215 | 157.201 | 199.5679 | 232.2639 | 269.5608 | 1.088%
3452 | 15-85 | -85.0375 | 15.0009 | 1626.0412 | 121.8095 | 154.1486 | 196.7699 | 228.9773 | 265.6157 | 1.008%
3453 | 15-85.5 | -85.3089 | 15.0009 | 1644.0985 | 119.1874 | 151.1953 | 194.0885 | 225.8392 | 261.8207 | 0.9375%
3454 | 15-85.5 | -85.5802 | 15.0009 | 1662.1552 | 116.8617 | 148.5074 | 191.6272 | 223.0256 | 258.4024 | 0.8786%
3455 | 15-86 | -85.8515 | 15.0009 | 1680.2113 | 115.2387 | 146.7955 | 190.0182 | 221.2215 | 256.2249 | 0.8414%
3456 | 15-86 | -86.1228 | 15.0009 | 1698.2667 | 114.1542 | 145.7536 | 189.0353 | 220.229 | 255.0675 | 0.8188%
3457 | 15-86.5 | -86.3941 | 15.0009 | 1716.3215 | 113.5285 | 145.1891 | 188.6019 | 219.9271 | 254.7899 | 0.8074%
3458 | 15-86.5 | -86.6655 | 15.0009 | 1734.3757 | 112.4261 | 144.2472 | 187.6578 | 218.8384 | 253.4613 | 0.7862%
3459 | 15-87 | -86.9368 | 15.0009 | 1752.4292 | 111.0694 | 142.9414 | 186.4525 | 217.3282 | 251.5754 | 0.7595%
3460 | 15-87 | -87.2081 | 15.0009 | 1770.482 | 109.5922 | 141.3879 | 185.1641 | 215.5874 | 249.3865 | 0.7307%
3461 | 15-87.5 | -87.4794 | 15.0009 | 1788.5342 | 108.2567 | 139.9962 | 184.1158 | 214.0183 | 247.3947 | 0.706%
3462 | 15-88 | -87.7507 | 15.0009 | 1806.5856 | 106.9946 | 138.6225 | 183.0457 | 212.4453 | 245.3841 | 0.6828%
3463 | 15-88 | -88.0221 | 15.0009 | 1824.6364 | 105.8378 | 137.3252 | 181.9739 | 210.9198 | 243.4258 | 0.6616%
3464 | 15-88.5 | -88.2934 | 15.0009 | 1842.6864 | 104.864 | 136.2278 | 180.9893 | 209.5612 | 241.6653 | 0.6438%
3465 | 15-88.5 | -88.5647 | 15.0009 | 1860.7357 | 104.2852 | 135.6585 | 180.4734 | 208.7708 | 240.6127 | 0.6339%
3466 | 15-89 | -88.836 | 15.0009 | 1878.7843 | 104.0917 | 135.6153 | 180.4031 | 208.4919 | 240.1852 | 0.6313%
3467 | 15-89 | -89.1074 | 15.0009 | 1896.8322 | 104.2102 | 135.9974 | 180.691 | 208.5602 | 240.1627 | 0.6343%
3468 | 15-89.5 | -89.3787 | 15.0009 | 1914.8793 | 104.266 | 136.1453 | 180.74 | 208.3451 | 239.7589 | 0.6346%
3469 | 15-89.5 | -89.65 | 15.0009 | 1932.9256 | 104.1334 | 135.9913 | 180.4249 | 207.6251 | 238.682 | 0.63%
3470 | 15-90 | -89.9213 | 15.0009 | 1950.9712 | 103.9212 | 135.7297 | 179.8339 | 206.5479 | 237.1173 | 0.6226%
3471 | 15-90 | -90.1926 | 15.0009 | 1969.016 | 104.6311 | 136.265 | 180.0877 | 206.669 | 237.0969 | 0.6303%
3472 | 15-90.5 | -90.464 | 15.0009 | 1987.06 | 106.2123 | 137.8018 | 181.2054 | 207.9311 | 238.5206 | 0.6541%
3473 | 15-90.5 | -90.7353 | 15.0009 | 2005.1032 | 108.5291 | 140.2298 | 183.0999 | 210.1565 | 241.1364 | 0.6939%
3474 | 15-50 | -50.0371 | 15.2722 | 706.4658 | 142.5975 | 175.5216 | 210.2592 | 240.9139 | 276.0403 | 1.787%
3475 | 15-50.5 | -50.3084 | 15.2722 | 688.3953 | 142.6354 | 175.632 | 210.5215 | 241.3335 | 276.6573 | 1.79%
3476 | 15-50.5 | -50.5797 | 15.2722 | 670.3246 | 142.6334 | 175.7222 | 210.7532 | 241.7133 | 277.2234 | 1.791%
3477 | 15-51 | -50.851 | 15.2722 | 652.2537 | 142.6258 | 175.8157 | 210.9868 | 242.0946 | 277.7906 | 1.791%
3478 | 15-51 | -51.1224 | 15.2722 | 634.1827 | 142.6491 | 175.9379 | 211.2575 | 242.5232 | 278.4178 | 1.793%
3479 | 15-51.5 | -51.3937 | 15.2722 | 616.1116 | 142.6647 | 176.0557 | 211.5126 | 242.9263 | 279.0068 | 1.795%
3480 | 15-51.5 | -51.665 | 15.2722 | 598.0404 | 142.6895 | 176.1796 | 211.7763 | 243.3412 | 279.6121 | 1.797%
3481 | 15-52 | -51.9363 | 15.2722 | 579.9691 | 142.7416 | 176.3209 | 212.0722 | 243.8039 | 280.285 | 1.801%
3482 | 15-52 | -52.2077 | 15.2722 | 561.8978 | 142.769 | 176.4327 | 212.321 | 244.2019 | 280.8712 | 1.803%
3483 | 15-52.5 | -52.479 | 15.2722 | 543.8265 | 142.7998 | 176.5323 | 212.5536 | 244.5792 | 281.4315 | 1.805%
3484 | 15-53 | -52.7503 | 15.2722 | 525.7552 | 142.8532 | 176.631 | 212.7912 | 244.9657 | 282.0065 | 1.808%
3485 | 15-53 | -53.0216 | 15.2722 | 507.6839 | 142.875 | 176.6859 | 212.9637 | 245.2642 | 282.4651 | 1.809%
3486 | 15-53.5 | -53.2929 | 15.2722 | 489.6127 | 142.909 | 176.7313 | 213.1274 | 245.5537 | 282.9147 | 1.81%
3487 | 15-53.5 | -53.5643 | 15.2722 | 471.5416 | 142.9758 | 176.7834 | 213.3086 | 245.87 | 283.403 | 1.813%
3488 | 15-54 | -53.8356 | 15.2722 | 453.4706 | 143.0346 | 176.8159 | 213.4593 | 246.1428 | 283.8315 | 1.814%
3489 | 15-54 | -54.1069 | 15.2722 | 435.3999 | 143.1218 | 176.8574 | 213.62 | 246.4259 | 284.2707 | 1.818%
3490 | 15-54.5 | -54.3782 | 15.2722 | 417.3294 | 143.2485 | 176.9167 | 213.8038 | 246.7367 | 284.743 | 1.822%
3491 | 15-54.5 | -54.6495 | 15.2722 | 399.2593 | 143.3733 | 176.964 | 213.9572 | 246.9977 | 285.1411 | 1.827%
3492 | 15-55 | -54.9209 | 15.2722 | 381.1896 | 143.5385 | 177.0347 | 214.1362 | 247.2862 | 285.5685 | 1.833%
3493 | 15-55 | -55.1922 | 15.2722 | 363.1203 | 143.7504 | 177.1355 | 214.3468 | 247.6067 | 286.0281 | 1.842%
3494 | 15-55.5 | -55.4635 | 15.2722 | 345.0517 | 143.9476 | 177.2145 | 214.4817 | 247.797 | 286.2877 | 1.85%
3495 | 15-55.5 | -55.7348 | 15.2722 | 326.9838 | 144.1973 | 177.3303 | 214.6344 | 247.9844 | 286.5172 | 1.861%
3496 | 15-56 | -56.0061 | 15.2722 | 308.9168 | 144.5194 | 177.5016 | 214.8274 | 248.1951 | 286.7468 | 1.876%
3497 | 15-56.5 | -56.2775 | 15.2722 | 290.851 | 144.8668 | 177.694 | 215.0152 | 248.3732 | 286.9079 | 1.892%
3498 | 15-56.5 | -56.5488 | 15.2722 | 272.7864 | 145.3097 | 177.9603 | 215.2781 | 248.6254 | 287.14 | 1.914%
3499 | 15-57 | -56.8201 | 15.2722 | 254.7236 | 145.8603 | 178.3085 | 215.6236 | 248.9587 | 287.4495 | 1.942%
3500 | 15-57 | -57.0914 | 15.2722 | 236.6628 | 146.4669 | 178.6994 | 216.001 | 249.3116 | 287.7618 | 1.973%
3501 | 15-57.5 | -57.3628 | 15.2722 | 218.6046 | 147.1786 | 179.162 | 216.46 | 249.7543 | 288.1725 | 2.01%
3502 | 15-57.5 | -57.6341 | 15.2722 | 200.5498 | 147.9872 | 179.6888 | 216.9883 | 250.2699 | 288.6592 | 2.054%
3503 | 15-58 | -57.9054 | 15.2722 | 182.4995 | 148.8406 | 180.241 | 217.5314 | 250.7884 | 289.1329 | 2.101%
3504 | 15-58 | -58.1767 | 15.2722 | 164.455 | 149.7841 | 180.8502 | 218.1415 | 251.3825 | 289.692 | 2.155%
3505 | 15-58.5 | -58.448 | 15.2722 | 146.4186 | 150.7892 | 181.4975 | 218.7919 | 252.0181 | 290.2928 | 2.214%
3506 | 15-58.5 | -58.7194 | 15.2722 | 128.3937 | 151.7913 | 182.1378 | 219.426 | 252.628 | 290.856 | 2.275%
3507 | 15-59 | -58.9907 | 15.2722 | 110.3861 | 152.849 | 182.8252 | 220.1497 | 253.3699 | 291.6047 | 2.34%
3508 | 15-59.5 | -59.262 | 15.2722 | 92.4059 | 153.9533 | 183.5662 | 220.9686 | 254.2479 | 292.5408 | 2.411%
3509 | 15-59.5 | -59.5333 | 15.2722 | 74.4729 | 155.0979 | 184.3891 | 221.9151 | 255.2983 | 293.7046 | 2.487%
3510 | 15-60 | -59.8046 | 15.2722 | 56.632 | 156.3232 | 185.3342 | 223.0414 | 256.5842 | 295.1725 | 2.572%
3511 | 15-60 | -60.076 | 15.2722 | 39.0098 | 157.522 | 186.2841 | 224.1915 | 257.9135 | 296.7087 | 2.658%
3512 | 15-60.5 | -60.3473 | 15.2722 | 22.1353 | 158.5382 | 187.0603 | 225.1286 | 258.994 | 297.9546 | 2.732%
3513 | 15-60.5 | -60.6186 | 15.2722 | 10.5736 | 159.4204 | 187.7055 | 225.9083 | 259.8936 | 298.9926 | 2.797%
3514 | 15-61 | -60.8899 | 15.2722 | 19.6787 | 160.1819 | 188.254 | 226.5744 | 260.6652 | 299.8863 | 2.855%
3515 | 15-61 | -61.1613 | 15.2722 | 36.2811 | 160.856 | 188.7582 | 227.1947 | 261.3904 | 300.734 | 2.906%
3516 | 15-61.5 | -61.4326 | 15.2722 | 53.8425 | 161.4915 | 189.2599 | 227.828 | 262.1448 | 301.6316 | 2.956%
3517 | 15-61.5 | -61.7039 | 15.2722 | 71.6611 | 162.0452 | 189.7243 | 228.4248 | 262.8646 | 302.4979 | 3%
3518 | 15-62 | -61.9752 | 15.2722 | 89.5837 | 162.504 | 190.1326 | 228.9541 | 263.5066 | 303.2746 | 3.037%
3519 | 15-62 | -62.2465 | 15.2722 | 107.5582 | 162.9306 | 190.5336 | 229.481 | 264.1514 | 304.0612 | 3.071%
3520 | 15-62.5 | -62.5179 | 15.2722 | 125.5623 | 163.2974 | 190.8987 | 229.9628 | 264.7427 | 304.7843 | 3.102%
3521 | 15-63 | -62.7892 | 15.2722 | 143.5849 | 163.573 | 191.1855 | 230.3435 | 265.2118 | 305.3598 | 3.125%
3522 | 15-63 | -63.0605 | 15.2722 | 161.6198 | 163.7446 | 191.3567 | 230.5836 | 265.518 | 305.7467 | 3.138%
3523 | 15-63.5 | -63.3318 | 15.2722 | 179.6632 | 163.7863 | 191.381 | 230.6406 | 265.6078 | 305.878 | 3.141%
3524 | 15-63.5 | -63.6031 | 15.2722 | 197.7127 | 163.7657 | 191.3463 | 230.6316 | 265.626 | 305.932 | 3.137%
3525 | 15-64 | -63.8745 | 15.2722 | 215.7669 | 163.8259 | 191.428 | 230.7925 | 265.866 | 306.2716 | 3.14%
3526 | 15-64 | -64.1458 | 15.2722 | 233.8246 | 163.9258 | 191.5773 | 231.047 | 266.2242 | 306.7594 | 3.146%
3527 | 15-64.5 | -64.4171 | 15.2722 | 251.885 | 164.0192 | 191.7336 | 231.3104 | 266.5933 | 307.2604 | 3.153%
3528 | 15-64.5 | -64.6884 | 15.2722 | 269.9476 | 164.0781 | 191.8544 | 231.5301 | 266.9111 | 307.7013 | 3.156%
3529 | 15-65 | -64.9598 | 15.2722 | 288.0118 | 164.0795 | 191.9115 | 231.6576 | 267.1091 | 307.9885 | 3.154%
3530 | 15-65 | -65.2311 | 15.2722 | 306.0775 | 164.0463 | 191.9278 | 231.7252 | 267.229 | 308.1751 | 3.15%
3531 | 15-65.5 | -65.5024 | 15.2722 | 324.1444 | 164.0125 | 191.94 | 231.7908 | 267.349 | 308.3647 | 3.146%
3532 | 15-66 | -65.7737 | 15.2722 | 342.2121 | 163.9478 | 191.9201 | 231.8143 | 267.4178 | 308.4922 | 3.139%
3533 | 15-66 | -66.045 | 15.2722 | 360.2806 | 163.8641 | 191.885 | 231.8258 | 267.478 | 308.6159 | 3.13%
3534 | 15-66.5 | -66.3164 | 15.2722 | 378.3498 | 163.7794 | 191.8576 | 231.8625 | 267.5815 | 308.8057 | 3.121%
3535 | 15-66.5 | -66.5877 | 15.2722 | 396.4194 | 163.6464 | 191.7861 | 231.8458 | 267.6229 | 308.9238 | 3.108%
3536 | 15-67 | -66.859 | 15.2722 | 414.4895 | 163.477 | 191.6834 | 231.7929 | 267.6241 | 308.9968 | 3.091%
3537 | 15-67 | -67.1303 | 15.2722 | 432.5599 | 163.2883 | 191.5678 | 231.7309 | 267.6205 | 309.0713 | 3.074%
3538 | 15-67.5 | -67.4016 | 15.2722 | 450.6306 | 163.0404 | 191.39 | 231.5715 | 267.485 | 308.971 | 3.052%
3539 | 15-67.5 | -67.673 | 15.2722 | 468.7015 | 162.7636 | 191.1858 | 231.3689 | 267.2898 | 308.7901 | 3.028%
3540 | 15-68 | -67.9443 | 15.2722 | 486.7726 | 162.4792 | 190.9786 | 231.1612 | 267.0874 | 308.5996 | 3.004%
3541 | 15-68 | -68.2156 | 15.2722 | 504.8438 | 162.1513 | 190.7336 | 230.8995 | 266.8156 | 308.3208 | 2.977%
3542 | 15-68.5 | -68.4869 | 15.2722 | 522.9151 | 161.7981 | 190.4738 | 230.6254 | 266.5342 | 308.0367 | 2.948%
3543 | 15-69 | -68.7583 | 15.2722 | 540.9864 | 161.4325 | 190.2114 | 230.3604 | 266.2741 | 307.7895 | 2.919%
3544 | 15-69 | -69.0296 | 15.2722 | 559.0577 | 161.0139 | 189.8954 | 230.0031 | 265.8835 | 307.3638 | 2.886%
3545 | 15-69.5 | -69.3009 | 15.2722 | 577.1291 | 160.5688 | 189.5515 | 229.5894 | 265.4078 | 306.817 | 2.853%
3546 | 15-69.5 | -69.5722 | 15.2722 | 595.2003 | 160.111 | 189.1914 | 229.1363 | 264.8693 | 306.1775 | 2.819%
3547 | 15-70 | -69.8435 | 15.2722 | 613.2715 | 159.6045 | 188.775 | 228.566 | 264.1526 | 305.2831 | 2.784%
3548 | 15-70 | -70.1149 | 15.2722 | 631.3427 | 159.0993 | 188.3541 | 227.96 | 263.3682 | 304.2798 | 2.749%
3549 | 15-70.5 | -70.3862 | 15.2722 | 649.4137 | 158.6107 | 187.9415 | 227.3396 | 262.546 | 303.2083 | 2.717%
3550 | 15-70.5 | -70.6575 | 15.2722 | 667.4846 | 158.1025 | 187.505 | 226.6536 | 261.6162 | 301.976 | 2.685%
3551 | 15-71 | -70.9288 | 15.2722 | 685.5553 | 157.6193 | 187.0935 | 225.9931 | 260.7118 | 300.7686 | 2.655%
3552 | 15-71 | -71.2001 | 15.2722 | 703.6259 | 157.1679 | 186.7113 | 225.3694 | 259.8512 | 299.6134 | 2.627%
3553 | 15-71.5 | -71.4715 | 15.2722 | 721.6963 | 156.6977 | 186.3171 | 224.7155 | 258.9423 | 298.3872 | 2.598%
3554 | 15-71.5 | -71.7428 | 15.2722 | 739.7665 | 156.2491 | 185.9447 | 224.0814 | 258.0506 | 297.1743 | 2.572%
3555 | 15-72 | -72.0141 | 15.2722 | 757.8365 | 155.8219 | 185.5906 | 223.4635 | 257.1724 | 295.9709 | 2.547%
3556 | 15-72.5 | -72.2854 | 15.2722 | 775.9063 | 155.3645 | 185.2168 | 222.8058 | 256.2344 | 294.6825 | 2.52%
3557 | 15-72.5 | -72.5568 | 15.2722 | 793.9759 | 154.9236 | 184.8732 | 222.2093 | 255.3884 | 293.525 | 2.495%
3558 | 15-73 | -72.8281 | 15.2722 | 812.0452 | 154.4955 | 184.5523 | 221.6639 | 254.6223 | 292.4838 | 2.47%
3559 | 15-73 | -73.0994 | 15.2722 | 830.1143 | 154.0433 | 184.2219 | 221.1189 | 253.867 | 291.4672 | 2.443%
3560 | 15-73.5 | -73.3707 | 15.2722 | 848.183 | 153.6102 | 183.9227 | 220.6536 | 253.2402 | 290.6412 | 2.417%
3561 | 15-73.5 | -73.642 | 15.2722 | 866.2516 | 153.1877 | 183.6449 | 220.2513 | 252.7188 | 289.9741 | 2.392%
3562 | 15-74 | -73.9134 | 15.2722 | 884.3198 | 152.7519 | 183.3672 | 219.8761 | 252.2518 | 289.3968 | 2.365%
3563 | 15-74 | -74.1847 | 15.2722 | 902.3877 | 152.3474 | 183.1244 | 219.5839 | 251.916 | 289.0113 | 2.34%
3564 | 15-74.5 | -74.456 | 15.2722 | 920.4553 | 151.9555 | 182.8987 | 219.3406 | 251.6611 | 288.7472 | 2.316%
3565 | 15-74.5 | -74.7273 | 15.2722 | 938.5226 | 151.5371 | 182.6534 | 219.0757 | 251.383 | 288.4582 | 2.29%
3566 | 15-75 | -74.9986 | 15.2722 | 956.5896 | 151.1521 | 182.4326 | 218.8604 | 251.1794 | 288.2749 | 2.266%
3567 | 15-75.5 | -75.27 | 15.2722 | 974.6562 | 150.7847 | 182.2221 | 218.6664 | 251.008 | 288.1375 | 2.244%
3568 | 15-75.5 | -75.5413 | 15.2722 | 992.7224 | 150.4138 | 182.0012 | 218.453 | 250.8075 | 287.9585 | 2.221%
3569 | 15-76 | -75.8126 | 15.2722 | 1010.7883 | 150.1024 | 181.8119 | 218.2816 | 250.6573 | 287.84 | 2.202%
3570 | 15-76 | -76.0839 | 15.2722 | 1028.8539 | 149.8343 | 181.6429 | 218.1307 | 250.5272 | 287.7403 | 2.186%
3571 | 15-76.5 | -76.3553 | 15.2722 | 1046.919 | 149.5916 | 181.4818 | 217.9775 | 250.3844 | 287.6146 | 2.172%
3572 | 15-76.5 | -76.6266 | 15.2722 | 1064.9838 | 149.4221 | 181.3639 | 217.8747 | 250.2997 | 287.5557 | 2.161%
3573 | 15-77 | -76.8979 | 15.2722 | 1083.0481 | 149.3089 | 181.2762 | 217.7997 | 250.24 | 287.5172 | 2.154%
3574 | 15-77 | -77.1692 | 15.2722 | 1101.1121 | 149.2412 | 181.2115 | 217.7398 | 250.1863 | 287.4729 | 2.15%
3575 | 15-77.5 | -77.4405 | 15.2722 | 1119.1756 | 149.2555 | 181.1969 | 217.7363 | 250.1945 | 287.4959 | 2.15%
3576 | 15-77.5 | -77.7119 | 15.2722 | 1137.2387 | 149.3296 | 181.2184 | 217.7711 | 250.2419 | 287.5587 | 2.153%
3577 | 15-78 | -77.9832 | 15.2722 | 1155.3014 | 149.4644 | 181.2815 | 217.8619 | 250.359 | 287.7077 | 2.16%
3578 | 15-78.5 | -78.2545 | 15.2722 | 1173.3636 | 149.7127 | 181.4313 | 218.0893 | 250.6615 | 288.1026 | 2.174%
3579 | 15-78.5 | -78.5258 | 15.2722 | 1191.4254 | 150.0162 | 181.6254 | 218.3854 | 251.0564 | 288.6193 | 2.19%
3580 | 15-79 | -78.7971 | 15.2722 | 1209.4867 | 150.3517 | 181.8475 | 218.7273 | 251.5147 | 289.2212 | 2.208%
3581 | 15-79 | -79.0685 | 15.2722 | 1227.5476 | 150.7524 | 182.1283 | 219.1663 | 252.1088 | 290.0075 | 2.23%
3582 | 15-79.5 | -79.3398 | 15.2722 | 1245.6079 | 151.1663 | 182.4324 | 219.6473 | 252.7647 | 290.8804 | 2.253%
3583 | 15-79.5 | -79.6111 | 15.2722 | 1263.6678 | 151.5809 | 182.753 | 220.1626 | 253.4731 | 291.8289 | 2.276%
3584 | 15-80 | -79.8824 | 15.2722 | 1281.7272 | 152.0258 | 183.1133 | 220.7509 | 254.2873 | 292.9243 | 2.301%
3585 | 15-80 | -80.1537 | 15.2722 | 1299.7861 | 152.4165 | 183.4503 | 221.3287 | 255.1031 | 294.0379 | 2.323%
3586 | 15-80.5 | -80.4251 | 15.2722 | 1317.8445 | 152.7298 | 183.7483 | 221.879 | 255.9043 | 295.1544 | 2.34%
3587 | 15-80.5 | -80.6964 | 15.2722 | 1335.9023 | 152.9841 | 184.0219 | 222.4279 | 256.7282 | 296.3254 | 2.353%
3588 | 15-81 | -80.9677 | 15.2722 | 1353.9596 | 153.1156 | 184.2216 | 222.9092 | 257.4888 | 297.4405 | 2.358%
3589 | 15-81 | -81.239 | 15.2722 | 1372.0164 | 153.1223 | 184.346 | 223.3175 | 258.1768 | 298.4859 | 2.355%
3590 | 15-81.5 | -81.5104 | 15.2722 | 1390.0726 | 153.0206 | 184.4105 | 223.6705 | 258.8134 | 299.4866 | 2.347%
3591 | 15-82 | -81.7817 | 15.2722 | 1408.1283 | 152.4821 | 184.1109 | 223.5856 | 258.9012 | 299.8036 | 2.312%
3592 | 15-82 | -82.053 | 15.2722 | 1426.1834 | 151.4777 | 183.3584 | 223.0244 | 258.3972 | 299.3885 | 2.249%
3593 | 15-82.5 | -82.3243 | 15.2722 | 1444.238 | 150.0602 | 182.1383 | 222.0469 | 257.3868 | 298.3586 | 2.163%
3594 | 15-82.5 | -82.5956 | 15.2722 | 1462.2919 | 148.4175 | 180.6753 | 220.8472 | 256.1012 | 296.9894 | 2.068%
3595 | 15-83 | -82.867 | 15.2722 | 1480.3453 | 146.6336 | 179.0618 | 219.5159 | 254.6558 | 295.4266 | 1.97%
3596 | 15-83 | -83.1383 | 15.2722 | 1498.398 | 144.7392 | 177.3261 | 218.0856 | 253.0952 | 293.7299 | 1.872%
3597 | 15-83.5 | -83.4096 | 15.2722 | 1516.4502 | 142.6024 | 175.2886 | 216.3572 | 251.1545 | 291.5508 | 1.767%
3598 | 15-83.5 | -83.6809 | 15.2722 | 1534.5018 | 140.2874 | 173.0007 | 214.3366 | 248.9068 | 288.9807 | 1.659%
3599 | 15-84 | -83.9522 | 15.2722 | 1552.5527 | 137.8431 | 170.5145 | 212.0518 | 246.4166 | 286.1027 | 1.552%
3600 | 15-84 | -84.2236 | 15.2722 | 1570.603 | 135.3166 | 167.9507 | 209.6976 | 243.8028 | 283.0655 | 1.449%
3601 | 15-84.5 | -84.4949 | 15.2722 | 1588.6526 | 132.7686 | 165.3616 | 207.3529 | 241.152 | 279.9803 | 1.353%
3602 | 15-85 | -84.7662 | 15.2722 | 1606.7016 | 130.224 | 162.7711 | 205.0476 | 238.4927 | 276.8824 | 1.264%
3603 | 15-85 | -85.0375 | 15.2722 | 1624.75 | 127.4895 | 159.9029 | 202.4194 | 235.399 | 273.1887 | 1.173%
3604 | 15-85.5 | -85.3089 | 15.2722 | 1642.7976 | 124.8946 | 157.0723 | 199.8486 | 232.3839 | 269.5589 | 1.093%
3605 | 15-85.5 | -85.5802 | 15.2722 | 1660.8446 | 122.5426 | 154.4402 | 197.4359 | 229.6203 | 266.2154 | 1.024%
3606 | 15-86 | -85.8515 | 15.2722 | 1678.891 | 120.8418 | 152.7264 | 195.8262 | 227.8004 | 264.0335 | 0.9791%
3607 | 15-86 | -86.1228 | 15.2722 | 1696.9366 | 119.6488 | 151.6546 | 194.8186 | 226.7631 | 262.8405 | 0.9506%
3608 | 15-86.5 | -86.3941 | 15.2722 | 1714.9815 | 118.8815 | 151.0309 | 194.3282 | 226.3829 | 262.4902 | 0.9343%
3609 | 15-86.5 | -86.6655 | 15.2722 | 1733.0257 | 117.5357 | 149.9409 | 193.2086 | 225.0762 | 260.9156 | 0.9045%
3610 | 15-87 | -86.9368 | 15.2722 | 1751.0692 | 115.8318 | 148.3295 | 191.6883 | 223.2001 | 258.6017 | 0.8661%
3611 | 15-87 | -87.2081 | 15.2722 | 1769.112 | 113.9157 | 146.3347 | 189.9494 | 220.9613 | 255.8246 | 0.8236%
3612 | 15-87.5 | -87.4794 | 15.2722 | 1787.154 | 112.1143 | 144.4621 | 188.401 | 218.857 | 253.2039 | 0.7858%
3613 | 15-88 | -87.7507 | 15.2722 | 1805.1953 | 110.387 | 142.6029 | 186.8405 | 216.762 | 250.5872 | 0.7507%
3614 | 15-88 | -88.0221 | 15.2722 | 1823.2358 | 108.7618 | 140.8113 | 185.2876 | 214.723 | 248.039 | 0.7185%
3615 | 15-88.5 | -88.2934 | 15.2722 | 1841.2756 | 107.2988 | 139.1852 | 183.8108 | 212.8296 | 245.665 | 0.6903%
3616 | 15-88.5 | -88.5647 | 15.2722 | 1859.3146 | 106.2112 | 138.0474 | 182.787 | 211.4877 | 243.9831 | 0.6707%
3617 | 15-89 | -88.836 | 15.2722 | 1877.3528 | 105.4822 | 137.3846 | 182.1887 | 210.634 | 242.9038 | 0.6586%
3618 | 15-89 | -89.1074 | 15.2722 | 1895.3902 | 105.0187 | 137.0668 | 181.9051 | 210.0786 | 242.1779 | 0.6517%
3619 | 15-89.5 | -89.3787 | 15.2722 | 1913.4268 | 104.4362 | 136.4578 | 181.3097 | 209.1826 | 241.0118 | 0.641%
3620 | 15-89.5 | -89.65 | 15.2722 | 1931.4626 | 103.6371 | 135.5176 | 180.309 | 207.7521 | 239.1386 | 0.6253%
3621 | 15-90 | -89.9213 | 15.2722 | 1949.4976 | 102.7337 | 134.4551 | 179.0159 | 205.9513 | 236.764 | 0.6069%
3622 | 15-90 | -90.1926 | 15.2722 | 1967.5318 | 102.7853 | 134.2345 | 178.6374 | 205.4378 | 236.0535 | 0.6039%
3623 | 15-90.5 | -90.464 | 15.2722 | 1985.5651 | 103.7571 | 135.1354 | 179.2231 | 206.174 | 236.9271 | 0.6171%
3624 | 15-90.5 | -90.7353 | 15.2722 | 2003.5976 | 105.5509 | 137.0593 | 180.7197 | 208.0077 | 239.1575 | 0.646%
3625 | 16-50 | -50.0371 | 15.5435 | 705.9744 | 144.577 | 177.0657 | 211.8693 | 242.6676 | 277.945 | 1.89%
3626 | 16-50.5 | -50.3084 | 15.5435 | 687.9149 | 144.6454 | 177.1844 | 212.1602 | 243.1295 | 278.6214 | 1.893%
3627 | 16-50.5 | -50.5797 | 15.5435 | 669.8553 | 144.6689 | 177.278 | 212.4156 | 243.5462 | 279.2408 | 1.895%
3628 | 16-51 | -50.851 | 15.5435 | 651.7955 | 144.6826 | 177.3699 | 212.6683 | 243.9595 | 279.8562 | 1.896%
3629 | 16-51 | -51.1224 | 15.5435 | 633.7354 | 144.7237 | 177.485 | 212.9538 | 244.4155 | 280.5266 | 1.898%
3630 | 16-51.5 | -51.3937 | 15.5435 | 615.6752 | 144.7525 | 177.5912 | 213.2175 | 244.8374 | 281.1477 | 1.9%
3631 | 16-51.5 | -51.665 | 15.5435 | 597.6149 | 144.7866 | 177.7001 | 213.4837 | 245.2622 | 281.7726 | 1.902%
3632 | 16-52 | -51.9363 | 15.5435 | 579.5544 | 144.8448 | 177.8241 | 213.7772 | 245.7272 | 282.4537 | 1.905%
3633 | 16-52 | -52.2077 | 15.5435 | 561.4938 | 144.8741 | 177.9171 | 214.0204 | 246.1227 | 283.0416 | 1.907%
3634 | 16-52.5 | -52.479 | 15.5435 | 543.4331 | 144.9046 | 177.9983 | 214.2457 | 246.4943 | 283.5983 | 1.908%
3635 | 16-53 | -52.7503 | 15.5435 | 525.3723 | 144.9566 | 178.0805 | 214.4752 | 246.8724 | 284.1647 | 1.911%
3636 | 16-53 | -53.0216 | 15.5435 | 507.3115 | 144.9745 | 178.1213 | 214.6397 | 247.1622 | 284.6139 | 1.911%
3637 | 16-53.5 | -53.2929 | 15.5435 | 489.2506 | 145.0026 | 178.1555 | 214.7978 | 247.4461 | 285.058 | 1.912%
3638 | 16-53.5 | -53.5643 | 15.5435 | 471.1897 | 145.0624 | 178.2 | 214.9763 | 247.7605 | 285.5453 | 1.914%
3639 | 16-54 | -53.8356 | 15.5435 | 453.1289 | 145.1136 | 178.2292 | 215.1268 | 248.0343 | 285.9765 | 1.915%
3640 | 16-54 | -54.1069 | 15.5435 | 435.0681 | 145.1945 | 178.2706 | 215.29 | 248.3209 | 286.4205 | 1.918%
3641 | 16-54.5 | -54.3782 | 15.5435 | 417.0074 | 145.3167 | 178.3337 | 215.4793 | 248.6381 | 286.9001 | 1.923%
3642 | 16-54.5 | -54.6495 | 15.5435 | 398.9468 | 145.4386 | 178.3888 | 215.6431 | 248.9119 | 287.314 | 1.928%
3643 | 16-55 | -54.9209 | 15.5435 | 380.8865 | 145.6036 | 178.4715 | 215.8401 | 249.2241 | 287.7722 | 1.934%
3644 | 16-55 | -55.1922 | 15.5435 | 362.8264 | 145.8175 | 178.5875 | 216.0755 | 249.5789 | 288.2779 | 1.944%
3645 | 16-55.5 | -55.4635 | 15.5435 | 344.7666 | 146.0143 | 178.681 | 216.2384 | 249.8107 | 288.5961 | 1.952%
3646 | 16-55.5 | -55.7348 | 15.5435 | 326.7072 | 146.2602 | 178.8083 | 216.4188 | 250.0423 | 288.8906 | 1.964%
3647 | 16-56 | -56.0061 | 15.5435 | 308.6483 | 146.5712 | 178.9847 | 216.635 | 250.2948 | 289.1858 | 1.979%
3648 | 16-56.5 | -56.2775 | 15.5435 | 290.5901 | 146.8988 | 179.1734 | 216.8349 | 250.5012 | 289.3961 | 1.995%
3649 | 16-56.5 | -56.5488 | 15.5435 | 272.5326 | 147.3133 | 179.4269 | 217.0969 | 250.765 | 289.6566 | 2.017%
3650 | 16-57 | -56.8201 | 15.5435 | 254.4762 | 147.8262 | 179.7529 | 217.4286 | 251.0938 | 289.974 | 2.044%
3651 | 16-57 | -57.0914 | 15.5435 | 236.421 | 148.3938 | 180.118 | 217.785 | 251.4315 | 290.2791 | 2.075%
3652 | 16-57.5 | -57.3628 | 15.5435 | 218.3675 | 149.0651 | 180.552 | 218.2174 | 251.8505 | 290.6705 | 2.112%
3653 | 16-57.5 | -57.6341 | 15.5435 | 200.316 | 149.8333 | 181.0486 | 218.7157 | 252.3369 | 291.1299 | 2.155%
3654 | 16-58 | -57.9054 | 15.5435 | 182.2672 | 150.6504 | 181.5718 | 219.2293 | 252.8262 | 291.5756 | 2.203%
3655 | 16-58 | -58.1767 | 15.5435 | 164.222 | 151.5627 | 182.1534 | 219.8096 | 253.3892 | 292.1023 | 2.258%
3656 | 16-58.5 | -58.448 | 15.5435 | 146.1819 | 152.5382 | 182.7748 | 220.43 | 253.9913 | 292.6659 | 2.318%
3657 | 16-58.5 | -58.7194 | 15.5435 | 128.149 | 153.5143 | 183.3909 | 221.0327 | 254.5631 | 293.183 | 2.38%
3658 | 16-59 | -58.9907 | 15.5435 | 110.1269 | 154.5533 | 184.0597 | 221.7274 | 255.2657 | 293.8794 | 2.448%
3659 | 16-59.5 | -59.262 | 15.5435 | 92.1219 | 155.6477 | 184.7896 | 222.5215 | 256.1053 | 294.7598 | 2.521%
3660 | 16-59.5 | -59.5333 | 15.5435 | 74.1465 | 156.7948 | 185.6104 | 223.4501 | 257.1215 | 295.8684 | 2.601%
3661 | 16-60 | -59.8046 | 15.5435 | 56.2292 | 158.0353 | 186.5644 | 224.5715 | 258.3881 | 297.2982 | 2.691%
3662 | 16-60 | -60.076 | 15.5435 | 38.4514 | 159.2619 | 187.5338 | 225.7284 | 259.7104 | 298.8094 | 2.783%
3663 | 16-60.5 | -60.3473 | 15.5435 | 21.1676 | 160.3167 | 188.3377 | 226.6801 | 260.7914 | 300.037 | 2.865%
3664 | 16-60.5 | -60.6186 | 15.5435 | 8.3897 | 161.2395 | 189.0131 | 227.477 | 261.6942 | 301.0594 | 2.937%
3665 | 16-61 | -60.8899 | 15.5435 | 18.587 | 162.0443 | 189.5947 | 228.1638 | 262.4728 | 301.9417 | 3.001%
3666 | 16-61 | -61.1613 | 15.5435 | 35.6838 | 162.7647 | 190.1362 | 228.8096 | 263.2106 | 302.7845 | 3.06%
3667 | 16-61.5 | -61.4326 | 15.5435 | 53.4225 | 163.4446 | 190.676 | 229.4692 | 263.978 | 303.6772 | 3.117%
3668 | 16-61.5 | -61.7039 | 15.5435 | 71.3257 | 164.0408 | 191.1801 | 230.0954 | 264.7153 | 304.5452 | 3.168%
3669 | 16-62 | -61.9752 | 15.5435 | 89.2945 | 164.5441 | 191.6301 | 230.6596 | 265.3842 | 305.3375 | 3.211%
3670 | 16-62 | -62.2465 | 15.5435 | 107.2959 | 165.0153 | 192.0749 | 231.2283 | 266.0676 | 306.1573 | 3.252%
3671 | 16-62.5 | -62.5179 | 15.5435 | 125.3159 | 165.4304 | 192.4903 | 231.7638 | 266.7148 | 306.9377 | 3.289%
3672 | 16-63 | -62.7892 | 15.5435 | 143.3473 | 165.7617 | 192.8382 | 232.215 | 267.2623 | 307.6005 | 3.319%
3673 | 16-63 | -63.0605 | 15.5435 | 161.3865 | 165.9968 | 193.0829 | 232.5439 | 267.6707 | 308.105 | 3.339%
3674 | 16-63.5 | -63.3318 | 15.5435 | 179.4309 | 166.0953 | 193.1733 | 232.6799 | 267.8509 | 308.3397 | 3.347%
3675 | 16-63.5 | -63.6031 | 15.5435 | 197.4792 | 166.1162 | 193.1855 | 232.7241 | 267.9275 | 308.4575 | 3.347%
3676 | 16-64 | -63.8745 | 15.5435 | 215.5303 | 166.2049 | 193.2979 | 232.9171 | 268.2 | 308.8293 | 3.353%
3677 | 16-64 | -64.1458 | 15.5435 | 233.5836 | 166.3277 | 193.4702 | 233.1951 | 268.5816 | 309.3398 | 3.362%
3678 | 16-64.5 | -64.4171 | 15.5435 | 251.6386 | 166.4404 | 193.6449 | 233.4784 | 268.9714 | 309.8619 | 3.37%
3679 | 16-64.5 | -64.6884 | 15.5435 | 269.6948 | 166.5123 | 193.7776 | 233.7111 | 269.3029 | 310.3168 | 3.375%
3680 | 16-65 | -64.9598 | 15.5435 | 287.7521 | 166.5218 | 193.8405 | 233.8453 | 269.5085 | 310.6124 | 3.373%
3681 | 16-65 | -65.2311 | 15.5435 | 305.8102 | 166.4914 | 193.8557 | 233.9111 | 269.6257 | 310.7954 | 3.369%
3682 | 16-65.5 | -65.5024 | 15.5435 | 323.869 | 166.4544 | 193.8601 | 233.9644 | 269.7289 | 310.9626 | 3.364%
3683 | 16-66 | -65.7737 | 15.5435 | 341.9283 | 166.3814 | 193.825 | 233.9648 | 269.7668 | 311.0496 | 3.356%
3684 | 16-66 | -66.045 | 15.5435 | 359.9881 | 166.2807 | 193.7633 | 233.9376 | 269.7766 | 311.1083 | 3.345%
3685 | 16-66.5 | -66.3164 | 15.5435 | 378.0481 | 166.1672 | 193.6945 | 233.9162 | 269.8058 | 311.2041 | 3.332%
3686 | 16-66.5 | -66.5877 | 15.5435 | 396.1085 | 165.9957 | 193.5672 | 233.8228 | 269.7506 | 311.2011 | 3.314%
3687 | 16-67 | -66.859 | 15.5435 | 414.169 | 165.7932 | 193.4145 | 233.7028 | 269.6687 | 311.1717 | 3.293%
3688 | 16-67 | -67.1303 | 15.5435 | 432.2297 | 165.5871 | 193.2682 | 233.6026 | 269.62 | 311.1928 | 3.272%
3689 | 16-67.5 | -67.4016 | 15.5435 | 450.2904 | 165.3384 | 193.0779 | 233.4314 | 269.4737 | 311.0831 | 3.248%
3690 | 16-67.5 | -67.673 | 15.5435 | 468.3513 | 165.07 | 192.8705 | 233.2303 | 269.2848 | 310.915 | 3.223%
3691 | 16-68 | -67.9443 | 15.5435 | 486.4122 | 164.7992 | 192.6649 | 233.0308 | 269.0972 | 310.7477 | 3.198%
3692 | 16-68 | -68.2156 | 15.5435 | 504.473 | 164.4856 | 192.4207 | 232.777 | 268.8406 | 310.4934 | 3.169%
3693 | 16-68.5 | -68.4869 | 15.5435 | 522.5339 | 164.1461 | 192.1601 | 232.5092 | 268.5727 | 310.2318 | 3.139%
3694 | 16-69 | -68.7583 | 15.5435 | 540.5947 | 163.7924 | 191.8953 | 232.2484 | 268.3235 | 310.0044 | 3.108%
3695 | 16-69 | -69.0296 | 15.5435 | 558.6554 | 163.3824 | 191.5716 | 231.8896 | 267.9379 | 309.5921 | 3.073%
3696 | 16-69.5 | -69.3009 | 15.5435 | 576.716 | 162.9424 | 191.2157 | 231.4693 | 267.4615 | 309.0525 | 3.037%
3697 | 16-69.5 | -69.5722 | 15.5435 | 594.7765 | 162.4857 | 190.8393 | 231.0045 | 266.9166 | 308.4138 | 3.001%
3698 | 16-70 | -69.8435 | 15.5435 | 612.8369 | 161.9769 | 190.402 | 230.419 | 266.1912 | 307.5194 | 2.963%
3699 | 16-70 | -70.1149 | 15.5435 | 630.8971 | 161.4645 | 189.9559 | 229.7939 | 265.3949 | 306.5143 | 2.925%
3700 | 16-70.5 | -70.3862 | 15.5435 | 648.9572 | 160.9628 | 189.5137 | 229.1504 | 264.5571 | 305.4376 | 2.89%
3701 | 16-70.5 | -70.6575 | 15.5435 | 667.017 | 160.435 | 189.0415 | 228.4318 | 263.5988 | 304.1832 | 2.853%
3702 | 16-71 | -70.9288 | 15.5435 | 685.0767 | 159.9254 | 188.5898 | 227.7319 | 262.6571 | 302.9421 | 2.819%
3703 | 16-71 | -71.2001 | 15.5435 | 703.1362 | 159.4423 | 188.1639 | 227.0638 | 261.7527 | 301.7451 | 2.787%
3704 | 16-71.5 | -71.4715 | 15.5435 | 721.1954 | 158.9392 | 187.7252 | 226.3657 | 260.8013 | 300.4797 | 2.754%
3705 | 16-71.5 | -71.7428 | 15.5435 | 739.2545 | 158.4616 | 187.3132 | 225.6946 | 259.8765 | 299.2396 | 2.724%
3706 | 16-72 | -72.0141 | 15.5435 | 757.3133 | 158.0103 | 186.9251 | 225.0468 | 258.9737 | 298.0194 | 2.696%
3707 | 16-72.5 | -72.2854 | 15.5435 | 775.3718 | 157.5306 | 186.5195 | 224.3605 | 258.0111 | 296.7123 | 2.666%
3708 | 16-72.5 | -72.5568 | 15.5435 | 793.43 | 157.0716 | 186.1504 | 223.7402 | 257.1439 | 295.5378 | 2.638%
3709 | 16-73 | -72.8281 | 15.5435 | 811.488 | 156.6314 | 185.8107 | 223.177 | 256.3615 | 294.483 | 2.611%
3710 | 16-73 | -73.0994 | 15.5435 | 829.5457 | 156.1744 | 185.4693 | 222.6227 | 255.599 | 293.4622 | 2.583%
3711 | 16-73.5 | -73.3707 | 15.5435 | 847.6031 | 155.744 | 185.1671 | 222.1547 | 254.9701 | 292.6347 | 2.556%
3712 | 16-73.5 | -73.642 | 15.5435 | 865.6602 | 155.3318 | 184.8939 | 221.7563 | 254.4515 | 291.9692 | 2.529%
3713 | 16-74 | -73.9134 | 15.5435 | 883.717 | 154.9131 | 184.6272 | 221.3907 | 253.9926 | 291.3974 | 2.503%
3714 | 16-74 | -74.1847 | 15.5435 | 901.7734 | 154.5337 | 184.4035 | 221.1196 | 253.6795 | 291.0363 | 2.478%
3715 | 16-74.5 | -74.456 | 15.5435 | 919.8295 | 154.1752 | 184.2051 | 220.9098 | 253.4637 | 290.8177 | 2.454%
3716 | 16-74.5 | -74.7273 | 15.5435 | 937.8853 | 153.8001 | 183.9964 | 220.6927 | 253.2437 | 290.5994 | 2.43%
3717 | 16-75 | -74.9986 | 15.5435 | 955.9407 | 153.465 | 183.8186 | 220.534 | 253.1096 | 290.501 | 2.407%
3718 | 16-75.5 | -75.27 | 15.5435 | 973.9958 | 153.1512 | 183.6549 | 220.4013 | 253.0131 | 290.4547 | 2.387%
3719 | 16-75.5 | -75.5413 | 15.5435 | 992.0504 | 152.8348 | 183.4826 | 220.2488 | 252.8855 | 290.3631 | 2.366%
3720 | 16-76 | -75.8126 | 15.5435 | 1010.1047 | 152.5829 | 183.3472 | 220.144 | 252.8158 | 290.3415 | 2.35%
3721 | 16-76 | -76.0839 | 15.5435 | 1028.1586 | 152.3767 | 183.2341 | 220.0626 | 252.7699 | 290.3436 | 2.336%
3722 | 16-76.5 | -76.3553 | 15.5435 | 1046.2121 | 152.1947 | 183.1268 | 219.9767 | 252.7085 | 290.3161 | 2.325%
3723 | 16-76.5 | -76.6266 | 15.5435 | 1064.2652 | 152.084 | 183.0591 | 219.937 | 252.699 | 290.3466 | 2.317%
3724 | 16-77 | -76.8979 | 15.5435 | 1082.3179 | 152.0266 | 183.0182 | 219.9203 | 252.708 | 290.3893 | 2.313%
3725 | 16-77 | -77.1692 | 15.5435 | 1100.3701 | 152.0103 | 182.9967 | 219.9134 | 252.7163 | 290.4174 | 2.311%
3726 | 16-77.5 | -77.4405 | 15.5435 | 1118.422 | 152.072 | 183.0224 | 219.9586 | 252.7804 | 290.5047 | 2.315%
3727 | 16-77.5 | -77.7119 | 15.5435 | 1136.4733 | 152.1894 | 183.0814 | 220.0368 | 252.8765 | 290.6219 | 2.321%
3728 | 16-78 | -77.9832 | 15.5435 | 1154.5242 | 152.3625 | 183.1782 | 220.1641 | 253.032 | 290.8109 | 2.331%
3729 | 16-78.5 | -78.2545 | 15.5435 | 1172.5747 | 152.6403 | 183.3563 | 220.4178 | 253.3577 | 291.2244 | 2.348%
3730 | 16-78.5 | -78.5258 | 15.5435 | 1190.6247 | 152.9672 | 183.5745 | 220.7312 | 253.7623 | 291.7403 | 2.367%
3731 | 16-79 | -78.7971 | 15.5435 | 1208.6742 | 153.3237 | 183.8191 | 221.0861 | 254.2233 | 292.3311 | 2.388%
3732 | 16-79 | -79.0685 | 15.5435 | 1226.7232 | 153.7453 | 184.1229 | 221.5397 | 254.8216 | 293.1076 | 2.413%
3733 | 16-79.5 | -79.3398 | 15.5435 | 1244.7718 | 154.1807 | 184.45 | 222.0358 | 255.4818 | 293.9702 | 2.44%
3734 | 16-79.5 | -79.6111 | 15.5435 | 1262.8198 | 154.6199 | 184.796 | 222.5696 | 256.1985 | 294.9131 | 2.466%
3735 | 16-80 | -79.8824 | 15.5435 | 1280.8673 | 155.0944 | 185.188 | 223.1843 | 257.0307 | 296.0151 | 2.495%
3736 | 16-80 | -80.1537 | 15.5435 | 1298.9143 | 155.5199 | 185.562 | 223.7945 | 257.8728 | 297.146 | 2.521%
3737 | 16-80.5 | -80.4251 | 15.5435 | 1316.9608 | 155.8739 | 185.9009 | 224.3828 | 258.7077 | 298.2895 | 2.541%
3738 | 16-80.5 | -80.6964 | 15.5435 | 1335.0068 | 156.1751 | 186.2199 | 224.9752 | 259.5723 | 299.4963 | 2.558%
3739 | 16-81 | -80.9677 | 15.5435 | 1353.0521 | 156.3641 | 186.4756 | 225.5086 | 260.3842 | 300.6604 | 2.567%
3740 | 16-81 | -81.239 | 15.5435 | 1371.097 | 156.4388 | 186.6674 | 225.9792 | 261.1366 | 301.7711 | 2.569%
3741 | 16-81.5 | -81.5104 | 15.5435 | 1389.1413 | 156.4141 | 186.8089 | 226.4043 | 261.8506 | 302.8545 | 2.563%
3742 | 16-82 | -81.7817 | 15.5435 | 1407.185 | 155.9871 | 186.6337 | 226.427 | 262.0616 | 303.3123 | 2.533%
3743 | 16-82 | -82.053 | 15.5435 | 1425.2281 | 155.1312 | 186.0602 | 226.0145 | 261.7338 | 303.1059 | 2.474%
3744 | 16-82.5 | -82.3243 | 15.5435 | 1443.2706 | 153.8943 | 185.0689 | 225.2259 | 260.9517 | 302.3513 | 2.391%
3745 | 16-82.5 | -82.5956 | 15.5435 | 1461.3126 | 152.4419 | 183.8494 | 224.2242 | 259.9076 | 301.2761 | 2.298%
3746 | 16-83 | -82.867 | 15.5435 | 1479.3539 | 150.8506 | 182.4864 | 223.0944 | 258.7101 | 300.0173 | 2.2%
3747 | 16-83 | -83.1383 | 15.5435 | 1497.3947 | 149.1492 | 181.0073 | 221.8701 | 257.4049 | 298.636 | 2.101%
3748 | 16-83.5 | -83.4096 | 15.5435 | 1515.4348 | 147.2224 | 179.2585 | 220.3755 | 255.7547 | 296.8183 | 1.994%
3749 | 16-83.5 | -83.6809 | 15.5435 | 1533.4743 | 145.1335 | 177.2931 | 218.6526 | 253.8372 | 294.6602 | 1.885%
3750 | 16-84 | -83.9522 | 15.5435 | 1551.5131 | 142.9281 | 175.1591 | 216.7221 | 251.717 | 292.2446 | 1.775%
3751 | 16-84 | -84.2236 | 15.5435 | 1569.5513 | 140.6158 | 172.9176 | 214.6795 | 249.4345 | 289.622 | 1.668%
3752 | 16-84.5 | -84.4949 | 15.5435 | 1587.5888 | 138.2449 | 170.6091 | 212.5907 | 247.0657 | 286.8906 | 1.565%
3753 | 16-85 | -84.7662 | 15.5435 | 1605.6257 | 135.8395 | 168.2558 | 210.4809 | 244.6362 | 284.0825 | 1.468%
3754 | 16-85 | -85.0375 | 15.5435 | 1623.6619 | 133.2143 | 165.5975 | 208.0139 | 241.7365 | 280.6367 | 1.368%
3755 | 16-85.5 | -85.3089 | 15.5435 | 1641.6974 | 130.674 | 162.9099 | 205.5411 | 238.8471 | 277.1725 | 1.276%
3756 | 16-85.5 | -85.5802 | 15.5435 | 1659.7323 | 128.3183 | 160.3477 | 203.1613 | 236.1359 | 273.9065 | 1.196%
3757 | 16-86 | -85.8515 | 15.5435 | 1677.7664 | 126.5674 | 158.6569 | 201.5606 | 234.3241 | 271.7539 | 1.142%
3758 | 16-86 | -86.1228 | 15.5435 | 1695.7998 | 125.2992 | 157.5907 | 200.5592 | 233.2834 | 270.5836 | 1.107%
3759 | 16-86.5 | -86.3941 | 15.5435 | 1713.8325 | 124.4286 | 156.9511 | 200.0583 | 232.8784 | 270.2372 | 1.086%
3760 | 16-86.5 | -86.6655 | 15.5435 | 1731.8645 | 122.8801 | 155.758 | 198.8091 | 231.4126 | 268.5001 | 1.046%
3761 | 16-87 | -86.9368 | 15.5435 | 1749.8958 | 120.8616 | 153.8889 | 197.0133 | 229.2178 | 265.8263 | 0.9937%
3762 | 16-87 | -87.2081 | 15.5435 | 1767.9263 | 118.5295 | 151.4846 | 194.8366 | 226.5114 | 262.506 | 0.9343%
3763 | 16-87.5 | -87.4794 | 15.5435 | 1785.9561 | 116.2648 | 149.1336 | 192.7657 | 223.8679 | 259.2562 | 0.8802%
3764 | 16-88 | -87.7507 | 15.5435 | 1803.9851 | 114.067 | 146.7907 | 190.7026 | 221.2477 | 256.0311 | 0.8303%
3765 | 16-88 | -88.0221 | 15.5435 | 1822.0133 | 111.9696 | 144.5102 | 188.6721 | 218.6976 | 252.8951 | 0.7848%
3766 | 16-88.5 | -88.2934 | 15.5435 | 1840.0407 | 110.022 | 142.3736 | 186.73 | 216.2865 | 249.9262 | 0.7446%
3767 | 16-88.5 | -88.5647 | 15.5435 | 1858.0674 | 108.4298 | 140.6848 | 185.225 | 214.4042 | 247.6233 | 0.714%
3768 | 16-89 | -88.836 | 15.5435 | 1876.0933 | 107.1731 | 139.4258 | 184.1304 | 212.9865 | 245.8966 | 0.6915%
3769 | 16-89 | -89.1074 | 15.5435 | 1894.1183 | 106.1483 | 138.4507 | 183.3219 | 211.8325 | 244.4877 | 0.6742%
3770 | 16-89.5 | -89.3787 | 15.5435 | 1912.1426 | 104.9561 | 137.1183 | 182.1269 | 210.2732 | 242.5647 | 0.6526%
3771 | 16-89.5 | -89.65 | 15.5435 | 1930.166 | 103.5177 | 135.4161 | 180.4675 | 208.1362 | 239.8794 | 0.6259%
3772 | 16-90 | -89.9213 | 15.5435 | 1948.1886 | 101.9492 | 133.567 | 178.4822 | 205.6028 | 236.6598 | 0.5969%
3773 | 16-90 | -90.1926 | 15.5435 | 1966.2103 | 101.3727 | 132.6007 | 177.4792 | 204.4393 | 235.2152 | 0.5842%
3774 | 16-90.5 | -90.464 | 15.5435 | 1984.2312 | 101.7544 | 132.8509 | 177.5326 | 204.6222 | 235.4809 | 0.5881%
3775 | 16-90.5 | -90.7353 | 15.5435 | 2002.2513 | 103.0114 | 134.2423 | 178.6108 | 206.0184 | 237.249 | 0.6077%
3776 | 16-50 | -50.0371 | 15.8149 | 705.9753 | 146.3771 | 178.3562 | 213.3027 | 244.2216 | 279.6242 | 1.987%
3777 | 16-50.5 | -50.3084 | 15.8149 | 687.9402 | 146.4853 | 178.4965 | 213.6267 | 244.7277 | 280.3584 | 1.992%
3778 | 16-50.5 | -50.5797 | 15.8149 | 669.9055 | 146.543 | 178.6073 | 213.9108 | 245.1843 | 281.0315 | 1.995%
3779 | 16-51 | -50.851 | 15.8149 | 651.8713 | 146.5857 | 178.7122 | 214.1884 | 245.6341 | 281.698 | 1.997%
3780 | 16-51 | -51.1224 | 15.8149 | 633.8378 | 146.6515 | 178.8362 | 214.4958 | 246.1244 | 282.4183 | 2%
3781 | 16-51.5 | -51.3937 | 15.8149 | 615.8049 | 146.6993 | 178.9465 | 214.7764 | 246.5752 | 283.0834 | 2.002%
3782 | 16-51.5 | -51.665 | 15.8149 | 597.7728 | 146.7487 | 179.0562 | 215.0552 | 247.0232 | 283.7446 | 2.005%
3783 | 16-52 | -51.9363 | 15.8149 | 579.7415 | 146.8194 | 179.1791 | 215.3582 | 247.5064 | 284.4551 | 2.008%
3784 | 16-52 | -52.2077 | 15.8149 | 561.7113 | 146.8571 | 179.2692 | 215.6072 | 247.915 | 285.0655 | 2.01%
3785 | 16-52.5 | -52.479 | 15.8149 | 543.6821 | 146.8937 | 179.3474 | 215.8362 | 248.2958 | 285.6384 | 2.011%
3786 | 16-53 | -52.7503 | 15.8149 | 525.6542 | 146.9502 | 179.4276 | 216.0678 | 248.6796 | 286.2151 | 2.014%
3787 | 16-53 | -53.0216 | 15.8149 | 507.6278 | 146.9693 | 179.4669 | 216.234 | 248.9744 | 286.6735 | 2.014%
3788 | 16-53.5 | -53.2929 | 15.8149 | 489.6029 | 146.996 | 179.5003 | 216.3946 | 249.2641 | 287.1277 | 2.014%
3789 | 16-53.5 | -53.5643 | 15.8149 | 471.5799 | 147.0524 | 179.545 | 216.5767 | 249.5854 | 287.6262 | 2.016%
3790 | 16-54 | -53.8356 | 15.8149 | 453.559 | 147.0977 | 179.5748 | 216.7309 | 249.8662 | 288.0685 | 2.017%
3791 | 16-54 | -54.1069 | 15.8149 | 435.5404 | 147.1723 | 179.6179 | 216.8983 | 250.1597 | 288.5226 | 2.019%
3792 | 16-54.5 | -54.3782 | 15.8149 | 417.5245 | 147.2892 | 179.6844 | 217.0931 | 250.4843 | 289.0121 | 2.024%
3793 | 16-54.5 | -54.6495 | 15.8149 | 399.5117 | 147.4074 | 179.7455 | 217.2655 | 250.7693 | 289.4402 | 2.029%
3794 | 16-55 | -54.9209 | 15.8149 | 381.5026 | 147.5717 | 179.8376 | 217.4769 | 251.1005 | 289.9234 | 2.036%
3795 | 16-55 | -55.1922 | 15.8149 | 363.4975 | 147.7874 | 179.9663 | 217.7325 | 251.4831 | 290.4662 | 2.046%
3796 | 16-55.5 | -55.4635 | 15.8149 | 345.4973 | 147.9854 | 180.0725 | 217.9195 | 251.7504 | 290.8341 | 2.055%
3797 | 16-55.5 | -55.7348 | 15.8149 | 327.5027 | 148.2308 | 180.2114 | 218.1265 | 252.0238 | 291.1896 | 2.067%
3798 | 16-56 | -56.0061 | 15.8149 | 309.5148 | 148.5358 | 180.3948 | 218.3681 | 252.3204 | 291.5529 | 2.082%
3799 | 16-56.5 | -56.2775 | 15.8149 | 291.5348 | 148.8506 | 180.584 | 218.5866 | 252.564 | 291.8245 | 2.099%
3800 | 16-56.5 | -56.5488 | 15.8149 | 273.5643 | 149.245 | 180.8309 | 218.8583 | 252.8546 | 292.1338 | 2.12%
3801 | 16-57 | -56.8201 | 15.8149 | 255.6053 | 149.7291 | 181.1419 | 219.1895 | 253.1982 | 292.4861 | 2.147%
3802 | 16-57 | -57.0914 | 15.8149 | 237.6606 | 150.2643 | 181.487 | 219.5367 | 253.5382 | 292.8088 | 2.178%
3803 | 16-57.5 | -57.3628 | 15.8149 | 219.7336 | 150.9007 | 181.8976 | 219.953 | 253.9493 | 293.2036 | 2.215%
3804 | 16-57.5 | -57.6341 | 15.8149 | 201.8291 | 151.6331 | 182.3685 | 220.4304 | 254.4204 | 293.6554 | 2.258%
3805 | 16-58 | -57.9054 | 15.8149 | 183.9537 | 152.4171 | 182.8663 | 220.9216 | 254.8912 | 294.0881 | 2.306%
3806 | 16-58 | -58.1767 | 15.8149 | 166.1168 | 153.2955 | 183.4227 | 221.4775 | 255.4312 | 294.5942 | 2.361%
3807 | 16-58.5 | -58.448 | 15.8149 | 148.3323 | 154.2369 | 184.0191 | 222.0712 | 256.0056 | 295.1294 | 2.422%
3808 | 16-58.5 | -58.7194 | 15.8149 | 130.6216 | 155.1807 | 184.6109 | 222.6444 | 256.5431 | 295.6066 | 2.485%
3809 | 16-59 | -58.9907 | 15.8149 | 113.0197 | 156.1924 | 185.2592 | 223.309 | 257.2062 | 296.2522 | 2.554%
3810 | 16-59.5 | -59.262 | 15.8149 | 95.5864 | 157.2664 | 185.974 | 224.0748 | 258.0044 | 297.0743 | 2.63%
3811 | 16-59.5 | -59.5333 | 15.8149 | 78.4346 | 158.4034 | 186.7874 | 224.9799 | 258.9807 | 298.1222 | 2.713%
3812 | 16-60 | -59.8046 | 15.8149 | 61.7988 | 159.6451 | 187.7435 | 226.088 | 260.2181 | 299.5023 | 2.807%
3813 | 16-60 | -60.076 | 15.8149 | 46.2396 | 160.8837 | 188.7238 | 227.2402 | 261.5194 | 300.9713 | 2.904%
3814 | 16-60.5 | -60.3473 | 15.8149 | 33.3019 | 161.9606 | 189.5454 | 228.1927 | 262.5833 | 302.1583 | 2.991%
3815 | 16-60.5 | -60.6186 | 15.8149 | 27.0525 | 162.9088 | 190.2419 | 228.9946 | 263.474 | 303.1461 | 3.07%
3816 | 16-61 | -60.8899 | 15.8149 | 31.7264 | 163.7425 | 190.8483 | 229.6905 | 264.2449 | 303.9988 | 3.14%
3817 | 16-61 | -61.1613 | 15.8149 | 43.9681 | 164.4953 | 191.4178 | 230.3492 | 264.9793 | 304.8167 | 3.206%
3818 | 16-61.5 | -61.4326 | 15.8149 | 59.2599 | 165.2061 | 191.9866 | 231.0224 | 265.7438 | 305.6847 | 3.269%
3819 | 16-61.5 | -61.7039 | 15.8149 | 75.7771 | 165.8357 | 192.5213 | 231.6654 | 266.4832 | 306.5347 | 3.326%
3820 | 16-62 | -61.9752 | 15.8149 | 92.8682 | 166.3757 | 193.0049 | 232.2534 | 267.1647 | 307.3247 | 3.376%
3821 | 16-62 | -62.2465 | 15.8149 | 110.2667 | 166.8839 | 193.4863 | 232.8536 | 267.8735 | 308.1612 | 3.424%
3822 | 16-62.5 | -62.5179 | 15.8149 | 127.847 | 167.3474 | 193.9542 | 233.4461 | 268.5807 | 309.0044 | 3.467%
3823 | 16-63 | -62.7892 | 15.8149 | 145.5433 | 167.7478 | 194.3829 | 233.9956 | 269.2422 | 309.7993 | 3.505%
3824 | 16-63 | -63.0605 | 15.8149 | 163.3179 | 168.0729 | 194.7382 | 234.465 | 269.819 | 310.5054 | 3.536%
3825 | 16-63.5 | -63.3318 | 15.8149 | 181.1476 | 168.2527 | 194.9293 | 234.7288 | 270.1519 | 310.9225 | 3.552%
3826 | 16-63.5 | -63.6031 | 15.8149 | 199.0177 | 168.3277 | 195.0072 | 234.853 | 270.3215 | 311.1481 | 3.558%
3827 | 16-64 | -63.8745 | 15.8149 | 216.9181 | 168.4459 | 195.1543 | 235.0847 | 270.6355 | 311.5644 | 3.567%
3828 | 16-64 | -64.1458 | 15.8149 | 234.8419 | 168.5894 | 195.3491 | 235.3864 | 271.0415 | 312.0993 | 3.578%
3829 | 16-64.5 | -64.4171 | 15.8149 | 252.7841 | 168.7208 | 195.5436 | 235.6922 | 271.4558 | 312.648 | 3.588%
3830 | 16-64.5 | -64.6884 | 15.8149 | 270.741 | 168.8073 | 195.6923 | 235.9446 | 271.8102 | 313.1296 | 3.594%
3831 | 16-65 | -64.9598 | 15.8149 | 288.7098 | 168.8275 | 195.7666 | 236.0949 | 272.0363 | 313.4509 | 3.593%
3832 | 16-65 | -65.2311 | 15.8149 | 306.6885 | 168.8028 | 195.7871 | 236.1694 | 272.1654 | 313.6496 | 3.589%
3833 | 16-65.5 | -65.5024 | 15.8149 | 324.6752 | 168.7653 | 195.7898 | 236.2206 | 272.2662 | 313.814 | 3.583%
3834 | 16-66 | -65.7737 | 15.8149 | 342.6689 | 168.6865 | 195.7456 | 236.2086 | 272.2886 | 313.8814 | 3.573%
3835 | 16-66 | -66.045 | 15.8149 | 360.6683 | 168.5641 | 195.6543 | 236.1411 | 272.248 | 313.8777 | 3.56%
3836 | 16-66.5 | -66.3164 | 15.8149 | 378.6726 | 168.4038 | 195.5238 | 236.0367 | 272.1738 | 313.8454 | 3.541%
3837 | 16-66.5 | -66.5877 | 15.8149 | 396.6812 | 168.1616 | 195.3018 | 235.8148 | 271.9581 | 313.6429 | 3.515%
3838 | 16-67 | -66.859 | 15.8149 | 414.6934 | 167.8947 | 195.0608 | 235.5759 | 271.7281 | 313.4299 | 3.487%
3839 | 16-67 | -67.1303 | 15.8149 | 432.7088 | 167.651 | 194.8601 | 235.4043 | 271.5921 | 313.3446 | 3.461%
3840 | 16-67.5 | -67.4016 | 15.8149 | 450.727 | 167.3926 | 194.6481 | 235.2084 | 271.4185 | 313.2049 | 3.434%
3841 | 16-67.5 | -67.673 | 15.8149 | 468.7476 | 167.1271 | 194.433 | 235.0029 | 271.2289 | 313.0408 | 3.407%
3842 | 16-68 | -67.9443 | 15.8149 | 486.7703 | 166.8632 | 194.2237 | 234.8051 | 271.0488 | 312.8885 | 3.38%
3843 | 16-68 | -68.2156 | 15.8149 | 504.7949 | 166.557 | 193.9747 | 234.5524 | 270.7993 | 312.6493 | 3.35%
3844 | 16-68.5 | -68.4869 | 15.8149 | 522.8211 | 166.2244 | 193.7085 | 234.2848 | 270.5377 | 312.4021 | 3.318%
3845 | 16-69 | -68.7583 | 15.8149 | 540.8488 | 165.877 | 193.4373 | 234.0236 | 270.2945 | 312.1887 | 3.285%
3846 | 16-69 | -69.0296 | 15.8149 | 558.8777 | 165.471 | 193.1032 | 233.6595 | 269.909 | 311.7841 | 3.248%
3847 | 16-69.5 | -69.3009 | 15.8149 | 576.9078 | 165.0323 | 192.7328 | 233.2285 | 269.4261 | 311.2436 | 3.209%
3848 | 16-69.5 | -69.5722 | 15.8149 | 594.9389 | 164.5738 | 192.3383 | 232.7472 | 268.8671 | 310.5942 | 3.171%
3849 | 16-70 | -69.8435 | 15.8149 | 612.9709 | 164.0606 | 191.8793 | 232.1433 | 268.1272 | 309.6911 | 3.129%
3850 | 16-70 | -70.1149 | 15.8149 | 631.0037 | 163.5399 | 191.4092 | 231.5003 | 267.32 | 308.6844 | 3.088%
3851 | 16-70.5 | -70.3862 | 15.8149 | 649.0372 | 163.0258 | 190.9411 | 230.8395 | 266.4746 | 307.6135 | 3.049%
3852 | 16-70.5 | -70.6575 | 15.8149 | 667.0712 | 162.4813 | 190.4371 | 230.0949 | 265.4973 | 306.3496 | 3.01%
3853 | 16-71 | -70.9288 | 15.8149 | 685.1058 | 161.9478 | 189.9485 | 229.3606 | 264.5247 | 305.0832 | 2.971%
3854 | 16-71 | -71.2001 | 15.8149 | 703.1409 | 161.435 | 189.4814 | 228.6506 | 263.5789 | 303.8464 | 2.935%
3855 | 16-71.5 | -71.4715 | 15.8149 | 721.1763 | 160.9005 | 189.0001 | 227.9083 | 262.5828 | 302.5366 | 2.898%
3856 | 16-71.5 | -71.7428 | 15.8149 | 739.2121 | 160.3947 | 188.5491 | 227.1975 | 261.6186 | 301.2586 | 2.864%
3857 | 16-72 | -72.0141 | 15.8149 | 757.2482 | 159.9194 | 188.126 | 226.5148 | 260.6819 | 300.0068 | 2.832%
3858 | 16-72.5 | -72.2854 | 15.8149 | 775.2845 | 159.4174 | 187.6871 | 225.7937 | 259.6839 | 298.6645 | 2.8%
3859 | 16-72.5 | -72.5568 | 15.8149 | 793.321 | 158.94 | 187.2898 | 225.1431 | 258.7853 | 297.4576 | 2.769%
3860 | 16-73 | -72.8281 | 15.8149 | 811.3576 | 158.4866 | 186.9279 | 224.5557 | 257.9773 | 296.3758 | 2.74%
3861 | 16-73 | -73.0994 | 15.8149 | 829.3944 | 158.0224 | 186.5708 | 223.9846 | 257.1974 | 295.3372 | 2.71%
3862 | 16-73.5 | -73.3707 | 15.8149 | 847.4312 | 157.591 | 186.2586 | 223.5027 | 256.5508 | 294.4876 | 2.681%
3863 | 16-73.5 | -73.642 | 15.8149 | 865.4681 | 157.1849 | 185.9811 | 223.0935 | 256.0149 | 293.7964 | 2.654%
3864 | 16-74 | -73.9134 | 15.8149 | 883.505 | 156.7791 | 185.7158 | 222.7214 | 255.5412 | 293.1993 | 2.627%
3865 | 16-74 | -74.1847 | 15.8149 | 901.5418 | 156.4196 | 185.5026 | 222.4576 | 255.2319 | 292.8371 | 2.603%
3866 | 16-74.5 | -74.456 | 15.8149 | 919.5787 | 156.0915 | 185.3244 | 222.2702 | 255.0401 | 292.6443 | 2.58%
3867 | 16-74.5 | -74.7273 | 15.8149 | 937.6154 | 155.7588 | 185.1465 | 222.0922 | 254.8672 | 292.4821 | 2.557%
3868 | 16-75 | -74.9986 | 15.8149 | 955.6521 | 155.4741 | 185.0071 | 221.9845 | 254.7956 | 292.4603 | 2.537%
3869 | 16-75.5 | -75.27 | 15.8149 | 973.6886 | 155.2162 | 184.8872 | 221.9104 | 254.7716 | 292.5034 | 2.519%
3870 | 16-75.5 | -75.5413 | 15.8149 | 991.7249 | 154.9576 | 184.761 | 221.8192 | 254.7197 | 292.5049 | 2.501%
3871 | 16-76 | -75.8126 | 15.8149 | 1009.7612 | 154.7693 | 184.6767 | 221.7839 | 254.7369 | 292.5912 | 2.487%
3872 | 16-76 | -76.0839 | 15.8149 | 1027.7972 | 154.6299 | 184.6174 | 221.776 | 254.7832 | 292.7081 | 2.477%
3873 | 16-76.5 | -76.3553 | 15.8149 | 1045.833 | 154.5139 | 184.563 | 221.7612 | 254.8102 | 292.7898 | 2.469%
3874 | 16-76.5 | -76.6266 | 15.8149 | 1063.8686 | 154.4669 | 184.5469 | 221.7893 | 254.8836 | 292.9215 | 2.465%
3875 | 16-77 | -76.8979 | 15.8149 | 1081.9039 | 154.4698 | 184.5557 | 221.8372 | 254.9709 | 293.0588 | 2.464%
3876 | 16-77 | -77.1692 | 15.8149 | 1099.939 | 154.5098 | 184.5815 | 221.8912 | 255.0527 | 293.1753 | 2.466%
3877 | 16-77.5 | -77.4405 | 15.8149 | 1117.9738 | 154.6232 | 184.6523 | 221.993 | 255.1842 | 293.3428 | 2.473%
3878 | 16-77.5 | -77.7119 | 15.8149 | 1136.0083 | 154.788 | 184.7533 | 222.122 | 255.3388 | 293.5276 | 2.484%
3879 | 16-78 | -77.9832 | 15.8149 | 1154.0425 | 155.0027 | 184.888 | 222.2916 | 255.5401 | 293.766 | 2.498%
3880 | 16-78.5 | -78.2545 | 15.8149 | 1172.0763 | 155.3131 | 185.0987 | 222.5766 | 255.895 | 294.2051 | 2.517%
3881 | 16-78.5 | -78.5258 | 15.8149 | 1190.1098 | 155.6655 | 185.3446 | 222.9112 | 256.3133 | 294.7245 | 2.54%
3882 | 16-79 | -78.7971 | 15.8149 | 1208.143 | 156.0437 | 185.6144 | 223.2813 | 256.7784 | 295.3047 | 2.565%
3883 | 16-79 | -79.0685 | 15.8149 | 1226.1758 | 156.4853 | 185.9443 | 223.7496 | 257.3792 | 296.0672 | 2.594%
3884 | 16-79.5 | -79.3398 | 15.8149 | 1244.2082 | 156.9404 | 186.298 | 224.2599 | 258.0401 | 296.9125 | 2.624%
3885 | 16-79.5 | -79.6111 | 15.8149 | 1262.2402 | 157.4015 | 186.6733 | 224.8114 | 258.7616 | 297.843 | 2.654%
3886 | 16-80 | -79.8824 | 15.8149 | 1280.2718 | 157.9019 | 187.1006 | 225.4531 | 259.6114 | 298.9493 | 2.687%
3887 | 16-80 | -80.1537 | 15.8149 | 1298.303 | 158.3605 | 187.5144 | 226.0977 | 260.481 | 300.098 | 2.717%
3888 | 16-80.5 | -80.4251 | 15.8149 | 1316.3337 | 158.7551 | 187.897 | 226.7259 | 261.3507 | 301.2685 | 2.742%
3889 | 16-80.5 | -80.6964 | 15.8149 | 1334.364 | 159.1038 | 188.2639 | 227.3635 | 262.2562 | 302.5094 | 2.763%
3890 | 16-81 | -80.9677 | 15.8149 | 1352.3938 | 159.3502 | 188.5734 | 227.9498 | 263.1184 | 303.7189 | 2.777%
3891 | 16-81 | -81.239 | 15.8149 | 1370.4231 | 159.4925 | 188.8256 | 228.4828 | 263.9334 | 304.891 | 2.783%
3892 | 16-81.5 | -81.5104 | 15.8149 | 1388.452 | 159.5441 | 189.034 | 228.9805 | 264.7238 | 306.0536 | 2.782%
3893 | 16-82 | -81.7817 | 15.8149 | 1406.4803 | 159.2304 | 188.9704 | 229.1125 | 265.0581 | 306.6507 | 2.756%
3894 | 16-82 | -82.053 | 15.8149 | 1424.5082 | 158.5287 | 188.5677 | 228.8534 | 264.9103 | 306.6552 | 2.703%
3895 | 16-82.5 | -82.3243 | 15.8149 | 1442.5355 | 157.4826 | 187.802 | 228.2617 | 264.3638 | 306.1823 | 2.626%
3896 | 16-82.5 | -82.5956 | 15.8149 | 1460.5623 | 156.2326 | 186.8246 | 227.467 | 263.5701 | 305.4095 | 2.538%
3897 | 16-83 | -82.867 | 15.8149 | 1478.5885 | 154.8477 | 185.712 | 226.5484 | 262.6305 | 304.4647 | 2.443%
3898 | 16-83 | -83.1383 | 15.8149 | 1496.6142 | 153.3551 | 184.4909 | 225.5401 | 261.5915 | 303.4102 | 2.346%
3899 | 16-83.5 | -83.4096 | 15.8149 | 1514.6393 | 151.6564 | 183.0334 | 224.2849 | 260.2379 | 301.9585 | 2.241%
3900 | 16-83.5 | -83.6809 | 15.8149 | 1532.6638 | 149.8136 | 181.394 | 222.8492 | 258.6517 | 300.2103 | 2.132%
3901 | 16-84 | -83.9522 | 15.8149 | 1550.6878 | 147.8688 | 179.6167 | 221.2631 | 256.8987 | 298.2501 | 2.023%
3902 | 16-84 | -84.2236 | 15.8149 | 1568.7111 | 145.7935 | 177.7042 | 219.5248 | 254.9464 | 296.0372 | 1.914%
3903 | 16-84.5 | -84.4949 | 15.8149 | 1586.7339 | 143.6299 | 175.6895 | 217.6884 | 252.8616 | 293.6583 | 1.806%
3904 | 16-85 | -84.7662 | 15.8149 | 1604.756 | 141.3983 | 173.5924 | 215.7744 | 250.6676 | 291.143 | 1.702%
3905 | 16-85 | -85.0375 | 15.8149 | 1622.7775 | 138.9208 | 171.1731 | 213.4825 | 247.9815 | 287.9676 | 1.593%
3906 | 16-85.5 | -85.3089 | 15.8149 | 1640.7983 | 136.4741 | 168.6658 | 211.1317 | 245.2481 | 284.7076 | 1.491%
3907 | 16-85.5 | -85.5802 | 15.8149 | 1658.8185 | 134.1536 | 166.2116 | 208.8154 | 242.6281 | 281.571 | 1.399%
3908 | 16-86 | -85.8515 | 15.8149 | 1676.838 | 132.3848 | 164.5729 | 207.2444 | 240.8553 | 279.4905 | 1.336%
3909 | 16-86 | -86.1228 | 15.8149 | 1694.8569 | 131.0699 | 163.5357 | 206.2616 | 239.8361 | 278.3785 | 1.293%
3910 | 16-86.5 | -86.3941 | 15.8149 | 1712.8751 | 130.1218 | 162.8998 | 205.7558 | 239.4272 | 278.0663 | 1.266%
3911 | 16-86.5 | -86.6655 | 15.8149 | 1730.8925 | 128.4008 | 161.6241 | 204.3826 | 237.8285 | 276.2018 | 1.214%
3912 | 16-87 | -86.9368 | 15.8149 | 1748.9093 | 126.1014 | 159.5445 | 202.3317 | 235.3503 | 273.2133 | 1.145%
3913 | 16-87 | -87.2081 | 15.8149 | 1766.9254 | 123.3881 | 156.7796 | 199.7651 | 232.2181 | 269.4016 | 1.066%
3914 | 16-87.5 | -87.4794 | 15.8149 | 1784.9407 | 120.6859 | 153.9852 | 197.2084 | 229.0667 | 265.5593 | 0.9921%
3915 | 16-88 | -87.7507 | 15.8149 | 1802.9553 | 118.0349 | 151.181 | 194.6673 | 225.9366 | 261.7411 | 0.9243%
3916 | 16-88 | -88.0221 | 15.8149 | 1820.9692 | 115.4703 | 148.4244 | 192.1735 | 222.8774 | 258.0138 | 0.8629%
3917 | 16-88.5 | -88.2934 | 15.8149 | 1838.9823 | 113.0424 | 145.7938 | 189.7813 | 219.9523 | 254.4481 | 0.8084%
3918 | 16-88.5 | -88.5647 | 15.8149 | 1856.9946 | 110.9491 | 143.5689 | 187.8023 | 217.5279 | 251.5148 | 0.765%
3919 | 16-89 | -88.836 | 15.8149 | 1875.0062 | 109.1689 | 141.7297 | 186.214 | 215.542 | 249.1273 | 0.7308%
3920 | 16-89 | -89.1074 | 15.8149 | 1893.0169 | 107.5919 | 140.121 | 184.8847 | 213.786 | 247.0191 | 0.7021%
3921 | 16-89.5 | -89.3787 | 15.8149 | 1911.0269 | 105.8121 | 138.0941 | 183.1148 | 211.577 | 244.3402 | 0.6691%
3922 | 16-89.5 | -89.65 | 15.8149 | 1929.0361 | 103.7636 | 135.6678 | 180.8475 | 208.7583 | 240.8571 | 0.6315%
3923 | 16-90 | -89.9213 | 15.8149 | 1947.0444 | 101.5622 | 133.0729 | 178.2314 | 205.5177 | 236.8055 | 0.5923%
3924 | 16-90 | -90.1926 | 15.8149 | 1965.052 | 100.3875 | 131.3989 | 176.6621 | 203.7205 | 234.6277 | 0.5708%
3925 | 16-90.5 | -90.464 | 15.8149 | 1983.0586 | 100.2048 | 131.0034 | 176.2214 | 203.3519 | 234.2695 | 0.5665%
3926 | 16-90.5 | -90.7353 | 15.8149 | 2001.0645 | 100.9367 | 131.8505 | 176.8831 | 204.2894 | 235.5334 | 0.578%
3927 | 16-50 | -50.0371 | 16.0862 | 706.4685 | 148.0227 | 179.5055 | 214.6053 | 245.6506 | 281.1888 | 2.079%
3928 | 16-50.5 | -50.3084 | 16.0862 | 688.4709 | 148.1813 | 179.6745 | 214.9661 | 246.2008 | 281.9758 | 2.087%
3929 | 16-50.5 | -50.5797 | 16.0862 | 670.475 | 148.2839 | 179.81 | 215.2828 | 246.6974 | 282.6978 | 2.092%
3930 | 16-51 | -50.851 | 16.0862 | 652.4812 | 148.3659 | 179.9357 | 215.5899 | 247.1852 | 283.4124 | 2.096%
3931 | 16-51 | -51.1224 | 16.0862 | 634.4895 | 148.466 | 180.0774 | 215.9254 | 247.7137 | 284.1833 | 2.101%
3932 | 16-51.5 | -51.3937 | 16.0862 | 616.5002 | 148.542 | 180.2013 | 216.231 | 248.2006 | 284.8984 | 2.104%
3933 | 16-51.5 | -51.665 | 16.0862 | 598.5136 | 148.616 | 180.3226 | 216.5333 | 248.6838 | 285.6095 | 2.108%
3934 | 16-52 | -51.9363 | 16.0862 | 580.5299 | 148.7095 | 180.4567 | 216.8596 | 249.2023 | 286.3702 | 2.112%
3935 | 16-52 | -52.2077 | 16.0862 | 562.5495 | 148.7663 | 180.5561 | 217.1285 | 249.6413 | 287.0243 | 2.114%
3936 | 16-52.5 | -52.479 | 16.0862 | 544.5727 | 148.8188 | 180.6422 | 217.3743 | 250.0478 | 287.634 | 2.116%
3937 | 16-53 | -52.7503 | 16.0862 | 526.5999 | 148.8885 | 180.7298 | 217.6204 | 250.4533 | 288.2414 | 2.119%
3938 | 16-53 | -53.0216 | 16.0862 | 508.6315 | 148.9164 | 180.7754 | 217.7999 | 250.7683 | 288.7286 | 2.119%
3939 | 16-53.5 | -53.2929 | 16.0862 | 490.6681 | 148.9483 | 180.8147 | 217.973 | 251.077 | 289.2099 | 2.119%
3940 | 16-53.5 | -53.5643 | 16.0862 | 472.7102 | 149.0069 | 180.8657 | 218.1669 | 251.4156 | 289.7327 | 2.121%
3941 | 16-54 | -53.8356 | 16.0862 | 454.7587 | 149.0496 | 180.8995 | 218.33 | 251.7101 | 290.1946 | 2.122%
3942 | 16-54 | -54.1069 | 16.0862 | 436.8142 | 149.1196 | 180.9461 | 218.5049 | 252.0151 | 290.6652 | 2.124%
3943 | 16-54.5 | -54.3782 | 16.0862 | 418.8777 | 149.231 | 181.0163 | 218.7065 | 252.3495 | 291.1683 | 2.128%
3944 | 16-54.5 | -54.6495 | 16.0862 | 400.9503 | 149.3453 | 181.0826 | 218.887 | 252.6454 | 291.6109 | 2.133%
3945 | 16-55 | -54.9209 | 16.0862 | 383.0334 | 149.5087 | 181.1827 | 219.1102 | 252.9922 | 292.1143 | 2.141%
3946 | 16-55 | -55.1922 | 16.0862 | 365.1285 | 149.7268 | 181.3223 | 219.3822 | 253.3966 | 292.6855 | 2.151%
3947 | 16-55.5 | -55.4635 | 16.0862 | 347.2374 | 149.9282 | 181.4406 | 219.5901 | 253.6934 | 293.0938 | 2.161%
3948 | 16-55.5 | -55.7348 | 16.0862 | 329.3626 | 150.1779 | 181.5928 | 219.8242 | 254.0077 | 293.5079 | 2.174%
3949 | 16-56 | -56.0061 | 16.0862 | 311.5067 | 150.4853 | 181.7881 | 220.0967 | 254.3543 | 293.9455 | 2.19%
3950 | 16-56.5 | -56.2775 | 16.0862 | 293.6733 | 150.798 | 181.9853 | 220.3438 | 254.6477 | 294.2939 | 2.207%
3951 | 16-56.5 | -56.5488 | 16.0862 | 275.8669 | 151.1854 | 182.2353 | 220.6398 | 254.9843 | 294.6769 | 2.229%
3952 | 16-57 | -56.8201 | 16.0862 | 258.0929 | 151.653 | 182.5429 | 220.9884 | 255.3667 | 295.0957 | 2.256%
3953 | 16-57 | -57.0914 | 16.0862 | 240.3586 | 152.1655 | 182.8773 | 221.3418 | 255.7307 | 295.4656 | 2.287%
3954 | 16-57.5 | -57.3628 | 16.0862 | 222.6736 | 152.774 | 183.2731 | 221.757 | 256.1552 | 295.8927 | 2.324%
3955 | 16-57.5 | -57.6341 | 16.0862 | 205.0506 | 153.4741 | 183.726 | 222.2272 | 256.6307 | 296.3644 | 2.368%
3956 | 16-58 | -57.9054 | 16.0862 | 187.5072 | 154.2249 | 184.2048 | 222.7071 | 257.0986 | 296.8054 | 2.415%
3957 | 16-58 | -58.1767 | 16.0862 | 170.068 | 155.067 | 184.7406 | 223.247 | 257.6278 | 297.3081 | 2.471%
3958 | 16-58.5 | -58.448 | 16.0862 | 152.7688 | 155.9691 | 185.315 | 223.8201 | 258.1836 | 297.8278 | 2.531%
3959 | 16-58.5 | -58.7194 | 16.0862 | 135.6631 | 156.873 | 185.8833 | 224.3667 | 258.6921 | 298.2733 | 2.595%
3960 | 16-59 | -58.9907 | 16.0862 | 118.8345 | 157.8463 | 186.5091 | 225.0002 | 259.316 | 298.8695 | 2.664%
3961 | 16-59.5 | -59.262 | 16.0862 | 102.4199 | 158.8856 | 187.2044 | 225.7331 | 260.0678 | 299.6287 | 2.741%
3962 | 16-59.5 | -59.5333 | 16.0862 | 86.6547 | 159.9948 | 188.003 | 226.6064 | 260.9953 | 300.6061 | 2.826%
3963 | 16-60 | -59.8046 | 16.0862 | 71.9671 | 161.2173 | 188.9517 | 227.6902 | 262.191 | 301.9224 | 2.923%
3964 | 16-60 | -60.076 | 16.0862 | 59.1653 | 162.4452 | 189.9314 | 228.8236 | 263.4549 | 303.3297 | 3.024%
3965 | 16-60.5 | -60.3473 | 16.0862 | 49.7275 | 163.5212 | 190.757 | 229.7597 | 264.4813 | 304.452 | 3.115%
3966 | 16-60.5 | -60.6186 | 16.0862 | 45.7837 | 164.4741 | 191.4631 | 230.5521 | 265.3426 | 305.3847 | 3.198%
3967 | 16-61 | -60.8899 | 16.0862 | 48.6878 | 165.3186 | 192.0833 | 231.2434 | 266.0896 | 306.1882 | 3.274%
3968 | 16-61 | -61.1613 | 16.0862 | 57.4099 | 166.0882 | 192.6698 | 231.9005 | 266.8029 | 306.9596 | 3.345%
3969 | 16-61.5 | -61.4326 | 16.0862 | 69.802 | 166.8169 | 193.2563 | 232.5734 | 267.5482 | 307.7837 | 3.414%
3970 | 16-61.5 | -61.7039 | 16.0862 | 84.2602 | 167.4675 | 193.811 | 233.2202 | 268.2741 | 308.5978 | 3.476%
3971 | 16-62 | -61.9752 | 16.0862 | 99.8912 | 168.0324 | 194.318 | 233.819 | 268.9531 | 309.3675 | 3.532%
3972 | 16-62 | -62.2465 | 16.0862 | 116.2229 | 168.5667 | 194.8263 | 234.4386 | 269.6727 | 310.2032 | 3.584%
3973 | 16-62.5 | -62.5179 | 16.0862 | 132.9973 | 169.0754 | 195.3471 | 235.0898 | 270.4432 | 311.1142 | 3.635%
3974 | 16-63 | -62.7892 | 16.0862 | 150.066 | 169.5564 | 195.8754 | 235.7651 | 271.2547 | 312.0879 | 3.683%
3975 | 16-63 | -63.0605 | 16.0862 | 167.3389 | 169.9977 | 196.3788 | 236.4289 | 272.0694 | 313.0844 | 3.726%
3976 | 16-63.5 | -63.3318 | 16.0862 | 184.7588 | 170.284 | 196.7061 | 236.8711 | 272.6205 | 313.7676 | 3.754%
3977 | 16-63.5 | -63.6031 | 16.0862 | 202.2877 | 170.4261 | 196.8691 | 237.1036 | 272.9198 | 314.1486 | 3.767%
3978 | 16-64 | -63.8745 | 16.0862 | 219.8995 | 170.5753 | 197.0554 | 237.3813 | 273.286 | 314.624 | 3.78%
3979 | 16-64 | -64.1458 | 16.0862 | 237.5757 | 170.7373 | 197.2722 | 237.7076 | 273.7184 | 315.1871 | 3.794%
3980 | 16-64.5 | -64.4171 | 16.0862 | 255.3029 | 170.8867 | 197.4877 | 238.0392 | 274.1628 | 315.7709 | 3.806%
3981 | 16-64.5 | -64.6884 | 16.0862 | 273.0712 | 170.9895 | 197.6568 | 238.3197 | 274.5526 | 316.2967 | 3.813%
3982 | 16-65 | -64.9598 | 16.0862 | 290.873 | 171.024 | 197.7489 | 238.497 | 274.8145 | 316.6647 | 3.813%
3983 | 16-65 | -65.2311 | 16.0862 | 308.7024 | 171.0096 | 197.7822 | 238.5925 | 274.9727 | 316.9023 | 3.809%
3984 | 16-65.5 | -65.5024 | 16.0862 | 326.555 | 170.9767 | 197.7913 | 238.6554 | 275.0905 | 317.0904 | 3.803%
3985 | 16-66 | -65.7737 | 16.0862 | 344.4271 | 170.8976 | 197.7467 | 238.646 | 275.1184 | 317.1671 | 3.792%
3986 | 16-66 | -66.045 | 16.0862 | 362.3158 | 170.7523 | 197.6254 | 238.5409 | 275.0332 | 317.1104 | 3.775%
3987 | 16-66.5 | -66.3164 | 16.0862 | 380.2187 | 170.5301 | 197.4153 | 238.3315 | 274.8302 | 316.9206 | 3.749%
3988 | 16-66.5 | -66.5877 | 16.0862 | 398.1338 | 170.1869 | 197.0607 | 237.9305 | 274.3911 | 316.4409 | 3.712%
3989 | 16-67 | -66.859 | 16.0862 | 416.0596 | 169.8255 | 196.6937 | 237.5211 | 273.9482 | 315.9633 | 3.673%
3990 | 16-67 | -67.1303 | 16.0862 | 433.9947 | 169.5255 | 196.4155 | 237.2457 | 273.6834 | 315.7191 | 3.64%
3991 | 16-67.5 | -67.4016 | 16.0862 | 451.938 | 169.2493 | 196.1733 | 237.0129 | 273.467 | 315.5295 | 3.609%
3992 | 16-67.5 | -67.673 | 16.0862 | 469.8886 | 168.9814 | 195.9465 | 236.7976 | 273.27 | 315.3614 | 3.58%
3993 | 16-68 | -67.9443 | 16.0862 | 487.8454 | 168.7177 | 195.7282 | 236.5953 | 273.09 | 315.2156 | 3.551%
3994 | 16-68 | -68.2156 | 16.0862 | 505.808 | 168.4117 | 195.4684 | 236.3355 | 272.8376 | 314.979 | 3.52%
3995 | 16-68.5 | -68.4869 | 16.0862 | 523.7756 | 168.0793 | 195.191 | 236.0608 | 272.5735 | 314.7354 | 3.485%
3996 | 16-69 | -68.7583 | 16.0862 | 541.7478 | 167.7318 | 194.9092 | 235.794 | 272.3303 | 314.5297 | 3.449%
3997 | 16-69 | -69.0296 | 16.0862 | 559.724 | 167.3248 | 194.5608 | 235.4199 | 271.9397 | 314.1264 | 3.41%
3998 | 16-69.5 | -69.3009 | 16.0862 | 577.7039 | 166.8833 | 194.1733 | 234.9741 | 271.445 | 313.5785 | 3.369%
3999 | 16-69.5 | -69.5722 | 16.0862 | 595.6871 | 166.4199 | 193.7584 | 234.4726 | 270.8663 | 312.9108 | 3.327%
4000 | 16-70 | -69.8435 | 16.0862 | 613.6733 | 165.8999 | 193.2766 | 233.8478 | 270.1083 | 311.9936 | 3.282%
4001 | 16-70 | -70.1149 | 16.0862 | 631.6621 | 165.3699 | 192.7837 | 233.1891 | 269.2933 | 310.99 | 3.238%
4002 | 16-70.5 | -70.3862 | 16.0862 | 649.6535 | 164.8435 | 192.2932 | 232.5186 | 268.452 | 309.9415 | 3.196%
4003 | 16-70.5 | -70.6575 | 16.0862 | 667.647 | 164.2839 | 191.7615 | 231.7563 | 267.4679 | 308.6858 | 3.152%
4004 | 16-71 | -70.9288 | 16.0862 | 685.6425 | 163.7311 | 191.2402 | 230.9944 | 266.4741 | 307.4071 | 3.11%
4005 | 16-71 | -71.2001 | 16.0862 | 703.6399 | 163.195 | 190.7357 | 230.2473 | 265.4926 | 306.1372 | 3.07%
4006 | 16-71.5 | -71.4715 | 16.0862 | 721.6389 | 162.6353 | 190.214 | 229.4606 | 264.449 | 304.777 | 3.03%
4007 | 16-71.5 | -71.7428 | 16.0862 | 739.6395 | 162.1062 | 189.7246 | 228.7062 | 263.4369 | 303.4464 | 2.992%
4008 | 16-72 | -72.0141 | 16.0862 | 757.6414 | 161.6109 | 189.2655 | 227.9815 | 262.4529 | 302.1411 | 2.958%
4009 | 16-72.5 | -72.2854 | 16.0862 | 775.6446 | 161.0897 | 188.7907 | 227.2159 | 261.4026 | 300.7372 | 2.922%
4010 | 16-72.5 | -72.5568 | 16.0862 | 793.6489 | 160.5961 | 188.3618 | 226.5251 | 260.4557 | 299.4724 | 2.889%
4011 | 16-73 | -72.8281 | 16.0862 | 811.6542 | 160.1306 | 187.9733 | 225.9032 | 259.6058 | 298.34 | 2.858%
4012 | 16-73 | -73.0994 | 16.0862 | 829.6605 | 159.658 | 187.5941 | 225.3035 | 258.7912 | 297.2595 | 2.826%
4013 | 16-73.5 | -73.3707 | 16.0862 | 847.6676 | 159.223 | 187.2636 | 224.7932 | 258.1062 | 296.359 | 2.796%
4014 | 16-73.5 | -73.642 | 16.0862 | 865.6755 | 158.8192 | 186.9717 | 224.3557 | 257.5281 | 295.608 | 2.769%
4015 | 16-74 | -73.9134 | 16.0862 | 883.6841 | 158.4229 | 186.6967 | 223.9573 | 257.0114 | 294.9465 | 2.742%
4016 | 16-74 | -74.1847 | 16.0862 | 901.6933 | 158.081 | 186.4843 | 223.684 | 256.6819 | 294.5502 | 2.718%
4017 | 16-74.5 | -74.456 | 16.0862 | 919.703 | 157.7796 | 186.3176 | 223.5046 | 256.4941 | 294.3558 | 2.696%
4018 | 16-74.5 | -74.7273 | 16.0862 | 937.7133 | 157.485 | 186.1628 | 223.3535 | 256.3511 | 294.227 | 2.674%
4019 | 16-75 | -74.9986 | 16.0862 | 955.7239 | 157.2484 | 186.056 | 223.2887 | 256.332 | 294.269 | 2.656%
4020 | 16-75.5 | -75.27 | 16.0862 | 973.735 | 157.0453 | 185.9757 | 223.2694 | 256.3774 | 294.399 | 2.641%
4021 | 16-75.5 | -75.5413 | 16.0862 | 991.7463 | 156.845 | 185.8928 | 223.2398 | 256.4044 | 294.5005 | 2.626%
4022 | 16-76 | -75.8126 | 16.0862 | 1009.758 | 156.7213 | 185.8584 | 223.2774 | 256.5165 | 294.7087 | 2.616%
4023 | 16-76 | -76.0839 | 16.0862 | 1027.7699 | 156.6476 | 185.8527 | 223.3478 | 256.6647 | 294.9567 | 2.609%
4024 | 16-76.5 | -76.3553 | 16.0862 | 1045.782 | 156.5963 | 185.8514 | 223.4084 | 256.7887 | 295.1615 | 2.604%
4025 | 16-76.5 | -76.6266 | 16.0862 | 1063.7942 | 156.6127 | 185.8885 | 223.5097 | 256.9543 | 295.4084 | 2.605%
4026 | 16-77 | -76.8979 | 16.0862 | 1081.8065 | 156.6769 | 185.9501 | 223.629 | 257.1306 | 295.6559 | 2.608%
4027 | 16-77 | -77.1692 | 16.0862 | 1099.819 | 156.7753 | 186.0276 | 223.7525 | 257.2988 | 295.8793 | 2.614%
4028 | 16-77.5 | -77.4405 | 16.0862 | 1117.8315 | 156.9421 | 186.1481 | 223.9207 | 257.5122 | 296.1475 | 2.625%
4029 | 16-77.5 | -77.7119 | 16.0862 | 1135.8439 | 157.1548 | 186.2957 | 224.1095 | 257.7389 | 296.419 | 2.64%
4030 | 16-78 | -77.9832 | 16.0862 | 1153.8564 | 157.4115 | 186.4727 | 224.3292 | 257.9974 | 296.7226 | 2.658%
4031 | 16-78.5 | -78.2545 | 16.0862 | 1171.8689 | 157.7548 | 186.7204 | 224.6533 | 258.3925 | 297.2029 | 2.682%
4032 | 16-78.5 | -78.5258 | 16.0862 | 1189.8812 | 158.1322 | 186.9979 | 225.0153 | 258.8332 | 297.7374 | 2.708%
4033 | 16-79 | -78.7971 | 16.0862 | 1207.8935 | 158.5303 | 187.296 | 225.4041 | 259.3067 | 298.3121 | 2.736%
4034 | 16-79 | -79.0685 | 16.0862 | 1225.9056 | 158.989 | 187.654 | 225.8882 | 259.9098 | 299.0592 | 2.769%
4035 | 16-79.5 | -79.3398 | 16.0862 | 1243.9175 | 159.4603 | 188.0357 | 226.4114 | 260.5674 | 299.8799 | 2.803%
4036 | 16-79.5 | -79.6111 | 16.0862 | 1261.9293 | 159.9415 | 188.4414 | 226.9787 | 261.2891 | 300.7897 | 2.837%
4037 | 16-80 | -79.8824 | 16.0862 | 1279.9409 | 160.4667 | 188.9053 | 227.6473 | 262.1544 | 301.8963 | 2.875%
4038 | 16-80 | -80.1537 | 16.0862 | 1297.9523 | 160.9573 | 189.3603 | 228.3258 | 263.0497 | 303.0587 | 2.91%
4039 | 16-80.5 | -80.4251 | 16.0862 | 1315.9634 | 161.3915 | 189.7877 | 228.9925 | 263.9499 | 304.2486 | 2.94%
4040 | 16-80.5 | -80.6964 | 16.0862 | 1333.9743 | 161.7866 | 190.2033 | 229.6722 | 264.8893 | 305.5113 | 2.966%
4041 | 16-81 | -80.9677 | 16.0862 | 1351.9849 | 162.0891 | 190.5666 | 230.3063 | 265.7915 | 306.7495 | 2.985%
4042 | 16-81 | -81.239 | 16.0862 | 1369.9951 | 162.2971 | 190.8788 | 230.8961 | 266.6581 | 307.9649 | 2.996%
4043 | 16-81.5 | -81.5104 | 16.0862 | 1388.0051 | 162.4227 | 191.1535 | 231.4609 | 267.5143 | 309.1898 | 3%
4044 | 16-82 | -81.7817 | 16.0862 | 1406.0147 | 162.2226 | 191.1852 | 231.6985 | 267.9634 | 309.9109 | 2.981%
4045 | 16-82 | -82.053 | 16.0862 | 1424.0239 | 161.6795 | 190.9422 | 231.5929 | 267.9914 | 310.1168 | 2.936%
4046 | 16-82.5 | -82.3243 | 16.0862 | 1442.0328 | 160.8335 | 190.3969 | 231.2032 | 267.683 | 309.9247 | 2.868%
4047 | 16-82.5 | -82.5956 | 16.0862 | 1460.0412 | 159.7969 | 189.6578 | 230.6225 | 267.1452 | 309.4572 | 2.787%
4048 | 16-83 | -82.867 | 16.0862 | 1478.0493 | 158.6308 | 188.7926 | 229.923 | 266.4707 | 308.8327 | 2.699%
4049 | 16-83 | -83.1383 | 16.0862 | 1496.0569 | 157.3606 | 187.8274 | 229.1397 | 265.7071 | 308.1144 | 2.607%
4050 | 16-83.5 | -83.4096 | 16.0862 | 1514.0641 | 155.901 | 186.6526 | 228.1232 | 264.6463 | 307.0207 | 2.506%
4051 | 16-83.5 | -83.6809 | 16.0862 | 1532.0708 | 154.3119 | 185.3238 | 226.9437 | 263.3753 | 305.6587 | 2.401%
4052 | 16-84 | -83.9522 | 16.0862 | 1550.0771 | 152.6327 | 183.8827 | 225.6536 | 261.9626 | 304.1172 | 2.296%
4053 | 16-84 | -84.2236 | 16.0862 | 1568.0828 | 150.8055 | 182.2877 | 224.1864 | 260.3246 | 302.2913 | 2.187%
4054 | 16-84.5 | -84.4949 | 16.0862 | 1586.088 | 148.8674 | 180.5661 | 222.5877 | 258.5215 | 300.2593 | 2.077%
4055 | 16-85 | -84.7662 | 16.0862 | 1604.0928 | 146.8377 | 178.7362 | 220.875 | 256.5757 | 298.05 | 1.968%
4056 | 16-85 | -85.0375 | 16.0862 | 1622.097 | 144.5523 | 176.5798 | 218.7875 | 254.1356 | 295.1837 | 1.852%
4057 | 16-85.5 | -85.3089 | 16.0862 | 1640.1006 | 142.2494 | 174.3052 | 216.6094 | 251.6076 | 292.1902 | 1.74%
4058 | 16-85.5 | -85.5802 | 16.0862 | 1658.1037 | 140.0169 | 172.0172 | 214.4242 | 249.1421 | 289.2645 | 1.637%
4059 | 16-86 | -85.8515 | 16.0862 | 1676.1062 | 138.2717 | 170.472 | 212.9269 | 247.453 | 287.3139 | 1.565%
4060 | 16-86 | -86.1228 | 16.0862 | 1694.1081 | 136.944 | 169.4949 | 211.9893 | 246.4875 | 286.3006 | 1.515%
4061 | 16-86.5 | -86.3941 | 16.0862 | 1712.1094 | 135.9479 | 168.8862 | 211.4933 | 246.0985 | 286.0502 | 1.48%
4062 | 16-86.5 | -86.6655 | 16.0862 | 1730.1101 | 134.0905 | 167.5563 | 210.0168 | 244.3977 | 284.0927 | 1.415%
4063 | 16-87 | -86.9368 | 16.0862 | 1748.1101 | 131.5568 | 165.3203 | 207.7552 | 241.6877 | 280.8493 | 1.327%
4064 | 16-87 | -87.2081 | 16.0862 | 1766.1095 | 128.5182 | 162.2789 | 204.88 | 238.2014 | 276.631 | 1.225%
4065 | 16-87.5 | -87.4794 | 16.0862 | 1784.1083 | 125.433 | 159.1241 | 201.9316 | 234.6183 | 272.2869 | 1.128%
4066 | 16-88 | -87.7507 | 16.0862 | 1802.1064 | 122.3724 | 155.9235 | 198.9836 | 231.0347 | 267.9412 | 1.039%
4067 | 16-88 | -88.0221 | 16.0862 | 1820.1038 | 119.3744 | 152.7388 | 196.0741 | 227.5029 | 263.6634 | 0.9592%
4068 | 16-88.5 | -88.2934 | 16.0862 | 1838.1005 | 116.4962 | 149.6593 | 193.2662 | 224.094 | 259.5337 | 0.888%
4069 | 16-88.5 | -88.5647 | 16.0862 | 1856.0965 | 113.9223 | 146.9401 | 190.8313 | 221.1482 | 255.9906 | 0.8297%
4070 | 16-89 | -88.836 | 16.0862 | 1874.0917 | 111.6373 | 144.5611 | 188.7517 | 218.6055 | 252.9501 | 0.7819%
4071 | 16-89 | -89.1074 | 16.0862 | 1892.0863 | 109.5284 | 142.3617 | 186.8931 | 216.2517 | 250.1377 | 0.7406%
4072 | 16-89.5 | -89.3787 | 16.0862 | 1910.0801 | 107.1987 | 139.6985 | 184.5698 | 213.4216 | 246.7273 | 0.6955%
4073 | 16-89.5 | -89.65 | 16.0862 | 1928.0731 | 104.5903 | 136.6066 | 181.7395 | 209.9692 | 242.4958 | 0.6466%
4074 | 16-90 | -89.9213 | 16.0862 | 1946.0654 | 101.814 | 133.3285 | 178.5521 | 206.0759 | 237.6694 | 0.5973%
4075 | 16-90 | -90.1926 | 16.0862 | 1964.0569 | 100.0969 | 131.0053 | 176.4754 | 203.6896 | 234.8022 | 0.5676%
4076 | 16-90.5 | -90.464 | 16.0862 | 1982.0476 | 99.4013 | 129.9992 | 175.5786 | 202.7971 | 233.8421 | 0.5561%
4077 | 16-90.5 | -90.7353 | 16.0862 | 2000.0375 | 99.6473 | 130.2983 | 175.8314 | 203.2739 | 234.5872 | 0.5606%
4078 | 16-50 | -50.0371 | 16.3575 | 707.453 | 149.2614 | 180.3546 | 215.522 | 246.6147 | 282.1948 | 2.152%
4079 | 16-50.5 | -50.3084 | 16.3575 | 689.5059 | 149.4813 | 180.5592 | 215.9245 | 247.2119 | 283.0345 | 2.164%
4080 | 16-50.5 | -50.5797 | 16.3575 | 671.5626 | 149.6411 | 180.7277 | 216.2806 | 247.7534 | 283.8078 | 2.172%
4081 | 16-51 | -50.851 | 16.3575 | 653.6234 | 149.7761 | 180.8837 | 216.6248 | 248.2842 | 284.5721 | 2.179%
4082 | 16-51 | -51.1224 | 16.3575 | 635.6889 | 149.9256 | 181.0532 | 216.9952 | 248.8542 | 285.3922 | 2.186%
4083 | 16-51.5 | -51.3937 | 16.3575 | 617.7593 | 150.0444 | 181.201 | 217.3333 | 249.3818 | 286.1578 | 2.192%
4084 | 16-51.5 | -51.665 | 16.3575 | 599.8353 | 150.1569 | 181.3439 | 217.6676 | 249.9068 | 286.9229 | 2.197%
4085 | 16-52 | -51.9363 | 16.3575 | 581.9172 | 150.2864 | 181.4989 | 218.0266 | 250.4694 | 287.7416 | 2.203%
4086 | 16-52 | -52.2077 | 16.3575 | 564.0058 | 150.3751 | 181.6176 | 218.3268 | 250.9514 | 288.4531 | 2.207%
4087 | 16-52.5 | -52.479 | 16.3575 | 546.1016 | 150.4556 | 181.7218 | 218.6026 | 251.3994 | 289.1186 | 2.21%
4088 | 16-53 | -52.7503 | 16.3575 | 528.2056 | 150.5494 | 181.8265 | 218.8775 | 251.845 | 289.7801 | 2.214%
4089 | 16-53 | -53.0216 | 16.3575 | 510.3185 | 150.5966 | 181.8881 | 219.0853 | 252.2004 | 290.3227 | 2.215%
4090 | 16-53.5 | -53.2929 | 16.3575 | 492.4414 | 150.6442 | 181.9427 | 219.2849 | 252.5467 | 290.8552 | 2.216%
4091 | 16-53.5 | -53.5643 | 16.3575 | 474.5755 | 150.7153 | 182.0082 | 219.5029 | 252.9188 | 291.423 | 2.218%
4092 | 16-54 | -53.8356 | 16.3575 | 456.722 | 150.7646 | 182.0535 | 219.6864 | 253.2422 | 291.9246 | 2.219%
4093 | 16-54 | -54.1069 | 16.3575 | 438.8825 | 150.8366 | 182.1089 | 219.8779 | 253.5716 | 292.4293 | 2.221%
4094 | 16-54.5 | -54.3782 | 16.3575 | 421.0589 | 150.9465 | 182.1856 | 220.0927 | 253.9258 | 292.9605 | 2.226%
4095 | 16-54.5 | -54.6495 | 16.3575 | 403.2533 | 151.0581 | 182.258 | 220.2861 | 254.2413 | 293.4312 | 2.23%
4096 | 16-55 | -54.9209 | 16.3575 | 385.4681 | 151.2207 | 182.3658 | 220.5232 | 254.6083 | 293.9624 | 2.238%
4097 | 16-55 | -55.1922 | 16.3575 | 367.7065 | 151.4407 | 182.5149 | 220.8109 | 255.0344 | 294.563 | 2.249%
4098 | 16-55.5 | -55.4635 | 16.3575 | 349.972 | 151.6454 | 182.6442 | 221.0393 | 255.3611 | 295.013 | 2.259%
4099 | 16-55.5 | -55.7348 | 16.3575 | 332.269 | 151.8997 | 182.8084 | 221.2993 | 255.7152 | 295.4844 | 2.273%
4100 | 16-56 | -56.0061 | 16.3575 | 314.6028 | 152.21 | 183.0144 | 221.6005 | 256.1089 | 295.9923 | 2.29%
4101 | 16-56.5 | -56.2775 | 16.3575 | 296.98 | 152.5206 | 183.2179 | 221.8739 | 256.4488 | 296.4133 | 2.308%
4102 | 16-56.5 | -56.5488 | 16.3575 | 279.409 | 152.9 | 183.4691 | 222.1918 | 256.8286 | 296.867 | 2.33%
4103 | 16-57 | -56.8201 | 16.3575 | 261.9001 | 153.3506 | 183.7713 | 222.556 | 257.2485 | 297.3514 | 2.357%
4104 | 16-57 | -57.0914 | 16.3575 | 244.4667 | 153.839 | 184.0935 | 222.9156 | 257.638 | 297.7719 | 2.387%
4105 | 16-57.5 | -57.3628 | 16.3575 | 227.1263 | 154.4185 | 184.4734 | 223.3305 | 258.0784 | 298.2363 | 2.424%
4106 | 16-57.5 | -57.6341 | 16.3575 | 209.9019 | 155.0846 | 184.9079 | 223.7951 | 258.5623 | 298.7346 | 2.467%
4107 | 16-58 | -57.9054 | 16.3575 | 192.8246 | 155.7993 | 185.3668 | 224.2655 | 259.0318 | 299.192 | 2.514%
4108 | 16-58 | -58.1767 | 16.3575 | 175.9374 | 156.6007 | 185.8804 | 224.79 | 259.5533 | 299.6972 | 2.568%
4109 | 16-58.5 | -58.448 | 16.3575 | 159.3007 | 157.458 | 186.4305 | 225.3423 | 260.0925 | 300.2062 | 2.628%
4110 | 16-58.5 | -58.7194 | 16.3575 | 143.0019 | 158.3158 | 186.9731 | 225.8625 | 260.5744 | 300.6257 | 2.691%
4111 | 16-59 | -58.9907 | 16.3575 | 127.1712 | 159.2429 | 187.5726 | 226.4619 | 261.157 | 301.172 | 2.76%
4112 | 16-59.5 | -59.262 | 16.3575 | 112.0073 | 160.2377 | 188.243 | 227.1569 | 261.8582 | 301.8648 | 2.836%
4113 | 16-59.5 | -59.5333 | 16.3575 | 97.8206 | 161.3078 | 189.0211 | 227.9942 | 262.7342 | 302.7714 | 2.922%
4114 | 16-60 | -59.8046 | 16.3575 | 85.1015 | 162.4996 | 189.9569 | 229.0497 | 263.8863 | 304.0245 | 3.02%
4115 | 16-60 | -60.076 | 16.3575 | 74.6043 | 163.7054 | 190.9305 | 230.1609 | 265.1114 | 305.3721 | 3.123%
4116 | 16-60.5 | -60.3473 | 16.3575 | 67.3757 | 164.7686 | 191.7549 | 231.0773 | 266.0992 | 306.4314 | 3.217%
4117 | 16-60.5 | -60.6186 | 16.3575 | 64.5238 | 165.7146 | 192.4648 | 231.8558 | 266.9283 | 307.3082 | 3.303%
4118 | 16-61 | -60.8899 | 16.3575 | 66.6131 | 166.558 | 193.0928 | 232.5373 | 267.6473 | 308.0601 | 3.382%
4119 | 16-61 | -61.1613 | 16.3575 | 73.2219 | 167.332 | 193.6895 | 233.1872 | 268.3351 | 308.7823 | 3.457%
4120 | 16-61.5 | -61.4326 | 16.3575 | 83.281 | 168.0667 | 194.2871 | 233.8541 | 269.0567 | 309.5596 | 3.529%
4121 | 16-61.5 | -61.7039 | 16.3575 | 95.7088 | 168.7271 | 194.8548 | 234.498 | 269.7629 | 310.3324 | 3.596%
4122 | 16-62 | -61.9752 | 16.3575 | 109.703 | 169.3063 | 195.3777 | 235.0992 | 270.4301 | 311.0715 | 3.656%
4123 | 16-62 | -62.2465 | 16.3575 | 124.7376 | 169.8558 | 195.9042 | 235.7266 | 271.1465 | 311.8895 | 3.713%
4124 | 16-62.5 | -62.5179 | 16.3575 | 140.4789 | 170.3927 | 196.4605 | 236.4131 | 271.9509 | 312.8317 | 3.769%
4125 | 16-63 | -62.7892 | 16.3575 | 156.714 | 170.9261 | 197.0554 | 237.1691 | 272.8557 | 313.9134 | 3.824%
4126 | 16-63 | -63.0605 | 16.3575 | 173.3043 | 171.4433 | 197.6565 | 237.9569 | 273.8188 | 315.0873 | 3.877%
4127 | 16-63.5 | -63.3318 | 16.3575 | 190.1567 | 171.8 | 198.0739 | 238.5123 | 274.5046 | 315.9307 | 3.913%
4128 | 16-63.5 | -63.6031 | 16.3575 | 207.2074 | 171.988 | 198.2943 | 238.8135 | 274.8824 | 316.4018 | 3.932%
4129 | 16-64 | -63.8745 | 16.3575 | 224.4109 | 172.1604 | 198.5092 | 239.1216 | 275.2801 | 316.9091 | 3.948%
4130 | 16-64 | -64.1458 | 16.3575 | 241.7348 | 172.3383 | 198.7445 | 239.467 | 275.7318 | 317.4912 | 3.964%
4131 | 16-64.5 | -64.4171 | 16.3575 | 259.1549 | 172.5049 | 198.9794 | 239.8221 | 276.2033 | 318.1064 | 3.978%
4132 | 16-64.5 | -64.6884 | 16.3575 | 276.6529 | 172.6255 | 199.1696 | 240.1313 | 276.6291 | 318.6768 | 3.987%
4133 | 16-65 | -64.9598 | 16.3575 | 294.2149 | 172.6774 | 199.2815 | 240.3374 | 276.9285 | 319.093 | 3.989%
4134 | 16-65 | -65.2311 | 16.3575 | 311.8301 | 172.6772 | 199.3304 | 240.4567 | 277.1183 | 319.3721 | 3.985%
4135 | 16-65.5 | -65.5024 | 16.3575 | 329.49 | 172.6532 | 199.3494 | 240.5356 | 277.258 | 319.5892 | 3.979%
4136 | 16-66 | -65.7737 | 16.3575 | 347.1876 | 172.5797 | 199.3099 | 240.537 | 277.3023 | 319.6895 | 3.969%
4137 | 16-66 | -66.045 | 16.3575 | 364.9175 | 172.4241 | 199.1737 | 240.4163 | 277.2014 | 319.617 | 3.949%
4138 | 16-66.5 | -66.3164 | 16.3575 | 382.6751 | 172.1647 | 198.9151 | 240.1459 | 276.9258 | 319.341 | 3.918%
4139 | 16-66.5 | -66.5877 | 16.3575 | 400.4568 | 171.7489 | 198.4642 | 239.6165 | 276.3281 | 318.666 | 3.872%
4140 | 16-67 | -66.859 | 16.3575 | 418.2593 | 171.3065 | 197.9883 | 239.0599 | 275.7014 | 317.9604 | 3.823%
4141 | 16-67 | -67.1303 | 16.3575 | 436.0803 | 170.9376 | 197.6159 | 238.656 | 275.2755 | 317.5151 | 3.782%
4142 | 16-67.5 | -67.4016 | 16.3575 | 453.9174 | 170.615 | 197.307 | 238.3343 | 274.9492 | 317.1906 | 3.745%
4143 | 16-67.5 | -67.673 | 16.3575 | 471.7688 | 170.31 | 197.0244 | 238.0468 | 274.6646 | 316.9162 | 3.711%
4144 | 16-68 | -67.9443 | 16.3575 | 489.6329 | 170.01 | 196.7514 | 237.7743 | 274.4001 | 316.6689 | 3.678%
4145 | 16-68 | -68.2156 | 16.3575 | 507.5083 | 169.6679 | 196.4345 | 237.4404 | 274.0576 | 316.3232 | 3.641%
4146 | 16-68.5 | -68.4869 | 16.3575 | 525.3939 | 169.2998 | 196.1006 | 237.0924 | 273.7047 | 315.972 | 3.601%
4147 | 16-69 | -68.7583 | 16.3575 | 543.2886 | 168.9161 | 195.7639 | 236.7555 | 273.3772 | 315.6649 | 3.561%
4148 | 16-69 | -69.0296 | 16.3575 | 561.1915 | 168.4637 | 195.3565 | 236.3074 | 272.8988 | 315.1576 | 3.515%
4149 | 16-69.5 | -69.3009 | 16.3575 | 579.1018 | 167.9669 | 194.9044 | 235.7803 | 272.3073 | 314.4945 | 3.467%
4150 | 16-69.5 | -69.5722 | 16.3575 | 597.0189 | 167.4386 | 194.419 | 235.1884 | 271.6198 | 313.696 | 3.418%
4151 | 16-70 | -69.8435 | 16.3575 | 614.942 | 166.8544 | 193.8687 | 234.4788 | 270.7621 | 312.6616 | 3.367%
4152 | 16-70 | -70.1149 | 16.3575 | 632.8707 | 166.2699 | 193.3234 | 233.7624 | 269.8854 | 311.5927 | 3.316%
4153 | 16-70.5 | -70.3862 | 16.3575 | 650.8045 | 165.7021 | 192.8001 | 233.0667 | 269.0278 | 310.54 | 3.269%
4154 | 16-70.5 | -70.6575 | 16.3575 | 668.743 | 165.1253 | 192.2591 | 232.3116 | 268.0683 | 309.3316 | 3.222%
4155 | 16-71 | -70.9288 | 16.3575 | 686.6857 | 164.5706 | 191.7392 | 231.5684 | 267.1109 | 308.1121 | 3.179%
4156 | 16-71 | -71.2001 | 16.3575 | 704.6322 | 164.0454 | 191.2436 | 230.8462 | 266.1705 | 306.904 | 3.138%
4157 | 16-71.5 | -71.4715 | 16.3575 | 722.5824 | 163.4946 | 190.728 | 230.0772 | 265.1563 | 305.5882 | 3.097%
4158 | 16-71.5 | -71.7428 | 16.3575 | 740.5358 | 162.9745 | 190.2453 | 229.3396 | 264.1713 | 304.2976 | 3.059%
4159 | 16-72 | -72.0141 | 16.3575 | 758.4922 | 162.4868 | 189.7922 | 228.6294 | 263.2104 | 303.0264 | 3.025%
4160 | 16-72.5 | -72.2854 | 16.3575 | 776.4514 | 161.9554 | 189.3111 | 227.861 | 262.1612 | 301.6288 | 2.988%
4161 | 16-72.5 | -72.5568 | 16.3575 | 794.4132 | 161.4443 | 188.8703 | 227.1586 | 261.2032 | 300.3543 | 2.953%
4162 | 16-73 | -72.8281 | 16.3575 | 812.3773 | 160.9627 | 188.4705 | 226.525 | 260.3419 | 299.2109 | 2.92%
4163 | 16-73 | -73.0994 | 16.3575 | 830.3437 | 160.5056 | 188.1006 | 225.9415 | 259.5504 | 298.1623 | 2.888%
4164 | 16-73.5 | -73.3707 | 16.3575 | 848.312 | 160.1083 | 187.7915 | 225.4595 | 258.9003 | 297.3045 | 2.861%
4165 | 16-73.5 | -73.642 | 16.3575 | 866.2822 | 159.7601 | 187.53 | 225.0583 | 258.3634 | 296.6003 | 2.837%
4166 | 16-74 | -73.9134 | 16.3575 | 884.2541 | 159.4227 | 187.2858 | 224.6926 | 257.8803 | 295.9729 | 2.814%
4167 | 16-74 | -74.1847 | 16.3575 | 902.2275 | 159.1319 | 187.1001 | 224.4483 | 257.5812 | 295.6081 | 2.793%
4168 | 16-74.5 | -74.456 | 16.3575 | 920.2025 | 158.8735 | 186.9566 | 224.2951 | 257.422 | 295.4446 | 2.773%
4169 | 16-74.5 | -74.7273 | 16.3575 | 938.1787 | 158.6159 | 186.8231 | 224.1706 | 257.3103 | 295.3524 | 2.754%
4170 | 16-75 | -74.9986 | 16.3575 | 956.1562 | 158.4253 | 186.7458 | 224.1457 | 257.341 | 295.4561 | 2.739%
4171 | 16-75.5 | -75.27 | 16.3575 | 974.1349 | 158.2754 | 186.7014 | 224.1774 | 257.4516 | 295.6686 | 2.726%
4172 | 16-75.5 | -75.5413 | 16.3575 | 992.1146 | 158.1362 | 186.6609 | 224.2094 | 257.5589 | 295.8731 | 2.714%
4173 | 16-76 | -75.8126 | 16.3575 | 1010.0952 | 158.0996 | 186.6868 | 224.3346 | 257.7846 | 296.2267 | 2.71%
4174 | 16-76 | -76.0839 | 16.3575 | 1028.0768 | 158.1362 | 186.7569 | 224.5132 | 258.0719 | 296.6514 | 2.71%
4175 | 16-76.5 | -76.3553 | 16.3575 | 1046.0591 | 158.2053 | 186.8385 | 224.6888 | 258.3411 | 297.0381 | 2.713%
4176 | 16-76.5 | -76.6266 | 16.3575 | 1064.0422 | 158.3212 | 186.9459 | 224.8847 | 258.6243 | 297.4302 | 2.72%
4177 | 16-77 | -76.8979 | 16.3575 | 1082.0259 | 158.4632 | 187.0656 | 225.0802 | 258.8939 | 297.7916 | 2.729%
4178 | 16-77 | -77.1692 | 16.3575 | 1100.0102 | 158.6222 | 187.1915 | 225.267 | 259.1392 | 298.1085 | 2.74%
4179 | 16-77.5 | -77.4405 | 16.3575 | 1117.9951 | 158.8448 | 187.3597 | 225.4968 | 259.4272 | 298.467 | 2.756%
4180 | 16-77.5 | -77.7119 | 16.3575 | 1135.9805 | 159.1082 | 187.5528 | 225.7427 | 259.7217 | 298.819 | 2.775%
4181 | 16-78 | -77.9832 | 16.3575 | 1153.9663 | 159.4098 | 187.7719 | 226.0119 | 260.0361 | 299.1859 | 2.797%
4182 | 16-78.5 | -78.2545 | 16.3575 | 1171.9524 | 159.7906 | 188.0579 | 226.3765 | 260.4733 | 299.709 | 2.825%
4183 | 16-78.5 | -78.5258 | 16.3575 | 1189.9389 | 160.1989 | 188.3694 | 226.7685 | 260.939 | 300.2618 | 2.856%
4184 | 16-79 | -78.7971 | 16.3575 | 1207.9257 | 160.6227 | 188.6974 | 227.177 | 261.4208 | 300.8296 | 2.888%
4185 | 16-79 | -79.0685 | 16.3575 | 1225.9128 | 161.1028 | 189.0835 | 227.6732 | 262.019 | 301.5491 | 2.925%
4186 | 16-79.5 | -79.3398 | 16.3575 | 1243.9 | 161.5929 | 189.4921 | 228.2032 | 262.6621 | 302.3275 | 2.963%
4187 | 16-79.5 | -79.6111 | 16.3575 | 1261.8874 | 162.0932 | 189.9258 | 228.7779 | 263.3692 | 303.1939 | 3.002%
4188 | 16-80 | -79.8824 | 16.3575 | 1279.875 | 162.6403 | 190.4219 | 229.4609 | 264.23 | 304.2709 | 3.045%
4189 | 16-80 | -80.1537 | 16.3575 | 1297.8626 | 163.1598 | 190.9129 | 230.1597 | 265.1283 | 305.4131 | 3.085%
4190 | 16-80.5 | -80.4251 | 16.3575 | 1315.8502 | 163.6308 | 191.3797 | 230.8497 | 266.034 | 306.5845 | 3.12%
4191 | 16-80.5 | -80.6964 | 16.3575 | 1333.8379 | 164.0694 | 191.8382 | 231.5541 | 266.9781 | 307.8251 | 3.153%
4192 | 16-81 | -80.9677 | 16.3575 | 1351.8256 | 164.4246 | 192.2484 | 232.2168 | 267.8884 | 309.0437 | 3.178%
4193 | 16-81 | -81.239 | 16.3575 | 1369.8133 | 164.6945 | 192.6128 | 232.842 | 268.7716 | 310.2497 | 3.195%
4194 | 16-81.5 | -81.5104 | 16.3575 | 1387.8008 | 164.8898 | 192.9453 | 233.4505 | 269.655 | 311.4789 | 3.206%
4195 | 16-82 | -81.7817 | 16.3575 | 1405.7883 | 164.8018 | 193.0651 | 233.7756 | 270.188 | 312.2768 | 3.194%
4196 | 16-82 | -82.053 | 16.3575 | 1423.7756 | 164.4199 | 192.9628 | 233.8132 | 270.3726 | 312.6532 | 3.159%
4197 | 16-82.5 | -82.3243 | 16.3575 | 1441.7628 | 163.7808 | 192.6256 | 233.6234 | 270.295 | 312.7273 | 3.103%
4198 | 16-82.5 | -82.5956 | 16.3575 | 1459.7498 | 162.9665 | 192.1152 | 233.2596 | 270.0132 | 312.5623 | 3.033%
4199 | 16-83 | -82.867 | 16.3575 | 1477.7366 | 162.0291 | 191.489 | 232.7842 | 269.6078 | 312.2604 | 2.955%
4200 | 16-83 | -83.1383 | 16.3575 | 1495.7231 | 160.993 | 190.7721 | 232.2316 | 269.1247 | 311.8823 | 2.872%
4201 | 16-83.5 | -83.4096 | 16.3575 | 1513.7094 | 159.7825 | 189.8691 | 231.4589 | 268.3624 | 311.153 | 2.779%
4202 | 16-83.5 | -83.6809 | 16.3575 | 1531.6954 | 158.4541 | 188.8354 | 230.5382 | 267.4105 | 310.1832 | 2.681%
4203 | 16-84 | -83.9522 | 16.3575 | 1549.6812 | 157.0443 | 187.7106 | 229.5224 | 266.3391 | 309.0642 | 2.581%
4204 | 16-84 | -84.2236 | 16.3575 | 1567.6666 | 155.4769 | 186.4257 | 228.3214 | 265.0344 | 307.6532 | 2.476%
4205 | 16-84.5 | -84.4949 | 16.3575 | 1585.6516 | 153.7858 | 185.0048 | 226.9775 | 263.5513 | 306.021 | 2.367%
4206 | 16-85 | -84.7662 | 16.3575 | 1603.6363 | 151.9889 | 183.4643 | 225.5076 | 261.912 | 304.196 | 2.257%
4207 | 16-85 | -85.0375 | 16.3575 | 1621.6206 | 149.9346 | 181.6064 | 223.6809 | 259.794 | 301.7407 | 2.138%
4208 | 16-85.5 | -85.3089 | 16.3575 | 1639.6045 | 147.8256 | 179.6109 | 221.7482 | 257.5549 | 299.1232 | 2.02%
4209 | 16-85.5 | -85.5802 | 16.3575 | 1657.588 | 145.7332 | 177.5573 | 219.7767 | 255.3282 | 296.5176 | 1.909%
4210 | 16-86 | -85.8515 | 16.3575 | 1675.5711 | 144.0362 | 176.1457 | 218.3936 | 253.7626 | 294.747 | 1.827%
4211 | 16-86 | -86.1228 | 16.3575 | 1693.5536 | 142.6973 | 175.2456 | 217.506 | 252.8528 | 293.8323 | 1.768%
4212 | 16-86.5 | -86.3941 | 16.3575 | 1711.5357 | 141.6363 | 174.6635 | 216.9964 | 252.4567 | 293.6044 | 1.725%
4213 | 16-86.5 | -86.6655 | 16.3575 | 1729.5173 | 139.6411 | 173.2901 | 215.4131 | 250.649 | 291.5424 | 1.644%
4214 | 16-87 | -86.9368 | 16.3575 | 1747.4984 | 136.889 | 170.9243 | 212.9597 | 247.7243 | 288.0588 | 1.533%
4215 | 16-87 | -87.2081 | 16.3575 | 1765.479 | 133.5576 | 167.6536 | 209.8131 | 243.9232 | 283.4754 | 1.404%
4216 | 16-87.5 | -87.4794 | 16.3575 | 1783.459 | 130.1373 | 164.2087 | 206.5502 | 239.9739 | 278.7047 | 1.282%
4217 | 16-88 | -87.7507 | 16.3575 | 1801.4385 | 126.7169 | 160.6832 | 203.2678 | 236.0014 | 273.9065 | 1.17%
4218 | 16-88 | -88.0221 | 16.3575 | 1819.4173 | 123.3343 | 157.1388 | 200.0022 | 232.055 | 269.1461 | 1.068%
4219 | 16-88.5 | -88.2934 | 16.3575 | 1837.3956 | 120.0504 | 153.6701 | 196.8188 | 228.2081 | 264.5054 | 0.9783%
4220 | 16-88.5 | -88.5647 | 16.3575 | 1855.3733 | 117.0375 | 150.5101 | 193.9587 | 224.7764 | 260.3925 | 0.9032%
4221 | 16-89 | -88.836 | 16.3575 | 1873.3503 | 114.279 | 147.638 | 191.3997 | 221.7004 | 256.7237 | 0.8403%
4222 | 16-89 | -89.1074 | 16.3575 | 1891.3267 | 111.6651 | 144.8879 | 189.0071 | 218.7601 | 253.2154 | 0.785%
4223 | 16-89.5 | -89.3787 | 16.3575 | 1909.3024 | 108.8386 | 141.656 | 186.1626 | 215.3562 | 249.1271 | 0.7271%
4224 | 16-89.5 | -89.65 | 16.3575 | 1927.2775 | 105.7492 | 137.9931 | 182.8389 | 211.3554 | 244.2503 | 0.6672%
4225 | 16-90 | -89.9213 | 16.3575 | 1945.2518 | 102.5047 | 134.1394 | 179.1886 | 206.9364 | 238.8061 | 0.6086%
4226 | 16-90 | -90.1926 | 16.3575 | 1963.2255 | 100.3478 | 131.2603 | 176.7053 | 204.0794 | 235.3939 | 0.5717%
4227 | 16-90.5 | -90.464 | 16.3575 | 1981.1985 | 99.2353 | 129.7324 | 175.4383 | 202.7664 | 233.9559 | 0.5542%
4228 | 16-90.5 | -90.7353 | 16.3575 | 1999.1707 | 99.0773 | 129.5517 | 175.3466 | 202.8571 | 234.2688 | 0.5531%
4229 | 17-50 | -50.0371 | 16.6288 | 708.9268 | 150.2589 | 181.0339 | 216.2535 | 247.3823 | 282.9937 | 2.214%
4230 | 17-50.5 | -50.3084 | 16.6288 | 691.043 | 150.5459 | 181.2764 | 216.6978 | 248.0242 | 283.881 | 2.229%
4231 | 17-50.5 | -50.5797 | 16.6288 | 673.1656 | 150.771 | 181.482 | 217.0958 | 248.6116 | 284.7043 | 2.241%
4232 | 17-51 | -50.851 | 16.6288 | 655.2954 | 150.9691 | 181.6738 | 217.4807 | 249.1873 | 285.518 | 2.252%
4233 | 17-51 | -51.1224 | 16.6288 | 637.4329 | 151.1795 | 181.8776 | 217.8904 | 249.8005 | 286.3856 | 2.263%
4234 | 17-51.5 | -51.3937 | 16.6288 | 619.5788 | 151.3534 | 182.0563 | 218.2651 | 250.3695 | 287.1981 | 2.272%
4235 | 17-51.5 | -51.665 | 16.6288 | 601.7338 | 151.5162 | 182.228 | 218.6354 | 250.9372 | 288.0135 | 2.28%
4236 | 17-52 | -51.9363 | 16.6288 | 583.899 | 151.6927 | 182.4108 | 219.0315 | 251.5455 | 288.8884 | 2.288%
4237 | 17-52 | -52.2077 | 16.6288 | 566.0753 | 151.8233 | 182.5556 | 219.3681 | 252.0738 | 289.658 | 2.294%
4238 | 17-52.5 | -52.479 | 16.6288 | 548.2637 | 151.9416 | 182.6851 | 219.6812 | 252.5705 | 290.3862 | 2.3%
4239 | 17-53 | -52.7503 | 16.6288 | 530.4655 | 152.0695 | 182.815 | 219.995 | 253.0684 | 291.1161 | 2.305%
4240 | 17-53 | -53.0216 | 16.6288 | 512.6822 | 152.1464 | 182.901 | 220.2422 | 253.4776 | 291.7305 | 2.308%
4241 | 17-53.5 | -53.2929 | 16.6288 | 494.9154 | 152.2202 | 182.9791 | 220.4794 | 253.8752 | 292.3312 | 2.31%
4242 | 17-53.5 | -53.5643 | 16.6288 | 477.167 | 152.3145 | 183.0674 | 220.7328 | 254.2947 | 292.9613 | 2.313%
4243 | 17-54 | -53.8356 | 16.6288 | 459.4391 | 152.381 | 183.1321 | 220.9472 | 254.6605 | 293.5192 | 2.315%
4244 | 17-54 | -54.1069 | 16.6288 | 441.7343 | 152.4644 | 183.2034 | 221.1656 | 255.0274 | 294.0746 | 2.318%
4245 | 17-54.5 | -54.3782 | 16.6288 | 424.0554 | 152.5809 | 183.2931 | 221.4032 | 255.414 | 294.6502 | 2.323%
4246 | 17-54.5 | -54.6495 | 16.6288 | 406.4059 | 152.6953 | 183.3766 | 221.6176 | 255.7604 | 295.1642 | 2.327%
4247 | 17-55 | -54.9209 | 16.6288 | 388.7897 | 152.8616 | 183.4959 | 221.8757 | 256.1577 | 295.7374 | 2.335%
4248 | 17-55 | -55.1922 | 16.6288 | 371.2118 | 153.087 | 183.6575 | 222.1851 | 256.6145 | 296.3799 | 2.347%
4249 | 17-55.5 | -55.4635 | 16.6288 | 353.6779 | 153.2986 | 183.8008 | 222.4392 | 256.9785 | 296.8819 | 2.358%
4250 | 17-55.5 | -55.7348 | 16.6288 | 336.1947 | 153.5623 | 183.9805 | 222.7298 | 257.3784 | 297.418 | 2.373%
4251 | 17-56 | -56.0061 | 16.6288 | 318.7708 | 153.8824 | 184.2015 | 223.0645 | 257.824 | 298.0013 | 2.391%
4252 | 17-56.5 | -56.2775 | 16.6288 | 301.4164 | 154.1984 | 184.4161 | 223.3682 | 258.2138 | 298.4969 | 2.409%
4253 | 17-56.5 | -56.5488 | 16.6288 | 284.1443 | 154.5777 | 184.6743 | 223.7138 | 258.6424 | 299.0261 | 2.432%
4254 | 17-57 | -56.8201 | 16.6288 | 266.9706 | 155.0197 | 184.9785 | 224.1014 | 259.1075 | 299.584 | 2.46%
4255 | 17-57 | -57.0914 | 16.6288 | 249.9154 | 155.4921 | 185.296 | 224.4758 | 259.532 | 300.0655 | 2.49%
4256 | 17-57.5 | -57.3628 | 16.6288 | 233.005 | 156.0502 | 185.6678 | 224.9002 | 260.0002 | 300.5814 | 2.526%
4257 | 17-57.5 | -57.6341 | 16.6288 | 216.2732 | 156.6891 | 186.0912 | 225.3696 | 260.5054 | 301.1226 | 2.569%
4258 | 17-58 | -57.9054 | 16.6288 | 199.765 | 157.3719 | 186.5365 | 225.8399 | 260.9891 | 301.6129 | 2.615%
4259 | 17-58 | -58.1767 | 16.6288 | 183.5408 | 158.1354 | 187.0333 | 226.3579 | 261.5152 | 302.1375 | 2.669%
4260 | 17-58.5 | -58.448 | 16.6288 | 167.6831 | 158.9492 | 187.5639 | 226.8978 | 262.0497 | 302.6523 | 2.729%
4261 | 17-58.5 | -58.7194 | 16.6288 | 152.3064 | 159.7605 | 188.0843 | 227.3984 | 262.5153 | 303.0601 | 2.79%
4262 | 17-59 | -58.9907 | 16.6288 | 137.5721 | 160.6382 | 188.6593 | 227.969 | 263.0654 | 303.5696 | 2.858%
4263 | 17-59.5 | -59.262 | 16.6288 | 123.71 | 161.5819 | 189.3045 | 228.6289 | 263.7221 | 304.2065 | 2.933%
4264 | 17-59.5 | -59.5333 | 16.6288 | 111.0473 | 162.6019 | 190.0586 | 229.4293 | 264.5486 | 305.0478 | 3.018%
4265 | 17-60 | -59.8046 | 16.6288 | 100.0404 | 163.7494 | 190.9762 | 230.4533 | 265.656 | 306.2397 | 3.116%
4266 | 17-60 | -60.076 | 16.6288 | 91.2903 | 164.9175 | 191.9364 | 231.5366 | 266.8387 | 307.5264 | 3.219%
4267 | 17-60.5 | -60.3473 | 16.6288 | 85.4927 | 165.9509 | 192.7508 | 232.4261 | 267.7823 | 308.5196 | 3.314%
4268 | 17-60.5 | -60.6186 | 16.6288 | 83.2668 | 166.8729 | 193.4557 | 233.183 | 268.5729 | 309.3364 | 3.402%
4269 | 17-61 | -60.8899 | 16.6288 | 84.8938 | 167.698 | 194.0821 | 233.8464 | 269.2568 | 310.0314 | 3.482%
4270 | 17-61 | -61.1613 | 16.6288 | 90.1656 | 168.4585 | 194.679 | 234.4797 | 269.9109 | 310.6978 | 3.559%
4271 | 17-61.5 | -61.4326 | 16.6288 | 98.4986 | 169.1824 | 195.2784 | 235.132 | 270.601 | 311.422 | 3.634%
4272 | 17-61.5 | -61.7039 | 16.6288 | 109.1941 | 169.8363 | 195.8495 | 235.7636 | 271.2788 | 312.1454 | 3.703%
4273 | 17-62 | -61.9752 | 16.6288 | 121.6305 | 170.4142 | 196.3783 | 236.3567 | 271.9232 | 312.843 | 3.766%
4274 | 17-62 | -62.2465 | 16.6288 | 135.3287 | 170.9638 | 196.9127 | 236.9808 | 272.6246 | 313.6305 | 3.825%
4275 | 17-62.5 | -62.5179 | 16.6288 | 149.9433 | 171.5085 | 197.4862 | 237.6794 | 273.4356 | 314.5719 | 3.884%
4276 | 17-63 | -62.7892 | 16.6288 | 165.2312 | 172.0625 | 198.1137 | 238.4715 | 274.3792 | 315.695 | 3.944%
4277 | 17-63 | -63.0605 | 16.6288 | 181.0219 | 172.6125 | 198.7628 | 239.3173 | 275.4091 | 316.946 | 4.002%
4278 | 17-63.5 | -63.3318 | 16.6288 | 197.1946 | 173.0008 | 199.2248 | 239.9261 | 276.156 | 317.8596 | 4.042%
4279 | 17-63.5 | -63.6031 | 16.6288 | 213.6627 | 173.2103 | 199.475 | 240.2607 | 276.5703 | 318.3702 | 4.064%
4280 | 17-64 | -63.8745 | 16.6288 | 230.3626 | 173.395 | 199.708 | 240.5874 | 276.9868 | 318.8961 | 4.082%
4281 | 17-64 | -64.1458 | 16.6288 | 247.2475 | 173.5836 | 199.9579 | 240.9491 | 277.4559 | 319.4969 | 4.1%
4282 | 17-64.5 | -64.4171 | 16.6288 | 264.2818 | 173.7636 | 200.2096 | 241.3259 | 277.9539 | 320.1441 | 4.116%
4283 | 17-64.5 | -64.6884 | 16.6288 | 281.4384 | 173.9001 | 200.42 | 241.664 | 278.4169 | 320.762 | 4.126%
4284 | 17-65 | -64.9598 | 16.6288 | 298.6961 | 173.9691 | 200.5516 | 241.8994 | 278.7549 | 321.2285 | 4.129%
4285 | 17-65 | -65.2311 | 16.6288 | 316.0385 | 173.9846 | 200.6168 | 242.0438 | 278.9785 | 321.5519 | 4.127%
4286 | 17-65.5 | -65.5024 | 16.6288 | 333.4522 | 173.9728 | 200.6479 | 242.1418 | 279.144 | 321.8033 | 4.122%
4287 | 17-66 | -65.7737 | 16.6288 | 350.9267 | 173.909 | 200.6169 | 242.1585 | 279.2105 | 321.9342 | 4.111%
4288 | 17-66 | -66.045 | 16.6288 | 368.4531 | 173.7548 | 200.4783 | 242.0391 | 279.1147 | 321.8722 | 4.091%
4289 | 17-66.5 | -66.3164 | 16.6288 | 386.0246 | 173.4824 | 200.1999 | 241.7468 | 278.8156 | 321.5709 | 4.057%
4290 | 17-66.5 | -66.5877 | 16.6288 | 403.635 | 173.023 | 199.6869 | 241.1352 | 278.1167 | 320.7718 | 4.005%
4291 | 17-67 | -66.859 | 16.6288 | 421.2795 | 172.5154 | 199.1191 | 240.4531 | 277.3326 | 319.8699 | 3.948%
4292 | 17-67 | -67.1303 | 16.6288 | 438.9541 | 172.0531 | 198.6383 | 239.8995 | 276.7176 | 319.1875 | 3.896%
4293 | 17-67.5 | -67.4016 | 16.6288 | 456.655 | 171.639 | 198.229 | 239.4406 | 276.219 | 318.6479 | 3.85%
4294 | 17-67.5 | -67.673 | 16.6288 | 474.3795 | 171.2439 | 197.8501 | 239.0225 | 275.7713 | 318.1714 | 3.806%
4295 | 17-68 | -67.9443 | 16.6288 | 492.1248 | 170.8521 | 197.48 | 238.6194 | 275.3445 | 317.723 | 3.763%
4296 | 17-68 | -68.2156 | 16.6288 | 509.8889 | 170.4166 | 197.0641 | 238.151 | 274.834 | 317.1684 | 3.717%
4297 | 17-68.5 | -68.4869 | 16.6288 | 527.6697 | 169.9557 | 196.633 | 237.6715 | 274.3168 | 316.6135 | 3.668%
4298 | 17-69 | -68.7583 | 16.6288 | 545.4656 | 169.4808 | 196.2026 | 237.2092 | 273.8339 | 316.1147 | 3.618%
4299 | 17-69 | -69.0296 | 16.6288 | 563.2752 | 168.9242 | 195.695 | 236.6299 | 273.1952 | 315.4122 | 3.562%
4300 | 17-69.5 | -69.3009 | 16.6288 | 581.0971 | 168.3094 | 195.135 | 235.9624 | 272.4331 | 314.5421 | 3.503%
4301 | 17-69.5 | -69.5722 | 16.6288 | 598.9302 | 167.65 | 194.5336 | 235.2196 | 271.562 | 313.5211 | 3.442%
4302 | 17-70 | -69.8435 | 16.6288 | 616.7736 | 166.9415 | 193.8733 | 234.3693 | 270.5352 | 312.2836 | 3.379%
4303 | 17-70 | -70.1149 | 16.6288 | 634.6263 | 166.2566 | 193.2489 | 233.5591 | 269.552 | 311.0936 | 3.32%
4304 | 17-70.5 | -70.3862 | 16.6288 | 652.4876 | 165.618 | 192.6838 | 232.826 | 268.6624 | 310.0172 | 3.265%
4305 | 17-70.5 | -70.6575 | 16.6288 | 670.3567 | 165.0392 | 192.1519 | 232.1039 | 267.7604 | 308.8973 | 3.218%
4306 | 17-71 | -70.9288 | 16.6288 | 688.2329 | 164.524 | 191.6677 | 231.4279 | 266.9015 | 307.8157 | 3.176%
4307 | 17-71 | -71.2001 | 16.6288 | 706.1158 | 164.0712 | 191.2277 | 230.7971 | 266.0876 | 306.7781 | 3.141%
4308 | 17-71.5 | -71.4715 | 16.6288 | 724.0047 | 163.5911 | 190.7645 | 230.1116 | 265.1876 | 305.6144 | 3.105%
4309 | 17-71.5 | -71.7428 | 16.6288 | 741.8993 | 163.1409 | 190.3328 | 229.454 | 264.3109 | 304.4675 | 3.072%
4310 | 17-72 | -72.0141 | 16.6288 | 759.7991 | 162.7166 | 189.9254 | 228.8153 | 263.4467 | 303.3243 | 3.041%
4311 | 17-72.5 | -72.2854 | 16.6288 | 777.7037 | 162.2084 | 189.4628 | 228.0804 | 262.4459 | 301.9937 | 3.006%
4312 | 17-72.5 | -72.5568 | 16.6288 | 795.6127 | 161.6979 | 189.0239 | 227.3868 | 261.5038 | 300.7441 | 2.97%
4313 | 17-73 | -72.8281 | 16.6288 | 813.5259 | 161.2118 | 188.6214 | 226.754 | 260.647 | 299.6102 | 2.937%
4314 | 17-73 | -73.0994 | 16.6288 | 831.4428 | 160.803 | 188.2844 | 226.2178 | 259.9166 | 298.6395 | 2.909%
4315 | 17-73.5 | -73.3707 | 16.6288 | 849.3634 | 160.4892 | 188.0294 | 225.8082 | 259.3561 | 297.8921 | 2.888%
4316 | 17-73.5 | -73.642 | 16.6288 | 867.2872 | 160.2508 | 187.8369 | 225.4956 | 258.926 | 297.3164 | 2.872%
4317 | 17-74 | -73.9134 | 16.6288 | 885.2141 | 160.0194 | 187.6566 | 225.2079 | 258.5335 | 296.7939 | 2.856%
4318 | 17-74 | -74.1847 | 16.6288 | 903.1439 | 159.8081 | 187.5163 | 225.0161 | 258.293 | 296.4944 | 2.841%
4319 | 17-74.5 | -74.456 | 16.6288 | 921.0763 | 159.6012 | 187.3994 | 224.8904 | 258.1612 | 296.3576 | 2.825%
4320 | 17-74.5 | -74.7273 | 16.6288 | 939.0113 | 159.3689 | 187.2764 | 224.7726 | 258.0519 | 296.2618 | 2.807%
4321 | 17-75 | -74.9986 | 16.6288 | 956.9485 | 159.2121 | 187.2167 | 224.7657 | 258.1005 | 296.3826 | 2.794%
4322 | 17-75.5 | -75.27 | 16.6288 | 974.8879 | 159.1039 | 187.1963 | 224.8259 | 258.2433 | 296.6315 | 2.784%
4323 | 17-75.5 | -75.5413 | 16.6288 | 992.8293 | 159.0193 | 187.1893 | 224.9014 | 258.4033 | 296.8994 | 2.776%
4324 | 17-76 | -75.8126 | 16.6288 | 1010.7725 | 159.0844 | 187.2808 | 225.1151 | 258.739 | 297.3892 | 2.778%
4325 | 17-76 | -76.0839 | 16.6288 | 1028.7175 | 159.2656 | 187.4458 | 225.4224 | 259.1869 | 298.0127 | 2.789%
4326 | 17-76.5 | -76.3553 | 16.6288 | 1046.6641 | 159.5013 | 187.6386 | 225.747 | 259.6406 | 298.6267 | 2.803%
4327 | 17-76.5 | -76.6266 | 16.6288 | 1064.6122 | 159.7461 | 187.8335 | 226.0584 | 260.0655 | 299.1919 | 2.82%
4328 | 17-77 | -76.8979 | 16.6288 | 1082.5617 | 159.9776 | 188.0167 | 226.3364 | 260.4351 | 299.6742 | 2.835%
4329 | 17-77 | -77.1692 | 16.6288 | 1100.5126 | 160.1954 | 188.1888 | 226.5821 | 260.7514 | 300.0765 | 2.851%
4330 | 17-77.5 | -77.4405 | 16.6288 | 1118.4646 | 160.4739 | 188.4045 | 226.8739 | 261.1148 | 300.5265 | 2.871%
4331 | 17-77.5 | -77.7119 | 16.6288 | 1136.4177 | 160.7888 | 188.6447 | 227.1805 | 261.4827 | 300.9671 | 2.895%
4332 | 17-78 | -77.9832 | 16.6288 | 1154.3719 | 161.1371 | 188.9084 | 227.5051 | 261.8624 | 301.4109 | 2.922%
4333 | 17-78.5 | -78.2545 | 16.6288 | 1172.327 | 161.5589 | 189.2369 | 227.9192 | 262.3551 | 301.9965 | 2.955%
4334 | 17-78.5 | -78.5258 | 16.6288 | 1190.283 | 162.003 | 189.5876 | 228.3526 | 262.8634 | 302.5925 | 2.99%
4335 | 17-79 | -78.7971 | 16.6288 | 1208.2398 | 162.4579 | 189.9515 | 228.7932 | 263.3726 | 303.181 | 3.027%
4336 | 17-79 | -79.0685 | 16.6288 | 1226.1974 | 162.9639 | 190.3707 | 229.3129 | 263.9838 | 303.8994 | 3.069%
4337 | 17-79.5 | -79.3398 | 16.6288 | 1244.1556 | 163.4759 | 190.8097 | 229.8586 | 264.6268 | 304.6565 | 3.112%
4338 | 17-79.5 | -79.6111 | 16.6288 | 1262.1145 | 163.9961 | 191.2733 | 230.4456 | 265.3274 | 305.4918 | 3.156%
4339 | 17-80 | -79.8824 | 16.6288 | 1280.0739 | 164.5644 | 191.801 | 231.1429 | 266.1837 | 306.5395 | 3.203%
4340 | 17-80 | -80.1537 | 16.6288 | 1298.0338 | 165.1104 | 192.3253 | 231.8564 | 267.0768 | 307.6502 | 3.248%
4341 | 17-80.5 | -80.4251 | 16.6288 | 1315.9942 | 165.6145 | 192.827 | 232.5605 | 267.9743 | 308.7837 | 3.29%
4342 | 17-80.5 | -80.6964 | 16.6288 | 1333.955 | 166.0918 | 193.3224 | 233.2781 | 268.9061 | 309.9784 | 3.328%
4343 | 17-81 | -80.9677 | 16.6288 | 1351.9161 | 166.4943 | 193.7725 | 233.9556 | 269.8044 | 311.1494 | 3.36%
4344 | 17-81 | -81.239 | 16.6288 | 1369.8776 | 166.8209 | 194.1818 | 234.6021 | 270.6829 | 312.3161 | 3.384%
4345 | 17-81.5 | -81.5104 | 16.6288 | 1387.8393 | 167.082 | 194.5656 | 235.2409 | 271.5734 | 313.521 | 3.402%
4346 | 17-82 | -81.7817 | 16.6288 | 1405.8013 | 167.1037 | 194.7683 | 235.6418 | 272.1726 | 314.3705 | 3.399%
4347 | 17-82 | -82.053 | 16.6288 | 1423.7634 | 166.8824 | 194.7885 | 235.8133 | 272.4992 | 314.8962 | 3.376%
4348 | 17-82.5 | -82.3243 | 16.6288 | 1441.7257 | 166.4514 | 194.6441 | 235.816 | 272.6404 | 315.2189 | 3.334%
4349 | 17-82.5 | -82.5956 | 16.6288 | 1459.688 | 165.8598 | 194.346 | 235.6596 | 272.5994 | 315.3333 | 3.279%
4350 | 17-83 | -82.867 | 16.6288 | 1477.6505 | 165.1512 | 193.9409 | 235.3972 | 272.4449 | 315.3269 | 3.214%
4351 | 17-83 | -83.1383 | 16.6288 | 1495.613 | 164.3488 | 193.453 | 235.0631 | 272.2224 | 315.2594 | 3.142%
4352 | 17-83.5 | -83.4096 | 16.6288 | 1513.5755 | 163.3839 | 192.7977 | 234.5205 | 271.7379 | 314.8648 | 3.059%
4353 | 17-83.5 | -83.6809 | 16.6288 | 1531.5379 | 162.3098 | 192.0303 | 233.843 | 271.0836 | 314.2581 | 2.971%
4354 | 17-84 | -83.9522 | 16.6288 | 1549.5003 | 161.1602 | 191.1884 | 233.0838 | 270.3304 | 313.5318 | 2.88%
4355 | 17-84 | -84.2236 | 16.6288 | 1567.4626 | 159.8489 | 190.1879 | 232.1387 | 269.346 | 312.5196 | 2.781%
4356 | 17-84.5 | -84.4949 | 16.6288 | 1585.4248 | 158.4061 | 189.05 | 231.0468 | 268.1809 | 311.2858 | 2.676%
4357 | 17-85 | -84.7662 | 16.6288 | 1603.3868 | 156.8488 | 187.7899 | 229.825 | 266.8569 | 309.8584 | 2.568%
4358 | 17-85 | -85.0375 | 16.6288 | 1621.3487 | 155.039 | 186.2318 | 228.2616 | 265.0799 | 307.8399 | 2.448%
4359 | 17-85.5 | -85.3089 | 16.6288 | 1639.3103 | 153.1433 | 184.5265 | 226.5865 | 263.157 | 305.6336 | 2.328%
4360 | 17-85.5 | -85.5802 | 16.6288 | 1657.2717 | 151.2204 | 182.7389 | 224.8507 | 261.2005 | 303.3874 | 2.21%
4361 | 17-86 | -85.8515 | 16.6288 | 1675.2329 | 149.5562 | 181.4356 | 223.5148 | 259.7152 | 301.7395 | 2.118%
4362 | 17-86 | -86.1228 | 16.6288 | 1693.1938 | 148.147 | 180.5336 | 222.5671 | 258.751 | 300.7795 | 2.046%
4363 | 17-86.5 | -86.3941 | 16.6288 | 1711.1543 | 146.9268 | 179.8544 | 221.9059 | 258.1857 | 300.3628 | 1.986%
4364 | 17-86.5 | -86.6655 | 16.6288 | 1729.1146 | 144.7451 | 178.3732 | 220.1519 | 256.1859 | 298.0847 | 1.884%
4365 | 17-87 | -86.9368 | 16.6288 | 1747.0745 | 141.7715 | 175.8725 | 217.4984 | 253.0331 | 294.3412 | 1.747%
4366 | 17-87 | -87.2081 | 16.6288 | 1765.034 | 138.1827 | 172.4235 | 214.1183 | 248.9629 | 289.4475 | 1.589%
4367 | 17-87.5 | -87.4794 | 16.6288 | 1782.9931 | 134.4709 | 168.7514 | 210.5881 | 244.7028 | 284.3158 | 1.44%
4368 | 17-88 | -87.7507 | 16.6288 | 1800.9518 | 130.7344 | 164.9629 | 207.0157 | 240.3926 | 279.1242 | 1.303%
4369 | 17-88 | -88.0221 | 16.6288 | 1818.9101 | 127.0108 | 161.1187 | 203.4349 | 236.0775 | 273.9326 | 1.179%
4370 | 17-88.5 | -88.2934 | 16.6288 | 1836.8679 | 123.3633 | 157.316 | 199.9104 | 231.8296 | 268.8203 | 1.069%
4371 | 17-88.5 | -88.5647 | 16.6288 | 1854.8252 | 119.9504 | 153.7648 | 196.6645 | 227.9407 | 264.1661 | 0.9766%
4372 | 17-89 | -88.836 | 16.6288 | 1872.782 | 116.7551 | 150.4439 | 193.6572 | 224.3523 | 259.8874 | 0.8976%
4373 | 17-89 | -89.1074 | 16.6288 | 1890.7383 | 113.6673 | 147.1879 | 190.7538 | 220.8431 | 255.6965 | 0.8274%
4374 | 17-89.5 | -89.3787 | 16.6288 | 1908.6941 | 110.4231 | 143.4933 | 187.5021 | 216.9569 | 251.0374 | 0.7577%
4375 | 17-89.5 | -89.65 | 16.6288 | 1926.6493 | 106.9811 | 139.4281 | 183.8485 | 212.5741 | 245.7178 | 0.6886%
4376 | 17-90 | -89.9213 | 16.6288 | 1944.6039 | 103.4434 | 135.2304 | 179.9417 | 207.8669 | 239.9498 | 0.6233%
4377 | 17-90 | -90.1926 | 16.6288 | 1962.5579 | 100.9885 | 131.9763 | 177.1991 | 204.7191 | 236.2119 | 0.5809%
4378 | 17-90.5 | -90.464 | 16.6288 | 1980.5113 | 99.5671 | 130.0482 | 175.6648 | 203.1063 | 234.4378 | 0.5586%
4379 | 17-90.5 | -90.7353 | 16.6288 | 1998.4641 | 99.0784 | 129.4562 | 175.2857 | 202.8719 | 234.3829 | 0.5528%
4380 | 17-50 | -50.0371 | 16.9002 | 710.8868 | 151.0424 | 181.5706 | 216.8399 | 248.0058 | 283.6531 | 2.263%
4381 | 17-50.5 | -50.3084 | 16.9002 | 693.0787 | 151.4002 | 181.8514 | 217.3242 | 248.6886 | 284.5814 | 2.283%
4382 | 17-50.5 | -50.5797 | 16.9002 | 675.2805 | 151.696 | 182.0962 | 217.7649 | 249.3212 | 285.4523 | 2.3%
4383 | 17-51 | -50.851 | 16.9002 | 657.4929 | 151.9648 | 182.3272 | 218.193 | 249.9429 | 286.3147 | 2.314%
4384 | 17-51 | -51.1224 | 16.9002 | 639.717 | 152.2455 | 182.5699 | 218.6449 | 250.6007 | 287.2289 | 2.33%
4385 | 17-51.5 | -51.3937 | 16.9002 | 621.9536 | 152.4846 | 182.7848 | 219.0589 | 251.2112 | 288.0848 | 2.343%
4386 | 17-51.5 | -51.665 | 16.9002 | 604.204 | 152.7079 | 182.9907 | 219.4675 | 251.8206 | 288.9453 | 2.355%
4387 | 17-52 | -51.9363 | 16.9002 | 586.4694 | 152.941 | 183.2066 | 219.9028 | 252.4733 | 289.8706 | 2.367%
4388 | 17-52 | -52.2077 | 16.9002 | 568.7513 | 153.1221 | 183.3823 | 220.2781 | 253.0472 | 290.694 | 2.376%
4389 | 17-52.5 | -52.479 | 16.9002 | 551.0513 | 153.287 | 183.5427 | 220.6327 | 253.5955 | 291.4858 | 2.384%
4390 | 17-53 | -52.7503 | 16.9002 | 533.3712 | 153.4588 | 183.7047 | 220.9931 | 254.1537 | 292.2929 | 2.392%
4391 | 17-53 | -53.0216 | 16.9002 | 515.7132 | 153.576 | 183.8228 | 221.2885 | 254.6268 | 292.9902 | 2.397%
4392 | 17-53.5 | -53.2929 | 16.9002 | 498.0796 | 153.6874 | 183.9327 | 221.5733 | 255.0871 | 293.6721 | 2.401%
4393 | 17-53.5 | -53.5643 | 16.9002 | 480.473 | 153.817 | 184.0521 | 221.8726 | 255.5667 | 294.3797 | 2.407%
4394 | 17-54 | -53.8356 | 16.9002 | 462.8968 | 153.9127 | 184.1443 | 222.1283 | 255.987 | 295.0084 | 2.41%
4395 | 17-54 | -54.1069 | 16.9002 | 445.3543 | 154.0195 | 184.24 | 222.3844 | 256.4046 | 295.6306 | 2.414%
4396 | 17-54.5 | -54.3782 | 16.9002 | 427.8499 | 154.1535 | 184.3508 | 222.656 | 256.8378 | 296.2683 | 2.42%
4397 | 17-54.5 | -54.6495 | 16.9002 | 410.3885 | 154.2797 | 184.4524 | 222.9019 | 257.2287 | 296.8429 | 2.425%
4398 | 17-55 | -54.9209 | 16.9002 | 392.9758 | 154.457 | 184.5894 | 223.1908 | 257.6698 | 297.4761 | 2.434%
4399 | 17-55 | -55.1922 | 16.9002 | 375.6185 | 154.6939 | 184.769 | 223.5313 | 258.1707 | 298.1788 | 2.447%
4400 | 17-55.5 | -55.4635 | 16.9002 | 358.3249 | 154.9183 | 184.9309 | 223.819 | 258.5833 | 298.7482 | 2.459%
4401 | 17-55.5 | -55.7348 | 16.9002 | 341.1046 | 155.1978 | 185.1305 | 224.1469 | 259.0376 | 299.3604 | 2.475%
4402 | 17-56 | -56.0061 | 16.9002 | 323.9694 | 155.5325 | 185.3719 | 224.5212 | 259.5421 | 300.0268 | 2.494%
4403 | 17-56.5 | -56.2775 | 16.9002 | 306.9335 | 155.8585 | 185.6028 | 224.8603 | 259.9864 | 300.601 | 2.514%
4404 | 17-56.5 | -56.5488 | 16.9002 | 290.0144 | 156.2423 | 185.8743 | 225.2399 | 260.4698 | 301.2117 | 2.538%
4405 | 17-57 | -56.8201 | 16.9002 | 273.234 | 156.6814 | 186.1878 | 225.6588 | 260.9887 | 301.8519 | 2.566%
4406 | 17-57 | -57.0914 | 16.9002 | 256.6194 | 157.1428 | 186.508 | 226.0569 | 261.4582 | 302.4058 | 2.596%
4407 | 17-57.5 | -57.3628 | 16.9002 | 240.205 | 157.6838 | 186.8796 | 226.5011 | 261.9669 | 302.9889 | 2.632%
4408 | 17-57.5 | -57.6341 | 16.9002 | 224.035 | 158.2985 | 187.2995 | 226.9865 | 262.5082 | 303.5921 | 2.675%
4409 | 17-58 | -57.9054 | 16.9002 | 208.1662 | 158.9507 | 187.7374 | 227.467 | 263.0204 | 304.1344 | 2.721%
4410 | 17-58 | -58.1767 | 16.9002 | 192.6733 | 159.6766 | 188.2236 | 227.989 | 263.5658 | 304.6982 | 2.774%
4411 | 17-58.5 | -58.448 | 16.9002 | 177.6545 | 160.4465 | 188.7404 | 228.5265 | 264.11 | 305.2386 | 2.832%
4412 | 17-58.5 | -58.7194 | 16.9002 | 163.2408 | 161.2095 | 189.2435 | 229.0164 | 264.5724 | 305.6531 | 2.892%
4413 | 17-59 | -58.9907 | 16.9002 | 149.6072 | 162.0335 | 189.7977 | 229.5668 | 265.1031 | 306.1452 | 2.958%
4414 | 17-59.5 | -59.262 | 16.9002 | 136.987 | 162.9187 | 190.4193 | 230.1981 | 265.7269 | 306.7439 | 3.032%
4415 | 17-59.5 | -59.5333 | 16.9002 | 125.6857 | 163.8803 | 191.1484 | 230.9643 | 266.5105 | 307.5316 | 3.115%
4416 | 17-60 | -59.8046 | 16.9002 | 116.0892 | 164.9731 | 192.0444 | 231.956 | 267.5752 | 308.668 | 3.212%
4417 | 17-60 | -60.076 | 16.9002 | 108.6502 | 166.0911 | 192.9858 | 233.0077 | 268.7136 | 309.8946 | 3.314%
4418 | 17-60.5 | -60.3473 | 16.9002 | 103.8334 | 167.0801 | 193.783 | 233.8643 | 269.6087 | 310.8195 | 3.408%
4419 | 17-60.5 | -60.6186 | 16.9002 | 102.011 | 167.9631 | 194.4753 | 234.5929 | 270.3552 | 311.5721 | 3.495%
4420 | 17-61 | -60.8899 | 16.9002 | 103.3416 | 168.7542 | 195.0919 | 235.2305 | 270.997 | 312.2044 | 3.576%
4421 | 17-61 | -61.1613 | 16.9002 | 107.7083 | 169.4855 | 195.6803 | 235.8384 | 271.6086 | 312.8066 | 3.653%
4422 | 17-61.5 | -61.4326 | 16.9002 | 114.765 | 170.183 | 196.2728 | 236.4675 | 272.2588 | 313.4696 | 3.728%
4423 | 17-61.5 | -61.7039 | 16.9002 | 124.0537 | 170.8152 | 196.8386 | 237.0775 | 272.8985 | 314.1338 | 3.798%
4424 | 17-62 | -61.9752 | 16.9002 | 135.1146 | 171.3763 | 197.3636 | 237.6515 | 273.5083 | 314.7768 | 3.861%
4425 | 17-62 | -62.2465 | 16.9002 | 147.5499 | 171.9109 | 197.8963 | 238.2614 | 274.1824 | 315.5205 | 3.922%
4426 | 17-62.5 | -62.5179 | 16.9002 | 161.0413 | 172.4431 | 198.4695 | 238.95 | 274.9735 | 316.4292 | 3.981%
4427 | 17-63 | -62.7892 | 16.9002 | 175.3452 | 172.9873 | 199.0979 | 239.7362 | 275.9041 | 317.5302 | 4.041%
4428 | 17-63 | -63.0605 | 16.9002 | 190.2786 | 173.5287 | 199.7493 | 240.5794 | 276.9266 | 318.7674 | 4.1%
4429 | 17-63.5 | -63.3318 | 16.9002 | 205.7043 | 173.9109 | 200.2141 | 241.1872 | 277.6685 | 319.6707 | 4.141%
4430 | 17-63.5 | -63.6031 | 16.9002 | 221.5194 | 174.1177 | 200.4687 | 241.5235 | 278.0817 | 320.1764 | 4.163%
4431 | 17-64 | -63.8745 | 16.9002 | 237.6463 | 174.3032 | 200.71 | 241.8587 | 278.5065 | 320.7104 | 4.182%
4432 | 17-64 | -64.1458 | 16.9002 | 254.0254 | 174.4965 | 200.9709 | 242.2343 | 278.9923 | 321.3315 | 4.201%
4433 | 17-64.5 | -64.4171 | 16.9002 | 270.6111 | 174.6856 | 201.2368 | 242.6314 | 279.5165 | 322.0121 | 4.218%
4434 | 17-64.5 | -64.6884 | 16.9002 | 287.3674 | 174.8357 | 201.4664 | 242.9985 | 280.0181 | 322.6807 | 4.229%
4435 | 17-65 | -64.9598 | 16.9002 | 304.2663 | 174.9212 | 201.6172 | 243.2638 | 280.3964 | 323.2004 | 4.234%
4436 | 17-65 | -65.2311 | 16.9002 | 321.2851 | 174.9536 | 201.6995 | 243.4348 | 280.6561 | 323.5717 | 4.233%
4437 | 17-65.5 | -65.5024 | 16.9002 | 338.4057 | 174.9575 | 201.7451 | 243.5555 | 280.8525 | 323.864 | 4.228%
4438 | 17-66 | -65.7737 | 16.9002 | 355.6135 | 174.9082 | 201.7257 | 243.5916 | 280.9461 | 324.0319 | 4.219%
4439 | 17-66 | -66.045 | 16.9002 | 372.8962 | 174.7664 | 201.5958 | 243.4884 | 280.8739 | 324.0027 | 4.198%
4440 | 17-66.5 | -66.3164 | 16.9002 | 390.244 | 174.504 | 201.3239 | 243.2092 | 280.5947 | 323.7301 | 4.165%
4441 | 17-66.5 | -66.5877 | 16.9002 | 407.6485 | 174.0291 | 200.7806 | 242.5579 | 279.8471 | 322.8715 | 4.11%
4442 | 17-67 | -66.859 | 16.9002 | 425.1027 | 173.467 | 200.1382 | 241.7727 | 278.9329 | 321.8066 | 4.047%
4443 | 17-67 | -67.1303 | 16.9002 | 442.6007 | 172.8882 | 199.5396 | 241.0558 | 278.1109 | 320.864 | 3.983%
4444 | 17-67.5 | -67.4016 | 16.9002 | 460.1374 | 172.345 | 199.003 | 240.4214 | 277.3911 | 320.0473 | 3.923%
4445 | 17-67.5 | -67.673 | 16.9002 | 477.7087 | 171.8168 | 198.4944 | 239.8256 | 276.7198 | 319.2914 | 3.866%
4446 | 17-68 | -67.9443 | 16.9002 | 495.3107 | 171.2887 | 197.9928 | 239.2429 | 276.0678 | 318.5626 | 3.81%
4447 | 17-68 | -68.2156 | 16.9002 | 512.9402 | 170.7152 | 197.4425 | 238.5902 | 275.3252 | 317.718 | 3.75%
4448 | 17-68.5 | -68.4869 | 16.9002 | 530.5946 | 170.1168 | 196.8789 | 237.9296 | 274.5808 | 316.8796 | 3.689%
4449 | 17-69 | -68.7583 | 16.9002 | 548.2713 | 169.5065 | 196.3201 | 237.2939 | 273.882 | 316.1131 | 3.626%
4450 | 17-69 | -69.0296 | 16.9002 | 565.9683 | 168.7978 | 195.6752 | 236.5329 | 273.0198 | 315.1369 | 3.556%
4451 | 17-69.5 | -69.3009 | 16.9002 | 583.6837 | 168.015 | 194.9687 | 235.6737 | 272.0237 | 313.9821 | 3.482%
4452 | 17-69.5 | -69.5722 | 16.9002 | 601.4158 | 167.1726 | 194.211 | 234.7283 | 270.9066 | 312.6631 | 3.406%
4453 | 17-70 | -69.8435 | 16.9002 | 619.1631 | 166.292 | 193.4035 | 233.6883 | 269.6507 | 311.1494 | 3.328%
4454 | 17-70 | -70.1149 | 16.9002 | 636.9244 | 165.4696 | 192.6747 | 232.751 | 268.5199 | 309.788 | 3.258%
4455 | 17-70.5 | -70.3862 | 16.9002 | 654.6985 | 164.7427 | 192.0575 | 231.966 | 267.5803 | 308.665 | 3.196%
4456 | 17-70.5 | -70.6575 | 16.9002 | 672.4843 | 164.1823 | 191.5483 | 231.296 | 266.7596 | 307.6637 | 3.15%
4457 | 17-71 | -70.9288 | 16.9002 | 690.2809 | 163.7468 | 191.1288 | 230.7284 | 266.0522 | 306.7874 | 3.115%
4458 | 17-71 | -71.2001 | 16.9002 | 708.0875 | 163.421 | 190.786 | 230.2487 | 265.4423 | 306.0192 | 3.089%
4459 | 17-71.5 | -71.4715 | 16.9002 | 725.9033 | 163.0675 | 190.4159 | 229.7056 | 264.7325 | 305.105 | 3.062%
4460 | 17-71.5 | -71.7428 | 16.9002 | 743.7275 | 162.7412 | 190.0747 | 229.1853 | 264.0386 | 304.1972 | 3.038%
4461 | 17-72 | -72.0141 | 16.9002 | 761.5597 | 162.4293 | 189.7496 | 228.671 | 263.3398 | 303.27 | 3.016%
4462 | 17-72.5 | -72.2854 | 16.9002 | 779.3992 | 161.9749 | 189.3286 | 228.0032 | 262.4311 | 302.0626 | 2.985%
4463 | 17-72.5 | -72.5568 | 16.9002 | 797.2454 | 161.4823 | 188.9046 | 227.3374 | 261.5297 | 300.8697 | 2.95%
4464 | 17-73 | -72.8281 | 16.9002 | 815.098 | 161.0026 | 188.5072 | 226.7161 | 260.6908 | 299.762 | 2.917%
4465 | 17-73 | -73.0994 | 16.9002 | 832.9564 | 160.6689 | 188.2236 | 226.2527 | 260.0515 | 298.9046 | 2.895%
4466 | 17-73.5 | -73.3707 | 16.9002 | 850.8203 | 160.4769 | 188.0518 | 225.9532 | 259.6264 | 298.3229 | 2.883%
4467 | 17-73.5 | -73.642 | 16.9002 | 868.6893 | 160.3953 | 187.9627 | 225.7752 | 259.3599 | 297.9453 | 2.878%
4468 | 17-74 | -73.9134 | 16.9002 | 886.563 | 160.311 | 187.8765 | 225.6056 | 259.1074 | 297.5887 | 2.874%
4469 | 17-74 | -74.1847 | 16.9002 | 904.4413 | 160.203 | 187.7974 | 225.4854 | 258.9474 | 297.3794 | 2.866%
4470 | 17-74.5 | -74.456 | 16.9002 | 922.3236 | 160.0518 | 187.7079 | 225.3836 | 258.8352 | 297.2559 | 2.855%
4471 | 17-74.5 | -74.7273 | 16.9002 | 940.2099 | 159.8327 | 187.5818 | 225.2475 | 258.6917 | 297.1056 | 2.838%
4472 | 17-75 | -74.9986 | 16.9002 | 958.0998 | 159.6942 | 187.5251 | 225.2314 | 258.7183 | 297.1877 | 2.826%
4473 | 17-75.5 | -75.27 | 16.9002 | 975.9931 | 159.6124 | 187.5139 | 225.2918 | 258.8518 | 297.4146 | 2.818%
4474 | 17-75.5 | -75.5413 | 16.9002 | 993.8897 | 159.5726 | 187.5289 | 225.3863 | 259.0268 | 297.692 | 2.814%
4475 | 17-76 | -75.8126 | 16.9002 | 1011.7892 | 159.7479 | 187.6872 | 225.6816 | 259.4577 | 298.2924 | 2.824%
4476 | 17-76 | -76.0839 | 16.9002 | 1029.6915 | 160.0976 | 187.9618 | 226.1294 | 260.0746 | 299.119 | 2.847%
4477 | 17-76.5 | -76.3553 | 16.9002 | 1047.5965 | 160.5337 | 188.2892 | 226.6284 | 260.7397 | 299.9885 | 2.877%
4478 | 17-76.5 | -76.6266 | 16.9002 | 1065.5039 | 160.9291 | 188.5859 | 227.0714 | 261.3236 | 300.7454 | 2.904%
4479 | 17-77 | -76.8979 | 16.9002 | 1083.4136 | 161.2575 | 188.8374 | 227.4364 | 261.7976 | 301.3527 | 2.928%
4480 | 17-77 | -77.1692 | 16.9002 | 1101.3255 | 161.5299 | 189.0533 | 227.737 | 262.179 | 301.8321 | 2.948%
4481 | 17-77.5 | -77.4405 | 16.9002 | 1119.2395 | 161.8624 | 189.317 | 228.0914 | 262.6188 | 302.375 | 2.973%
4482 | 17-77.5 | -77.7119 | 16.9002 | 1137.1553 | 162.2284 | 189.6063 | 228.463 | 263.0665 | 302.9133 | 3.002%
4483 | 17-78 | -77.9832 | 16.9002 | 1155.073 | 162.6237 | 189.9181 | 228.85 | 263.5219 | 303.4489 | 3.034%
4484 | 17-78.5 | -78.2545 | 16.9002 | 1172.9923 | 163.0881 | 190.2939 | 229.3242 | 264.0865 | 304.1202 | 3.071%
4485 | 17-78.5 | -78.5258 | 16.9002 | 1190.9132 | 163.5712 | 190.6904 | 229.8129 | 264.6587 | 304.7902 | 3.111%
4486 | 17-79 | -78.7971 | 16.9002 | 1208.8355 | 164.0614 | 191.0974 | 230.3017 | 265.2203 | 305.4353 | 3.153%
4487 | 17-79 | -79.0685 | 16.9002 | 1226.7592 | 164.5962 | 191.5566 | 230.8617 | 265.8709 | 306.1913 | 3.199%
4488 | 17-79.5 | -79.3398 | 16.9002 | 1244.6842 | 165.1315 | 192.0316 | 231.4379 | 266.5378 | 306.9631 | 3.247%
4489 | 17-79.5 | -79.6111 | 16.9002 | 1262.6104 | 165.6727 | 192.5286 | 232.0478 | 267.2498 | 307.7941 | 3.295%
4490 | 17-80 | -79.8824 | 16.9002 | 1280.5377 | 166.2615 | 193.0892 | 232.7644 | 268.1108 | 308.827 | 3.348%
4491 | 17-80 | -80.1537 | 16.9002 | 1298.466 | 166.8312 | 193.645 | 233.4917 | 268.9985 | 309.9071 | 3.398%
4492 | 17-80.5 | -80.4251 | 16.9002 | 1316.3953 | 167.3638 | 194.1778 | 234.2045 | 269.881 | 310.9945 | 3.446%
4493 | 17-80.5 | -80.6964 | 16.9002 | 1334.3254 | 167.8738 | 194.7049 | 234.9277 | 270.7908 | 312.1309 | 3.49%
4494 | 17-81 | -80.9677 | 16.9002 | 1352.2564 | 168.3171 | 195.1885 | 235.6104 | 271.6642 | 313.2376 | 3.529%
4495 | 17-81 | -81.239 | 16.9002 | 1370.1881 | 168.6947 | 195.6365 | 236.2679 | 272.5244 | 314.3473 | 3.56%
4496 | 17-81.5 | -81.5104 | 16.9002 | 1388.1206 | 169.0177 | 196.0665 | 236.9285 | 273.4101 | 315.5121 | 3.586%
4497 | 17-82 | -81.7817 | 16.9002 | 1406.0536 | 169.1464 | 196.347 | 237.3966 | 274.0633 | 316.3965 | 3.594%
4498 | 17-82 | -82.053 | 16.9002 | 1423.9872 | 169.0843 | 196.4851 | 237.693 | 274.5187 | 317.0533 | 3.585%
4499 | 17-82.5 | -82.3243 | 16.9002 | 1441.9214 | 168.8609 | 196.5151 | 237.8793 | 274.8651 | 317.6051 | 3.559%
4500 | 17-82.5 | -82.5956 | 16.9002 | 1459.856 | 168.4904 | 196.4086 | 237.917 | 275.0443 | 317.9691 | 3.52%
4501 | 17-83 | -82.867 | 16.9002 | 1477.7911 | 168.0076 | 196.2015 | 237.8515 | 275.1151 | 318.2206 | 3.471%
4502 | 17-83 | -83.1383 | 16.9002 | 1495.7265 | 167.4349 | 195.9178 | 237.7178 | 275.1246 | 318.4215 | 3.413%
4503 | 17-83.5 | -83.4096 | 16.9002 | 1513.6622 | 166.7083 | 195.4793 | 237.3847 | 274.8871 | 318.3179 | 3.344%
4504 | 17-83.5 | -83.6809 | 16.9002 | 1531.5983 | 165.8773 | 194.9413 | 236.9278 | 274.4982 | 318.0299 | 3.268%
4505 | 17-84 | -83.9522 | 16.9002 | 1549.5345 | 164.974 | 194.3403 | 236.4005 | 274.0292 | 317.651 | 3.188%
4506 | 17-84 | -84.2236 | 16.9002 | 1567.471 | 163.9087 | 193.5878 | 235.6921 | 273.3394 | 317.0035 | 3.097%
4507 | 17-84.5 | -84.4949 | 16.9002 | 1585.4076 | 162.7083 | 192.7024 | 234.8389 | 272.4749 | 316.1458 | 2.999%
4508 | 17-85 | -84.7662 | 16.9002 | 1603.3444 | 161.3884 | 191.6986 | 233.8575 | 271.4571 | 315.1051 | 2.895%
4509 | 17-85 | -85.0375 | 16.9002 | 1621.2812 | 159.8274 | 190.4263 | 232.5561 | 270.0199 | 313.5222 | 2.778%
4510 | 17-85.5 | -85.3089 | 16.9002 | 1639.2181 | 158.1558 | 189.008 | 231.1272 | 268.4218 | 311.738 | 2.658%
4511 | 17-85.5 | -85.5802 | 16.9002 | 1657.1549 | 156.4173 | 187.4906 | 229.6263 | 266.7506 | 309.869 | 2.537%
4512 | 17-86 | -85.8515 | 16.9002 | 1675.0918 | 154.7524 | 186.239 | 228.2802 | 265.2697 | 308.245 | 2.432%
4513 | 17-86 | -86.1228 | 16.9002 | 1693.0286 | 153.1797 | 185.1945 | 227.1452 | 264.0842 | 307.0235 | 2.338%
4514 | 17-86.5 | -86.3941 | 16.9002 | 1710.9653 | 151.654 | 184.2243 | 226.146 | 263.1047 | 306.1004 | 2.25%
4515 | 17-86.5 | -86.6655 | 16.9002 | 1728.9019 | 149.2076 | 182.5173 | 224.1179 | 260.7784 | 303.4334 | 2.119%
4516 | 17-87 | -86.9368 | 16.9002 | 1746.8384 | 145.9982 | 179.8558 | 221.2388 | 257.3643 | 299.3872 | 1.953%
4517 | 17-87 | -87.2081 | 16.9002 | 1764.7747 | 142.1877 | 176.2794 | 217.6612 | 253.0704 | 294.2405 | 1.767%
4518 | 17-87.5 | -87.4794 | 16.9002 | 1782.7107 | 138.2253 | 172.4385 | 213.9032 | 248.5479 | 288.8062 | 1.591%
4519 | 17-88 | -87.7507 | 16.9002 | 1800.6466 | 134.2115 | 168.4411 | 210.0758 | 243.9402 | 283.2676 | 1.429%
4520 | 17-88 | -88.0221 | 16.9002 | 1818.5821 | 130.1841 | 164.3476 | 206.21 | 239.2893 | 277.6805 | 1.283%
4521 | 17-88.5 | -88.2934 | 16.9002 | 1836.5174 | 126.2095 | 160.2588 | 202.3701 | 234.6665 | 272.1231 | 1.153%
4522 | 17-88.5 | -88.5647 | 16.9002 | 1854.4524 | 122.4306 | 156.3583 | 198.7596 | 230.3402 | 266.9448 | 1.042%
4523 | 17-89 | -88.836 | 16.9002 | 1872.387 | 118.8315 | 152.6276 | 195.3398 | 226.254 | 262.0664 | 0.9466%
4524 | 17-89 | -89.1074 | 16.9002 | 1890.3213 | 115.3073 | 148.9103 | 191.9594 | 222.1938 | 257.2073 | 0.8617%
4525 | 17-89.5 | -89.3787 | 16.9002 | 1908.2552 | 111.7385 | 144.8826 | 188.3964 | 217.9401 | 252.1144 | 0.7819%
4526 | 17-89.5 | -89.65 | 16.9002 | 1926.1887 | 108.1043 | 140.6395 | 184.5873 | 213.3914 | 246.6192 | 0.707%
4527 | 17-90 | -89.9213 | 16.9002 | 1944.1217 | 104.4975 | 136.392 | 180.6714 | 208.7083 | 240.9197 | 0.639%
4528 | 17-90 | -90.1926 | 16.9002 | 1962.0543 | 101.9119 | 132.9998 | 177.8487 | 205.4915 | 237.1292 | 0.5937%
4529 | 17-90.5 | -90.464 | 16.9002 | 1979.9864 | 100.2965 | 130.8223 | 176.1601 | 203.7132 | 235.1788 | 0.568%
4530 | 17-90.5 | -90.7353 | 16.9002 | 1997.918 | 99.5465 | 129.8906 | 175.5475 | 203.211 | 234.8168 | 0.5583%
4531 | 17-50 | -50.0371 | 17.1715 | 713.329 | 151.4272 | 181.8501 | 217.1075 | 248.2547 | 283.8726 | 2.288%
4532 | 17-50.5 | -50.3084 | 17.1715 | 695.6089 | 151.856 | 182.1687 | 217.6319 | 248.9789 | 284.8432 | 2.313%
4533 | 17-50.5 | -50.5797 | 17.1715 | 677.9024 | 152.2235 | 182.4526 | 218.1163 | 249.659 | 285.7651 | 2.334%
4534 | 17-51 | -50.851 | 17.1715 | 660.2109 | 152.5638 | 182.7232 | 218.5889 | 250.3291 | 286.6802 | 2.354%
4535 | 17-51 | -51.1224 | 17.1715 | 642.5354 | 152.9158 | 183.0051 | 219.084 | 251.0328 | 287.643 | 2.374%
4536 | 17-51.5 | -51.3937 | 17.1715 | 624.8775 | 153.2226 | 183.2573 | 219.5377 | 251.6845 | 288.541 | 2.391%
4537 | 17-51.5 | -51.665 | 17.1715 | 607.2386 | 153.5098 | 183.4984 | 219.983 | 252.3312 | 289.4387 | 2.407%
4538 | 17-52 | -51.9363 | 17.1715 | 589.6206 | 153.8033 | 183.7477 | 220.4529 | 253.0189 | 290.3984 | 2.424%
4539 | 17-52 | -52.2077 | 17.1715 | 572.0254 | 154.0398 | 183.9553 | 220.8629 | 253.6294 | 291.26 | 2.436%
4540 | 17-52.5 | -52.479 | 17.1715 | 554.4551 | 154.2576 | 184.148 | 221.2554 | 254.2202 | 292.0996 | 2.448%
4541 | 17-53 | -52.7503 | 17.1715 | 536.9123 | 154.4814 | 184.3441 | 221.6585 | 254.8291 | 292.9666 | 2.459%
4542 | 17-53 | -53.0216 | 17.1715 | 519.3998 | 154.6492 | 184.4978 | 222.0009 | 255.3596 | 293.7337 | 2.467%
4543 | 17-53.5 | -53.2929 | 17.1715 | 501.9208 | 154.8101 | 184.644 | 222.334 | 255.8794 | 294.4886 | 2.475%
4544 | 17-53.5 | -53.5643 | 17.1715 | 484.479 | 154.9871 | 184.7994 | 222.6814 | 256.4183 | 295.2688 | 2.483%
4545 | 17-54 | -53.8356 | 17.1715 | 467.0785 | 155.1247 | 184.9249 | 222.9824 | 256.8953 | 295.9678 | 2.489%
4546 | 17-54 | -54.1069 | 17.1715 | 449.7241 | 155.2682 | 185.0511 | 223.2813 | 257.3672 | 296.6581 | 2.495%
4547 | 17-54.5 | -54.3782 | 17.1715 | 432.4216 | 155.4343 | 185.1902 | 223.5931 | 257.852 | 297.3615 | 2.503%
4548 | 17-54.5 | -54.6495 | 17.1715 | 415.1773 | 155.5866 | 185.3173 | 223.8777 | 258.2945 | 298.0034 | 2.51%
4549 | 17-55 | -54.9209 | 17.1715 | 397.9989 | 155.7878 | 185.4788 | 224.2056 | 258.7886 | 298.707 | 2.52%
4550 | 17-55 | -55.1922 | 17.1715 | 380.8953 | 156.0477 | 185.6826 | 224.5858 | 259.3444 | 299.4835 | 2.535%
4551 | 17-55.5 | -55.4635 | 17.1715 | 363.8771 | 156.2956 | 185.8698 | 224.9178 | 259.8201 | 300.1395 | 2.548%
4552 | 17-55.5 | -55.7348 | 17.1715 | 346.957 | 156.6003 | 186.0955 | 225.2925 | 260.3418 | 300.8449 | 2.566%
4553 | 17-56 | -56.0061 | 17.1715 | 330.1499 | 156.9587 | 186.3629 | 225.7148 | 260.9162 | 301.6086 | 2.588%
4554 | 17-56.5 | -56.2775 | 17.1715 | 313.4742 | 157.3038 | 186.6165 | 226.0983 | 261.4264 | 302.2758 | 2.609%
4555 | 17-56.5 | -56.5488 | 17.1715 | 296.952 | 157.7007 | 186.9072 | 226.5191 | 261.9729 | 302.9774 | 2.634%
4556 | 17-57 | -56.8201 | 17.1715 | 280.6105 | 158.1449 | 187.2355 | 226.975 | 262.5512 | 303.7055 | 2.663%
4557 | 17-57 | -57.0914 | 17.1715 | 264.4831 | 158.601 | 187.5634 | 227.4026 | 263.0726 | 304.3397 | 2.694%
4558 | 17-57.5 | -57.3628 | 17.1715 | 248.6116 | 159.1285 | 187.9383 | 227.8722 | 263.6292 | 304.9992 | 2.73%
4559 | 17-57.5 | -57.6341 | 17.1715 | 233.0482 | 159.7204 | 188.357 | 228.3782 | 264.2133 | 305.674 | 2.772%
4560 | 17-58 | -57.9054 | 17.1715 | 217.8592 | 160.3408 | 188.7881 | 228.8716 | 264.7588 | 306.2761 | 2.817%
4561 | 17-58 | -58.1767 | 17.1715 | 203.1285 | 161.0263 | 189.2625 | 229.3982 | 265.326 | 306.8839 | 2.868%
4562 | 17-58.5 | -58.448 | 17.1715 | 188.9633 | 161.7477 | 189.7633 | 229.9327 | 265.8813 | 307.4537 | 2.925%
4563 | 17-58.5 | -58.7194 | 17.1715 | 175.5007 | 162.4567 | 190.2464 | 230.4124 | 266.3437 | 307.8822 | 2.982%
4564 | 17-59 | -58.9907 | 17.1715 | 162.9149 | 163.219 | 190.7759 | 230.9418 | 266.8582 | 308.3646 | 3.046%
4565 | 17-59.5 | -59.262 | 17.1715 | 151.4247 | 164.0355 | 191.3688 | 231.543 | 267.4511 | 308.9322 | 3.116%
4566 | 17-59.5 | -59.5333 | 17.1715 | 141.2978 | 164.9265 | 192.066 | 232.2713 | 268.1915 | 309.6708 | 3.195%
4567 | 17-60 | -59.8046 | 17.1715 | 132.8463 | 165.9489 | 192.9308 | 233.2233 | 269.2087 | 310.7504 | 3.289%
4568 | 17-60 | -60.076 | 17.1715 | 126.4067 | 166.9984 | 193.8419 | 234.234 | 270.2958 | 311.9134 | 3.388%
4569 | 17-60.5 | -60.3473 | 17.1715 | 122.2972 | 167.923 | 194.6103 | 235.0486 | 271.1364 | 312.7684 | 3.479%
4570 | 17-60.5 | -60.6186 | 17.1715 | 120.756 | 168.7498 | 195.2782 | 235.7387 | 271.8305 | 313.4512 | 3.563%
4571 | 17-61 | -60.8899 | 17.1715 | 121.8805 | 169.493 | 195.8742 | 236.3402 | 272.421 | 314.0131 | 3.641%
4572 | 17-61 | -61.1613 | 17.1715 | 125.5992 | 170.1841 | 196.4445 | 236.9137 | 272.9819 | 314.5442 | 3.716%
4573 | 17-61.5 | -61.4326 | 17.1715 | 131.6924 | 170.8484 | 197.0225 | 237.5126 | 273.5862 | 315.1413 | 3.79%
4574 | 17-61.5 | -61.7039 | 17.1715 | 139.8502 | 171.4549 | 197.5769 | 238.096 | 274.184 | 315.7443 | 3.859%
4575 | 17-62 | -61.9752 | 17.1715 | 149.7354 | 171.997 | 198.0933 | 238.6473 | 274.7567 | 316.3321 | 3.923%
4576 | 17-62 | -62.2465 | 17.1715 | 161.0303 | 172.5166 | 198.6198 | 239.2382 | 275.3992 | 317.0279 | 3.983%
4577 | 17-62.5 | -62.5179 | 17.1715 | 173.4596 | 173.0381 | 199.1889 | 239.9124 | 276.1651 | 317.8978 | 4.043%
4578 | 17-63 | -62.7892 | 17.1715 | 186.797 | 173.5757 | 199.8155 | 240.689 | 277.0783 | 318.9713 | 4.103%
4579 | 17-63 | -63.0605 | 17.1715 | 200.8617 | 174.1134 | 200.4675 | 241.5276 | 278.0907 | 320.1913 | 4.163%
4580 | 17-63.5 | -63.3318 | 17.1715 | 215.5114 | 174.4959 | 200.9349 | 242.1344 | 278.8278 | 321.0849 | 4.205%
4581 | 17-63.5 | -63.6031 | 17.1715 | 230.6344 | 174.7072 | 201.1946 | 242.4735 | 279.2414 | 321.5878 | 4.228%
4582 | 17-64 | -63.8745 | 17.1715 | 246.1437 | 174.9011 | 201.4443 | 242.8167 | 279.6735 | 322.1282 | 4.248%
4583 | 17-64 | -64.1458 | 17.1715 | 261.9706 | 175.1043 | 201.7164 | 243.2055 | 280.1745 | 322.7665 | 4.268%
4584 | 17-64.5 | -64.4171 | 17.1715 | 278.0607 | 175.3049 | 201.9966 | 243.6217 | 280.7224 | 323.4766 | 4.286%
4585 | 17-64.5 | -64.6884 | 17.1715 | 294.371 | 175.4689 | 202.2445 | 244.0147 | 281.2573 | 324.1875 | 4.299%
4586 | 17-65 | -64.9598 | 17.1715 | 310.8668 | 175.5685 | 202.4147 | 244.3085 | 281.673 | 324.7556 | 4.305%
4587 | 17-65 | -65.2311 | 17.1715 | 327.52 | 175.6142 | 202.516 | 244.5082 | 281.9707 | 325.1766 | 4.305%
4588 | 17-65.5 | -65.5024 | 17.1715 | 344.3077 | 175.6311 | 202.58 | 244.6567 | 282.2041 | 325.5174 | 4.302%
4589 | 17-66 | -65.7737 | 17.1715 | 361.2111 | 175.5922 | 202.5759 | 244.7166 | 282.3298 | 325.7277 | 4.292%
4590 | 17-66 | -66.045 | 17.1715 | 378.2148 | 175.458 | 202.4573 | 244.6314 | 282.2822 | 325.7313 | 4.272%
4591 | 17-66.5 | -66.3164 | 17.1715 | 395.3057 | 175.2006 | 202.1928 | 244.3637 | 282.0186 | 325.4794 | 4.239%
4592 | 17-66.5 | -66.5877 | 17.1715 | 412.473 | 174.7138 | 201.6326 | 243.6888 | 281.241 | 324.583 | 4.182%
4593 | 17-67 | -66.859 | 17.1715 | 429.7074 | 174.1198 | 200.9441 | 242.8388 | 280.244 | 323.4135 | 4.115%
4594 | 17-67 | -67.1303 | 17.1715 | 447.0013 | 173.477 | 200.2707 | 242.0171 | 279.2886 | 322.3025 | 4.044%
4595 | 17-67.5 | -67.4016 | 17.1715 | 464.3479 | 172.859 | 199.6514 | 241.2685 | 278.4244 | 321.3047 | 3.977%
4596 | 17-67.5 | -67.673 | 17.1715 | 481.7415 | 172.2518 | 199.0564 | 240.554 | 277.6037 | 320.3618 | 3.912%
4597 | 17-68 | -67.9443 | 17.1715 | 499.1771 | 171.6412 | 198.4651 | 239.8483 | 276.797 | 319.4396 | 3.847%
4598 | 17-68 | -68.2156 | 17.1715 | 516.6505 | 170.9635 | 197.8089 | 239.0494 | 275.8698 | 318.3635 | 3.777%
4599 | 17-68.5 | -68.4869 | 17.1715 | 534.158 | 170.2404 | 197.1249 | 238.2227 | 274.9156 | 317.2621 | 3.704%
4600 | 17-69 | -68.7583 | 17.1715 | 551.6962 | 169.4868 | 196.4333 | 237.4047 | 273.9873 | 316.209 | 3.629%
4601 | 17-69 | -69.0296 | 17.1715 | 569.2623 | 168.6256 | 195.651 | 236.4589 | 272.8955 | 314.9488 | 3.545%
4602 | 17-69.5 | -69.3009 | 17.1715 | 586.8538 | 167.6837 | 194.8049 | 235.4158 | 271.674 | 313.5184 | 3.458%
4603 | 17-69.5 | -69.5722 | 17.1715 | 604.4684 | 166.6763 | 193.9061 | 234.2881 | 270.3362 | 311.933 | 3.367%
4604 | 17-70 | -69.8435 | 17.1715 | 622.1041 | 165.6266 | 192.9562 | 233.0664 | 268.8621 | 310.1577 | 3.276%
4605 | 17-70 | -70.1149 | 17.1715 | 639.7591 | 164.6455 | 192.1041 | 231.9758 | 267.5508 | 308.5838 | 3.193%
4606 | 17-70.5 | -70.3862 | 17.1715 | 657.4319 | 163.7763 | 191.3895 | 231.0754 | 266.4798 | 307.3115 | 3.121%
4607 | 17-70.5 | -70.6575 | 17.1715 | 675.121 | 163.1609 | 190.8521 | 230.3859 | 265.6496 | 306.3138 | 3.071%
4608 | 17-71 | -70.9288 | 17.1715 | 692.8252 | 162.7404 | 190.4534 | 229.8659 | 265.0166 | 305.5461 | 3.037%
4609 | 17-71 | -71.2001 | 17.1715 | 710.5433 | 162.4908 | 190.1723 | 229.4892 | 264.5504 | 304.9726 | 3.016%
4610 | 17-71.5 | -71.4715 | 17.1715 | 728.2742 | 162.2127 | 189.8616 | 229.0433 | 263.9753 | 304.2397 | 2.995%
4611 | 17-71.5 | -71.7428 | 17.1715 | 746.017 | 161.9795 | 189.591 | 228.6347 | 263.4332 | 303.5336 | 2.978%
4612 | 17-72 | -72.0141 | 17.1715 | 763.7709 | 161.7743 | 189.3456 | 228.2429 | 262.8988 | 302.8226 | 2.963%
4613 | 17-72.5 | -72.2854 | 17.1715 | 781.535 | 161.4081 | 188.9917 | 227.6795 | 262.1307 | 301.8008 | 2.938%
4614 | 17-72.5 | -72.5568 | 17.1715 | 799.3087 | 160.9775 | 188.6152 | 227.0877 | 261.3292 | 300.7398 | 2.908%
4615 | 17-73 | -72.8281 | 17.1715 | 817.0912 | 160.5484 | 188.2555 | 226.5235 | 260.5659 | 299.7306 | 2.879%
4616 | 17-73 | -73.0994 | 17.1715 | 834.882 | 160.3086 | 188.0384 | 226.1509 | 260.0408 | 299.0155 | 2.864%
4617 | 17-73.5 | -73.3707 | 17.1715 | 852.6806 | 160.2537 | 187.961 | 225.9773 | 259.771 | 298.6246 | 2.862%
4618 | 17-73.5 | -73.642 | 17.1715 | 870.4864 | 160.3439 | 187.9882 | 225.952 | 259.6914 | 298.4747 | 2.87%
4619 | 17-74 | -73.9134 | 17.1715 | 888.299 | 160.4337 | 188.0186 | 225.933 | 259.6209 | 298.3377 | 2.878%
4620 | 17-74 | -74.1847 | 17.1715 | 906.1179 | 160.4436 | 188.0129 | 225.9019 | 259.564 | 298.2477 | 2.88%
4621 | 17-74.5 | -74.456 | 17.1715 | 923.9428 | 160.3504 | 187.953 | 225.8269 | 259.4748 | 298.1415 | 2.873%
4622 | 17-74.5 | -74.7273 | 17.1715 | 941.7732 | 160.1328 | 187.8175 | 225.6621 | 259.2832 | 297.918 | 2.857%
4623 | 17-75 | -74.9986 | 17.1715 | 959.6089 | 160.0018 | 187.7557 | 225.6235 | 259.2693 | 297.9366 | 2.846%
4624 | 17-75.5 | -75.27 | 17.1715 | 977.4495 | 159.935 | 187.7446 | 225.6685 | 259.3713 | 298.1114 | 2.839%
4625 | 17-75.5 | -75.5413 | 17.1715 | 995.2947 | 159.9256 | 187.7699 | 225.7616 | 259.5327 | 298.3591 | 2.837%
4626 | 17-76 | -75.8126 | 17.1715 | 1013.1442 | 160.1776 | 187.9694 | 226.0977 | 260.0026 | 298.9953 | 2.853%
4627 | 17-76 | -76.0839 | 17.1715 | 1030.9978 | 160.648 | 188.3151 | 226.6271 | 260.7101 | 299.9222 | 2.885%
4628 | 17-76.5 | -76.3553 | 17.1715 | 1048.8553 | 161.2302 | 188.7328 | 227.2352 | 261.5008 | 300.9364 | 2.927%
4629 | 17-76.5 | -76.6266 | 17.1715 | 1066.7163 | 161.7398 | 189.1015 | 227.7643 | 262.1837 | 301.8069 | 2.963%
4630 | 17-77 | -76.8979 | 17.1715 | 1084.5808 | 162.1481 | 189.4054 | 228.1914 | 262.7281 | 302.4942 | 2.994%
4631 | 17-77 | -77.1692 | 17.1715 | 1102.4485 | 162.4743 | 189.6601 | 228.5375 | 263.1606 | 303.0311 | 3.018%
4632 | 17-77.5 | -77.4405 | 17.1715 | 1120.3192 | 162.8624 | 189.9686 | 228.9476 | 263.6661 | 303.6512 | 3.049%
4633 | 17-77.5 | -77.7119 | 17.1715 | 1138.1928 | 163.2832 | 190.3055 | 229.3798 | 264.1865 | 304.2765 | 3.083%
4634 | 17-78 | -77.9832 | 17.1715 | 1156.069 | 163.7299 | 190.665 | 229.8275 | 264.7145 | 304.8987 | 3.119%
4635 | 17-78.5 | -78.2545 | 17.1715 | 1173.9478 | 164.241 | 191.0883 | 230.3616 | 265.3505 | 305.6552 | 3.162%
4636 | 17-78.5 | -78.5258 | 17.1715 | 1191.829 | 164.7682 | 191.5324 | 230.9097 | 265.9928 | 306.4077 | 3.207%
4637 | 17-79 | -78.7971 | 17.1715 | 1209.7124 | 165.2998 | 191.9866 | 231.456 | 266.6211 | 307.1303 | 3.254%
4638 | 17-79 | -79.0685 | 17.1715 | 1227.5979 | 165.8694 | 192.4912 | 232.0696 | 267.3326 | 307.9553 | 3.305%
4639 | 17-79.5 | -79.3398 | 17.1715 | 1245.4854 | 166.4332 | 193.0082 | 232.692 | 268.0488 | 308.7796 | 3.357%
4640 | 17-79.5 | -79.6111 | 17.1715 | 1263.3748 | 166.9972 | 193.5435 | 233.3391 | 268.7958 | 309.6421 | 3.41%
4641 | 17-80 | -79.8824 | 17.1715 | 1281.266 | 167.6052 | 194.1395 | 234.0845 | 269.678 | 310.6854 | 3.467%
4642 | 17-80 | -80.1537 | 17.1715 | 1299.1588 | 168.1958 | 194.7283 | 234.8326 | 270.5732 | 311.7551 | 3.523%
4643 | 17-80.5 | -80.4251 | 17.1715 | 1317.0531 | 168.7524 | 195.2926 | 235.5597 | 271.4514 | 312.8139 | 3.575%
4644 | 17-80.5 | -80.6964 | 17.1715 | 1334.949 | 169.2896 | 195.8507 | 236.2924 | 272.3478 | 313.9067 | 3.626%
4645 | 17-81 | -80.9677 | 17.1715 | 1352.8462 | 169.7684 | 196.3673 | 236.9843 | 273.2052 | 314.9641 | 3.671%
4646 | 17-81 | -81.239 | 17.1715 | 1370.7447 | 170.1931 | 196.854 | 237.6577 | 274.0566 | 316.0325 | 3.71%
4647 | 17-81.5 | -81.5104 | 17.1715 | 1388.6444 | 170.5759 | 197.3313 | 238.3455 | 274.9475 | 317.1729 | 3.744%
4648 | 17-82 | -81.7817 | 17.1715 | 1406.5452 | 170.8115 | 197.6912 | 238.8861 | 275.6639 | 318.1067 | 3.764%
4649 | 17-82 | -82.053 | 17.1715 | 1424.4471 | 170.9088 | 197.9471 | 239.3093 | 276.252 | 318.9007 | 3.77%
4650 | 17-82.5 | -82.3243 | 17.1715 | 1442.3499 | 170.893 | 198.1333 | 239.6755 | 276.7983 | 319.6745 | 3.763%
4651 | 17-82.5 | -82.5956 | 17.1715 | 1460.2537 | 170.7429 | 198.1984 | 239.9015 | 277.1882 | 320.274 | 3.743%
4652 | 17-83 | -82.867 | 17.1715 | 1478.1583 | 170.4855 | 198.1691 | 240.0272 | 277.4748 | 320.7686 | 3.711%
4653 | 17-83 | -83.1383 | 17.1715 | 1496.0636 | 170.1429 | 198.0696 | 240.0901 | 277.7083 | 321.2247 | 3.671%
4654 | 17-83.5 | -83.4096 | 17.1715 | 1513.9697 | 169.6501 | 197.8202 | 239.958 | 277.7046 | 321.393 | 3.618%
4655 | 17-83.5 | -83.6809 | 17.1715 | 1531.8765 | 169.0533 | 197.4751 | 239.7055 | 277.5578 | 321.3916 | 3.556%
4656 | 17-84 | -83.9522 | 17.1715 | 1549.7838 | 168.3827 | 197.0693 | 239.3849 | 277.3373 | 321.3109 | 3.489%
4657 | 17-84 | -84.2236 | 17.1715 | 1567.6917 | 167.5545 | 196.5247 | 238.8925 | 276.9122 | 320.9868 | 3.41%
4658 | 17-84.5 | -84.4949 | 17.1715 | 1585.6001 | 166.5909 | 195.8572 | 238.2605 | 276.3229 | 320.4698 | 3.321%
4659 | 17-85 | -84.7662 | 17.1715 | 1603.509 | 165.5056 | 195.0792 | 237.5042 | 275.5887 | 319.7839 | 3.225%
4660 | 17-85 | -85.0375 | 17.1715 | 1621.4182 | 164.1977 | 194.0741 | 236.4583 | 274.4799 | 318.619 | 3.115%
4661 | 17-85.5 | -85.3089 | 17.1715 | 1639.3278 | 162.7619 | 192.9365 | 235.2789 | 273.2074 | 317.2539 | 2.998%
4662 | 17-85.5 | -85.5802 | 17.1715 | 1657.2377 | 161.2256 | 191.6929 | 234.0112 | 271.8334 | 315.7727 | 2.879%
4663 | 17-86 | -85.8515 | 17.1715 | 1675.1478 | 159.5354 | 190.4399 | 232.6099 | 270.2946 | 314.0884 | 2.757%
4664 | 17-86 | -86.1228 | 17.1715 | 1693.0582 | 157.7148 | 189.1618 | 231.1732 | 268.733 | 312.3996 | 2.633%
4665 | 17-86.5 | -86.3941 | 17.1715 | 1710.9687 | 155.7385 | 187.8037 | 229.6569 | 267.0959 | 310.6445 | 2.505%
4666 | 17-86.5 | -86.6655 | 17.1715 | 1728.8794 | 152.9541 | 185.7939 | 227.2519 | 264.304 | 307.404 | 2.338%
4667 | 17-87 | -86.9368 | 17.1715 | 1746.7902 | 149.4987 | 182.9463 | 224.1207 | 260.5901 | 303.0014 | 2.141%
4668 | 17-87 | -87.2081 | 17.1715 | 1764.7011 | 145.5023 | 179.2945 | 220.3807 | 256.1142 | 297.6509 | 1.928%
4669 | 17-87.5 | -87.4794 | 17.1715 | 1782.6119 | 141.3308 | 175.3454 | 216.438 | 251.3802 | 291.9743 | 1.727%
4670 | 17-88 | -87.7507 | 17.1715 | 1800.5228 | 137.0792 | 171.1962 | 212.395 | 246.5196 | 286.1393 | 1.541%
4671 | 17-88 | -88.0221 | 17.1715 | 1818.4336 | 132.7868 | 166.9091 | 208.2825 | 241.5747 | 280.202 | 1.373%
4672 | 17-88.5 | -88.2934 | 17.1715 | 1836.3444 | 128.5275 | 162.596 | 204.1722 | 236.6281 | 274.2573 | 1.224%
4673 | 17-88.5 | -88.5647 | 17.1715 | 1854.255 | 124.4233 | 158.4047 | 200.239 | 231.9111 | 268.6067 | 1.096%
4674 | 17-89 | -88.836 | 17.1715 | 1872.1655 | 120.4628 | 154.3243 | 196.4492 | 227.3744 | 263.1814 | 0.9858%
4675 | 17-89 | -89.1074 | 17.1715 | 1890.0758 | 116.5605 | 150.2289 | 192.6658 | 222.8341 | 257.7386 | 0.8876%
4676 | 17-89.5 | -89.3787 | 17.1715 | 1907.9859 | 112.7886 | 146.0554 | 188.933 | 218.3892 | 252.4306 | 0.8009%
4677 | 17-89.5 | -89.65 | 17.1715 | 1925.8958 | 109.1536 | 141.8747 | 185.1877 | 213.9535 | 247.1123 | 0.7244%
4678 | 17-90 | -89.9213 | 17.1715 | 1943.8055 | 105.722 | 137.8116 | 181.5329 | 209.6436 | 241.9293 | 0.6581%
4679 | 17-90 | -90.1926 | 17.1715 | 1961.7148 | 103.1712 | 134.4844 | 178.8108 | 206.5845 | 238.3699 | 0.6123%
4680 | 17-90.5 | -90.464 | 17.1715 | 1979.6238 | 101.4672 | 132.214 | 177.0719 | 204.7651 | 236.3919 | 0.5846%
4681 | 17-90.5 | -90.7353 | 17.1715 | 1997.5325 | 100.5275 | 131.0226 | 176.2809 | 204.0554 | 235.7886 | 0.5715%
4682 | 17-50 | -50.0371 | 17.4428 | 716.2485 | 151.611 | 182.0145 | 217.2515 | 248.3742 | 283.9577 | 2.302%
4683 | 17-50.5 | -50.3084 | 17.4428 | 698.628 | 152.1137 | 182.3723 | 217.8195 | 249.1456 | 284.9791 | 2.331%
4684 | 17-50.5 | -50.5797 | 17.4428 | 681.0256 | 152.5548 | 182.6963 | 218.3501 | 249.8767 | 285.9576 | 2.357%
4685 | 17-51 | -50.851 | 17.4428 | 663.4428 | 152.9677 | 183.0067 | 218.8686 | 250.5979 | 286.9293 | 2.381%
4686 | 17-51 | -51.1224 | 17.4428 | 645.8812 | 153.3916 | 183.3281 | 219.4081 | 251.3503 | 287.9449 | 2.406%
4687 | 17-51.5 | -51.3937 | 17.4428 | 628.3428 | 153.7669 | 183.6174 | 219.9017 | 252.0436 | 288.8859 | 2.428%
4688 | 17-51.5 | -51.665 | 17.4428 | 610.8294 | 154.1198 | 183.8938 | 220.3834 | 252.7266 | 289.8191 | 2.449%
4689 | 17-52 | -51.9363 | 17.4428 | 593.3434 | 154.4773 | 184.1774 | 220.8874 | 253.4473 | 290.8095 | 2.469%
4690 | 17-52 | -52.2077 | 17.4428 | 575.8873 | 154.7744 | 184.4185 | 221.3321 | 254.0928 | 291.7057 | 2.486%
4691 | 17-52.5 | -52.479 | 17.4428 | 558.4638 | 155.0518 | 184.6459 | 221.7626 | 254.7241 | 292.5879 | 2.502%
4692 | 17-53 | -52.7503 | 17.4428 | 541.0763 | 155.3352 | 184.8786 | 222.2085 | 255.3808 | 293.5084 | 2.517%
4693 | 17-53 | -53.0216 | 17.4428 | 523.7282 | 155.5628 | 185.0713 | 222.5988 | 255.9672 | 294.3406 | 2.529%
4694 | 17-53.5 | -53.2929 | 17.4428 | 506.4238 | 155.7825 | 185.2576 | 222.9825 | 256.5471 | 295.1667 | 2.54%
4695 | 17-53.5 | -53.5643 | 17.4428 | 489.1676 | 156.0165 | 185.4532 | 223.3813 | 257.1479 | 296.021 | 2.553%
4696 | 17-54 | -53.8356 | 17.4428 | 471.965 | 156.2053 | 185.6156 | 223.7297 | 257.6819 | 296.7885 | 2.562%
4697 | 17-54 | -54.1069 | 17.4428 | 454.8221 | 156.3952 | 185.7764 | 224.0733 | 258.2078 | 297.544 | 2.571%
4698 | 17-54.5 | -54.3782 | 17.4428 | 437.746 | 156.6034 | 185.9478 | 224.4274 | 258.7443 | 298.3099 | 2.582%
4699 | 17-54.5 | -54.6495 | 17.4428 | 420.7447 | 156.7921 | 186.1047 | 224.7532 | 259.2386 | 299.0168 | 2.591%
4700 | 17-55 | -54.9209 | 17.4428 | 403.8279 | 157.0274 | 186.2956 | 225.1241 | 259.7888 | 299.7925 | 2.604%
4701 | 17-55 | -55.1922 | 17.4428 | 387.0065 | 157.3199 | 186.5287 | 225.5498 | 260.4059 | 300.6497 | 2.62%
4702 | 17-55.5 | -55.4635 | 17.4428 | 370.2937 | 157.5997 | 186.7461 | 225.9324 | 260.9524 | 301.4016 | 2.637%
4703 | 17-55.5 | -55.7348 | 17.4428 | 353.7049 | 157.9355 | 187.0025 | 226.3601 | 261.549 | 302.2094 | 2.657%
4704 | 17-56 | -56.0061 | 17.4428 | 337.2584 | 158.3225 | 187.3004 | 226.8361 | 262.1999 | 303.0782 | 2.68%
4705 | 17-56.5 | -56.2775 | 17.4428 | 320.976 | 158.6923 | 187.5817 | 227.2692 | 262.7814 | 303.8439 | 2.704%
4706 | 17-56.5 | -56.5488 | 17.4428 | 304.8842 | 159.1085 | 187.897 | 227.7352 | 263.3938 | 304.6371 | 2.731%
4707 | 17-57 | -56.8201 | 17.4428 | 289.0148 | 159.5648 | 188.2458 | 228.2313 | 264.032 | 305.4498 | 2.761%
4708 | 17-57 | -57.0914 | 17.4428 | 273.4065 | 160.0227 | 188.5871 | 228.6915 | 264.6049 | 306.1599 | 2.792%
4709 | 17-57.5 | -57.3628 | 17.4428 | 258.1068 | 160.5437 | 188.9716 | 229.1909 | 265.212 | 306.8962 | 2.829%
4710 | 17-57.5 | -57.6341 | 17.4428 | 243.174 | 161.1199 | 189.3957 | 229.7236 | 265.8445 | 307.647 | 2.871%
4711 | 17-58 | -57.9054 | 17.4428 | 228.6799 | 161.7144 | 189.8258 | 230.2359 | 266.4295 | 308.315 | 2.915%
4712 | 17-58 | -58.1767 | 17.4428 | 214.7134 | 162.3645 | 190.2934 | 230.773 | 267.0251 | 308.9744 | 2.966%
4713 | 17-58.5 | -58.448 | 17.4428 | 201.3844 | 163.041 | 190.7821 | 231.3104 | 267.5988 | 309.5829 | 3.02%
4714 | 17-58.5 | -58.7194 | 17.4428 | 188.828 | 163.6977 | 191.2486 | 231.7855 | 268.0696 | 310.0368 | 3.075%
4715 | 17-59 | -58.9907 | 17.4428 | 177.2085 | 164.399 | 191.7565 | 232.3012 | 268.579 | 310.5257 | 3.135%
4716 | 17-59.5 | -59.262 | 17.4428 | 166.7219 | 165.1425 | 192.3195 | 232.875 | 269.1479 | 311.0744 | 3.201%
4717 | 17-59.5 | -59.5333 | 17.4428 | 157.5945 | 165.9454 | 192.9715 | 233.5528 | 269.8336 | 311.7541 | 3.275%
4718 | 17-60 | -59.8046 | 17.4428 | 150.0747 | 166.871 | 193.7787 | 234.4367 | 270.7737 | 312.7463 | 3.362%
4719 | 17-60 | -60.076 | 17.4428 | 144.4136 | 167.8239 | 194.6291 | 235.3738 | 271.7759 | 313.8113 | 3.455%
4720 | 17-60.5 | -60.3473 | 17.4428 | 140.8357 | 168.6654 | 195.3486 | 236.1286 | 272.5465 | 314.5846 | 3.54%
4721 | 17-60.5 | -60.6186 | 17.4428 | 139.5014 | 169.426 | 195.9836 | 236.7762 | 273.1895 | 315.2061 | 3.619%
4722 | 17-61 | -60.8899 | 17.4428 | 140.4745 | 170.1161 | 196.556 | 237.3445 | 273.7376 | 315.7145 | 3.694%
4723 | 17-61 | -61.1613 | 17.4428 | 143.7083 | 170.7614 | 197.1045 | 237.8846 | 274.2538 | 316.1868 | 3.766%
4724 | 17-61.5 | -61.4326 | 17.4428 | 149.0556 | 171.3875 | 197.6648 | 238.4542 | 274.8174 | 316.7291 | 3.838%
4725 | 17-61.5 | -61.7039 | 17.4428 | 156.2997 | 171.9637 | 198.2047 | 239.0115 | 275.3775 | 317.2798 | 3.905%
4726 | 17-62 | -61.9752 | 17.4428 | 165.1913 | 172.4824 | 198.7093 | 239.5393 | 275.915 | 317.8176 | 3.967%
4727 | 17-62 | -62.2465 | 17.4428 | 175.48 | 172.9836 | 199.2263 | 240.1097 | 276.5258 | 318.4674 | 4.027%
4728 | 17-62.5 | -62.5179 | 17.4428 | 186.9352 | 173.4922 | 199.7884 | 240.7667 | 277.2644 | 319.2972 | 4.086%
4729 | 17-63 | -62.7892 | 17.4428 | 199.3561 | 174.0277 | 200.4142 | 241.5356 | 278.1628 | 320.3467 | 4.148%
4730 | 17-63 | -63.0605 | 17.4428 | 212.5733 | 174.5794 | 201.08 | 242.3871 | 279.1867 | 321.5763 | 4.209%
4731 | 17-63.5 | -63.3318 | 17.4428 | 226.4474 | 174.9867 | 201.5752 | 243.026 | 279.9596 | 322.5096 | 4.255%
4732 | 17-63.5 | -63.6031 | 17.4428 | 240.865 | 175.2267 | 201.8678 | 243.4048 | 280.4187 | 323.0648 | 4.281%
4733 | 17-64 | -63.8745 | 17.4428 | 255.734 | 175.4417 | 202.142 | 243.7776 | 280.8851 | 323.6447 | 4.304%
4734 | 17-64 | -64.1458 | 17.4428 | 270.9802 | 175.6578 | 202.4292 | 244.1853 | 281.4084 | 324.3095 | 4.326%
4735 | 17-64.5 | -64.4171 | 17.4428 | 286.5434 | 175.8673 | 202.7208 | 244.617 | 281.9756 | 325.0437 | 4.345%
4736 | 17-64.5 | -64.6884 | 17.4428 | 302.3745 | 176.0429 | 202.9841 | 245.0321 | 282.5392 | 325.7914 | 4.359%
4737 | 17-65 | -64.9598 | 17.4428 | 318.4337 | 176.1543 | 203.171 | 245.3509 | 282.9883 | 326.4032 | 4.366%
4738 | 17-65 | -65.2311 | 17.4428 | 334.6879 | 176.2116 | 203.2894 | 245.5773 | 283.3222 | 326.8724 | 4.366%
4739 | 17-65.5 | -65.5024 | 17.4428 | 351.1102 | 176.2401 | 203.3712 | 245.7543 | 283.5946 | 327.2654 | 4.364%
4740 | 17-66 | -65.7737 | 17.4428 | 367.678 | 176.2106 | 203.3815 | 245.8377 | 283.7529 | 327.5196 | 4.355%
4741 | 17-66 | -66.045 | 17.4428 | 384.3724 | 176.0827 | 203.2727 | 245.7683 | 283.7269 | 327.5522 | 4.336%
4742 | 17-66.5 | -66.3164 | 17.4428 | 401.1776 | 175.8292 | 203.0134 | 245.5079 | 283.4728 | 327.3126 | 4.302%
4743 | 17-66.5 | -66.5877 | 17.4428 | 418.0802 | 175.3372 | 202.4459 | 244.8221 | 282.6809 | 326.3977 | 4.244%
4744 | 17-67 | -66.859 | 17.4428 | 435.0689 | 174.7271 | 201.7358 | 243.9416 | 281.6447 | 325.1784 | 4.175%
4745 | 17-67 | -67.1303 | 17.4428 | 452.1338 | 174.0572 | 201.0272 | 243.0708 | 280.6271 | 323.9891 | 4.101%
4746 | 17-67.5 | -67.4016 | 17.4428 | 469.2667 | 173.4079 | 200.367 | 242.2661 | 279.6923 | 322.903 | 4.03%
4747 | 17-67.5 | -67.673 | 17.4428 | 486.4604 | 172.7682 | 199.7277 | 241.4911 | 278.7957 | 321.8655 | 3.961%
4748 | 17-68 | -67.9443 | 17.4428 | 503.7085 | 172.1241 | 199.0894 | 240.7217 | 277.9091 | 320.844 | 3.892%
4749 | 17-68 | -68.2156 | 17.4428 | 521.0057 | 171.379 | 198.3554 | 239.8155 | 276.8466 | 319.5982 | 3.816%
4750 | 17-68.5 | -68.4869 | 17.4428 | 538.3471 | 170.5439 | 197.563 | 238.839 | 275.7031 | 318.2593 | 3.732%
4751 | 17-69 | -68.7583 | 17.4428 | 555.7287 | 169.6373 | 196.7345 | 237.8323 | 274.5367 | 316.908 | 3.643%
4752 | 17-69 | -69.0296 | 17.4428 | 573.1468 | 168.6207 | 195.8143 | 236.6987 | 273.2098 | 315.355 | 3.546%
4753 | 17-69.5 | -69.3009 | 17.4428 | 590.598 | 167.5249 | 194.8345 | 235.4772 | 271.7675 | 313.6531 | 3.445%
4754 | 17-69.5 | -69.5722 | 17.4428 | 608.0795 | 166.3656 | 193.8068 | 234.1823 | 270.227 | 311.8221 | 3.342%
4755 | 17-70 | -69.8435 | 17.4428 | 625.5887 | 165.145 | 192.7165 | 232.7808 | 268.5363 | 309.7864 | 3.237%
4756 | 17-70 | -70.1149 | 17.4428 | 643.1233 | 163.981 | 191.7199 | 231.5066 | 267.0052 | 307.9498 | 3.14%
4757 | 17-70.5 | -70.3862 | 17.4428 | 660.6814 | 162.9235 | 190.8617 | 230.4249 | 265.7185 | 306.4208 | 3.054%
4758 | 17-70.5 | -70.6575 | 17.4428 | 678.2609 | 162.1966 | 190.244 | 229.6418 | 264.7831 | 305.305 | 2.996%
4759 | 17-71 | -70.9288 | 17.4428 | 695.8603 | 161.7399 | 189.8212 | 229.1061 | 264.1438 | 304.5435 | 2.96%
4760 | 17-71 | -71.2001 | 17.4428 | 713.4781 | 161.5226 | 189.5655 | 228.7827 | 263.7589 | 304.0867 | 2.941%
4761 | 17-71.5 | -71.4715 | 17.4428 | 731.1129 | 161.2746 | 189.278 | 228.3852 | 263.2573 | 303.4593 | 2.922%
4762 | 17-71.5 | -71.7428 | 17.4428 | 748.7635 | 161.1018 | 189.0571 | 228.061 | 262.8341 | 302.9151 | 2.909%
4763 | 17-72 | -72.0141 | 17.4428 | 766.4287 | 160.9978 | 188.8887 | 227.7908 | 262.4648 | 302.4233 | 2.901%
4764 | 17-72.5 | -72.2854 | 17.4428 | 784.1076 | 160.7561 | 188.6283 | 227.37 | 261.8872 | 301.6513 | 2.885%
4765 | 17-72.5 | -72.5568 | 17.4428 | 801.7991 | 160.4358 | 188.3341 | 226.9028 | 261.2513 | 300.8066 | 2.863%
4766 | 17-73 | -72.8281 | 17.4428 | 819.5025 | 160.1078 | 188.0488 | 226.4485 | 260.6324 | 299.984 | 2.841%
4767 | 17-73 | -73.0994 | 17.4428 | 837.217 | 159.9855 | 187.9147 | 226.1921 | 260.2549 | 299.455 | 2.834%
4768 | 17-73.5 | -73.3707 | 17.4428 | 854.9418 | 160.0864 | 187.9457 | 226.1652 | 260.1681 | 299.291 | 2.844%
4769 | 17-73.5 | -73.642 | 17.4428 | 872.6763 | 160.3654 | 188.1033 | 226.3133 | 260.3023 | 299.4037 | 2.866%
4770 | 17-74 | -73.9134 | 17.4428 | 890.4198 | 160.6572 | 188.2729 | 226.4765 | 260.4542 | 299.5372 | 2.889%
4771 | 17-74 | -74.1847 | 17.4428 | 908.1719 | 160.8004 | 188.3528 | 226.5508 | 260.5206 | 299.5914 | 2.9%
4772 | 17-74.5 | -74.456 | 17.4428 | 925.9319 | 160.7675 | 188.3241 | 226.5028 | 260.4534 | 299.4999 | 2.898%
4773 | 17-74.5 | -74.7273 | 17.4428 | 943.6995 | 160.5423 | 188.1711 | 226.2952 | 260.1933 | 299.1752 | 2.882%
4774 | 17-75 | -74.9986 | 17.4428 | 961.4741 | 160.408 | 188.0954 | 226.2182 | 260.1161 | 299.099 | 2.871%
4775 | 17-75.5 | -75.27 | 17.4428 | 979.2553 | 160.3445 | 188.0744 | 226.2297 | 260.1606 | 299.1856 | 2.866%
4776 | 17-75.5 | -75.5413 | 17.4428 | 997.0428 | 160.3496 | 188.0963 | 226.2972 | 260.2737 | 299.3556 | 2.865%
4777 | 17-76 | -75.8126 | 17.4428 | 1014.8362 | 160.6422 | 188.3093 | 226.63 | 260.7227 | 299.9481 | 2.885%
4778 | 17-76 | -76.0839 | 17.4428 | 1032.6352 | 161.1782 | 188.685 | 227.1788 | 261.4376 | 300.8663 | 2.922%
4779 | 17-76.5 | -76.3553 | 17.4428 | 1050.4393 | 161.8428 | 189.1453 | 227.8244 | 262.2597 | 301.9029 | 2.971%
4780 | 17-76.5 | -76.6266 | 17.4428 | 1068.2485 | 162.4229 | 189.5527 | 228.3893 | 262.9741 | 302.7986 | 3.014%
4781 | 17-77 | -76.8979 | 17.4428 | 1086.0623 | 162.8879 | 189.8906 | 228.8485 | 263.5478 | 303.5105 | 3.049%
4782 | 17-77 | -77.1692 | 17.4428 | 1103.8805 | 163.2605 | 190.1764 | 229.2256 | 264.0102 | 304.0752 | 3.078%
4783 | 17-77.5 | -77.4405 | 17.4428 | 1121.7029 | 163.6984 | 190.5237 | 229.6798 | 264.5642 | 304.7485 | 3.113%
4784 | 17-77.5 | -77.7119 | 17.4428 | 1139.5292 | 164.1702 | 190.9039 | 230.1637 | 265.1437 | 305.4412 | 3.152%
4785 | 17-78 | -77.9832 | 17.4428 | 1157.3592 | 164.6662 | 191.3078 | 230.665 | 265.7333 | 306.1344 | 3.194%
4786 | 17-78.5 | -78.2545 | 17.4428 | 1175.1928 | 165.2224 | 191.7763 | 231.2538 | 266.4325 | 306.9637 | 3.242%
4787 | 17-78.5 | -78.5258 | 17.4428 | 1193.0297 | 165.7925 | 192.2669 | 231.8584 | 267.1404 | 307.7924 | 3.292%
4788 | 17-79 | -78.7971 | 17.4428 | 1210.8698 | 166.3646 | 192.7687 | 232.4635 | 267.8374 | 308.5953 | 3.344%
4789 | 17-79 | -79.0685 | 17.4428 | 1228.7128 | 166.969 | 193.3212 | 233.1372 | 268.6203 | 309.5051 | 3.4%
4790 | 17-79.5 | -79.3398 | 17.4428 | 1246.5587 | 167.5612 | 193.8838 | 233.8155 | 269.4018 | 310.4054 | 3.456%
4791 | 17-79.5 | -79.6111 | 17.4428 | 1264.4073 | 168.1472 | 194.4609 | 234.5104 | 270.2016 | 311.326 | 3.513%
4792 | 17-80 | -79.8824 | 17.4428 | 1282.2583 | 168.7712 | 195.0948 | 235.2946 | 271.1223 | 312.4067 | 3.574%
4793 | 17-80 | -80.1537 | 17.4428 | 1300.1118 | 169.3777 | 195.7182 | 236.0727 | 272.0419 | 313.493 | 3.634%
4794 | 17-80.5 | -80.4251 | 17.4428 | 1317.9675 | 169.9525 | 196.3152 | 236.8232 | 272.9334 | 314.5511 | 3.691%
4795 | 17-80.5 | -80.6964 | 17.4428 | 1335.8253 | 170.5108 | 196.9057 | 237.5752 | 273.8347 | 315.6298 | 3.746%
4796 | 17-81 | -80.9677 | 17.4428 | 1353.6852 | 171.0182 | 197.4556 | 238.2845 | 274.6923 | 316.6644 | 3.797%
4797 | 17-81 | -81.239 | 17.4428 | 1371.547 | 171.482 | 197.9804 | 238.9801 | 275.5487 | 317.7147 | 3.843%
4798 | 17-81.5 | -81.5104 | 17.4428 | 1389.4105 | 171.9158 | 198.5035 | 239.7003 | 276.4567 | 318.8517 | 3.884%
4799 | 17-82 | -81.7817 | 17.4428 | 1407.2758 | 172.2403 | 198.9335 | 240.307 | 277.2331 | 319.8359 | 3.915%
4800 | 17-82 | -82.053 | 17.4428 | 1425.1426 | 172.4679 | 199.2878 | 240.8352 | 277.9305 | 320.7422 | 3.935%
4801 | 17-82.5 | -82.3243 | 17.4428 | 1443.011 | 172.6207 | 199.6001 | 241.3441 | 278.6328 | 321.6862 | 3.945%
4802 | 17-82.5 | -82.5956 | 17.4428 | 1460.8808 | 172.6509 | 199.7954 | 241.7174 | 279.1841 | 322.4619 | 3.942%
4803 | 17-83 | -82.867 | 17.4428 | 1478.7519 | 172.5795 | 199.898 | 241.9946 | 279.6383 | 323.1418 | 3.927%
4804 | 17-83 | -83.1383 | 17.4428 | 1496.6243 | 172.4286 | 199.9343 | 242.2167 | 280.0512 | 323.7998 | 3.903%
4805 | 17-83.5 | -83.4096 | 17.4428 | 1514.4978 | 172.1312 | 199.8192 | 242.246 | 280.2329 | 324.1811 | 3.864%
4806 | 17-83.5 | -83.6809 | 17.4428 | 1532.3724 | 171.7301 | 199.6061 | 242.1555 | 280.2752 | 324.4002 | 3.816%
4807 | 17-84 | -83.9522 | 17.4428 | 1550.2481 | 171.2539 | 199.3298 | 241.9966 | 280.2458 | 324.545 | 3.761%
4808 | 17-84 | -84.2236 | 17.4428 | 1568.1247 | 170.6255 | 198.9188 | 241.6728 | 280.0243 | 324.4662 | 3.692%
4809 | 17-84.5 | -84.4949 | 17.4428 | 1586.0022 | 169.8633 | 198.3962 | 241.2146 | 279.6483 | 324.21 | 3.613%
4810 | 17-85 | -84.7662 | 17.4428 | 1603.8806 | 168.9792 | 197.7723 | 240.636 | 279.1353 | 323.7983 | 3.525%
4811 | 17-85 | -85.0375 | 17.4428 | 1621.7597 | 167.8886 | 196.9585 | 239.793 | 278.2864 | 322.9632 | 3.423%
4812 | 17-85.5 | -85.3089 | 17.4428 | 1639.6395 | 166.6601 | 196.0298 | 238.8163 | 277.2786 | 321.9392 | 3.312%
4813 | 17-85.5 | -85.5802 | 17.4428 | 1657.5199 | 165.308 | 194.9973 | 237.7362 | 276.1545 | 320.7849 | 3.195%
4814 | 17-86 | -85.8515 | 17.4428 | 1675.4009 | 163.6157 | 193.7245 | 236.2917 | 274.5705 | 319.054 | 3.059%
4815 | 17-86 | -86.1228 | 17.4428 | 1693.2825 | 161.6029 | 192.2631 | 234.6073 | 272.6992 | 316.9797 | 2.907%
4816 | 17-86.5 | -86.3941 | 17.4428 | 1711.1646 | 159.268 | 190.5989 | 232.6662 | 270.5222 | 314.5418 | 2.742%
4817 | 17-86.5 | -86.6655 | 17.4428 | 1729.0471 | 156.2192 | 188.3581 | 229.9534 | 267.3494 | 310.8314 | 2.543%
4818 | 17-87 | -86.9368 | 17.4428 | 1746.93 | 152.5794 | 185.3926 | 226.625 | 263.4014 | 306.1512 | 2.318%
4819 | 17-87 | -87.2081 | 17.4428 | 1764.8132 | 148.454 | 181.7319 | 222.772 | 258.8027 | 300.6677 | 2.081%
4820 | 17-87.5 | -87.4794 | 17.4428 | 1782.6968 | 144.1392 | 177.7621 | 218.7069 | 253.9341 | 294.8435 | 1.858%
4821 | 17-88 | -87.7507 | 17.4428 | 1800.5806 | 139.7238 | 173.5695 | 214.5232 | 248.9147 | 288.8294 | 1.652%
4822 | 17-88 | -88.0221 | 17.4428 | 1818.4646 | 135.2465 | 169.207 | 210.2496 | 243.7844 | 282.6787 | 1.465%
4823 | 17-88.5 | -88.2934 | 17.4428 | 1836.3488 | 130.7827 | 164.7879 | 205.956 | 238.6242 | 276.4851 | 1.299%
4824 | 17-88.5 | -88.5647 | 17.4428 | 1854.2331 | 126.4364 | 160.4285 | 201.7921 | 233.6314 | 270.5053 | 1.155%
4825 | 17-89 | -88.836 | 17.4428 | 1872.1175 | 122.2032 | 156.129 | 197.7318 | 228.7672 | 264.6842 | 1.031%
4826 | 17-89 | -89.1074 | 17.4428 | 1890.0019 | 118.0256 | 151.8058 | 193.6716 | 223.8906 | 258.834 | 0.9208%
4827 | 17-89.5 | -89.3787 | 17.4428 | 1907.8864 | 114.1372 | 147.6233 | 189.8664 | 219.3737 | 253.4559 | 0.8286%
4828 | 17-89.5 | -89.65 | 17.4428 | 1925.7708 | 110.5664 | 143.5972 | 186.2505 | 215.128 | 248.4048 | 0.7511%
4829 | 17-90 | -89.9213 | 17.4428 | 1943.6552 | 107.3383 | 139.7808 | 182.8761 | 211.2048 | 243.7431 | 0.6864%
4830 | 17-90 | -90.1926 | 17.4428 | 1961.5395 | 104.8681 | 136.5912 | 180.289 | 208.3372 | 240.4468 | 0.6404%
4831 | 17-90.5 | -90.464 | 17.4428 | 1979.4237 | 103.1343 | 134.3098 | 178.5468 | 206.5264 | 238.4931 | 0.6109%
4832 | 17-90.5 | -90.7353 | 17.4428 | 1997.3077 | 102.0717 | 132.952 | 177.6329 | 205.6689 | 237.7122 | 0.595%
4833 | 18-50 | -50.0371 | 17.7141 | 719.6395 | 151.6056 | 182.0735 | 217.288 | 248.3867 | 283.9385 | 2.303%
4834 | 18-50.5 | -50.3084 | 17.7141 | 702.1297 | 152.1853 | 182.4719 | 217.9018 | 249.2079 | 285.0141 | 2.338%
4835 | 18-50.5 | -50.5797 | 17.7141 | 684.643 | 152.702 | 182.8364 | 218.4783 | 249.9896 | 286.048 | 2.368%
4836 | 18-51 | -50.851 | 17.7141 | 667.1812 | 153.1883 | 183.1863 | 219.0417 | 250.7601 | 287.0738 | 2.397%
4837 | 18-51 | -51.1224 | 17.7141 | 649.7463 | 153.6841 | 183.5464 | 219.6249 | 251.56 | 288.1411 | 2.427%
4838 | 18-51.5 | -51.3937 | 17.7141 | 632.3406 | 154.1275 | 183.8718 | 220.1567 | 252.2928 | 289.1223 | 2.454%
4839 | 18-51.5 | -51.665 | 17.7141 | 614.9666 | 154.5469 | 184.183 | 220.6735 | 253.0103 | 290.0883 | 2.479%
4840 | 18-52 | -51.9363 | 17.7141 | 597.6271 | 154.9714 | 184.5015 | 221.2119 | 253.7638 | 291.1086 | 2.504%
4841 | 18-52 | -52.2077 | 17.7141 | 580.3252 | 155.3337 | 184.7779 | 221.6926 | 254.4452 | 292.0396 | 2.525%
4842 | 18-52.5 | -52.479 | 17.7141 | 563.0645 | 155.6762 | 185.0419 | 222.1625 | 255.1174 | 292.9639 | 2.545%
4843 | 18-53 | -52.7503 | 17.7141 | 545.8488 | 156.0254 | 185.3133 | 222.652 | 255.8218 | 293.9362 | 2.565%
4844 | 18-53 | -53.0216 | 17.7141 | 528.6826 | 156.3195 | 185.5475 | 223.0917 | 256.4646 | 294.8326 | 2.582%
4845 | 18-53.5 | -53.2929 | 17.7141 | 511.571 | 156.6055 | 185.7765 | 223.5281 | 257.106 | 295.7305 | 2.598%
4846 | 18-53.5 | -53.5643 | 17.7141 | 494.5195 | 156.9039 | 186.0151 | 223.981 | 257.771 | 296.6609 | 2.614%
4847 | 18-54 | -53.8356 | 17.7141 | 477.5348 | 157.1514 | 186.2169 | 224.3779 | 258.3616 | 297.4945 | 2.628%
4848 | 18-54 | -54.1069 | 17.7141 | 460.6241 | 157.3959 | 186.415 | 224.7668 | 258.9402 | 298.311 | 2.641%
4849 | 18-54.5 | -54.3782 | 17.7141 | 443.796 | 157.655 | 186.6218 | 225.164 | 259.5264 | 299.1346 | 2.655%
4850 | 18-54.5 | -54.6495 | 17.7141 | 427.0604 | 157.8898 | 186.8119 | 225.5317 | 260.0708 | 299.9008 | 2.668%
4851 | 18-55 | -54.9209 | 17.7141 | 410.4284 | 158.1687 | 187.036 | 225.9475 | 260.6771 | 300.7462 | 2.684%
4852 | 18-55 | -55.1922 | 17.7141 | 393.9134 | 158.5015 | 187.3028 | 226.4225 | 261.3583 | 301.6859 | 2.703%
4853 | 18-55.5 | -55.4635 | 17.7141 | 377.5307 | 158.8185 | 187.5544 | 226.8595 | 261.9789 | 302.5362 | 2.722%
4854 | 18-55.5 | -55.7348 | 17.7141 | 361.2983 | 159.1894 | 187.8454 | 227.344 | 262.654 | 303.4496 | 2.745%
4855 | 18-56 | -56.0061 | 17.7141 | 345.2374 | 159.6086 | 188.1779 | 227.8775 | 263.3852 | 304.427 | 2.771%
4856 | 18-56.5 | -56.2775 | 17.7141 | 329.3732 | 160.0071 | 188.4915 | 228.3643 | 264.0413 | 305.2934 | 2.797%
4857 | 18-56.5 | -56.5488 | 17.7141 | 313.7356 | 160.4472 | 188.8362 | 228.8789 | 264.7211 | 306.1776 | 2.826%
4858 | 18-57 | -56.8201 | 17.7141 | 298.3601 | 160.9207 | 189.2107 | 229.418 | 265.4193 | 307.0714 | 2.858%
4859 | 18-57 | -57.0914 | 17.7141 | 283.2896 | 161.3857 | 189.5711 | 229.9132 | 266.0432 | 307.8523 | 2.891%
4860 | 18-57.5 | -57.3628 | 17.7141 | 268.5753 | 161.9062 | 189.9717 | 230.447 | 266.703 | 308.6645 | 2.929%
4861 | 18-57.5 | -57.6341 | 17.7141 | 254.2792 | 162.4724 | 190.408 | 231.0123 | 267.3887 | 309.4946 | 2.971%
4862 | 18-58 | -57.9054 | 17.7141 | 240.4759 | 163.0458 | 190.8431 | 231.5495 | 268.0189 | 310.2338 | 3.015%
4863 | 18-58 | -58.1767 | 17.7141 | 227.2553 | 163.6639 | 191.3091 | 232.1031 | 268.6495 | 310.9522 | 3.064%
4864 | 18-58.5 | -58.448 | 17.7141 | 214.7249 | 164.2974 | 191.7902 | 232.6491 | 269.2488 | 311.6082 | 3.116%
4865 | 18-58.5 | -58.7194 | 17.7141 | 203.0128 | 164.9034 | 192.2435 | 233.1254 | 269.7359 | 312.0982 | 3.168%
4866 | 18-59 | -58.9907 | 17.7141 | 192.2684 | 165.5457 | 192.7332 | 233.6346 | 270.2514 | 312.6098 | 3.225%
4867 | 18-59.5 | -59.262 | 17.7141 | 182.6627 | 166.2123 | 193.265 | 234.1831 | 270.8021 | 313.1501 | 3.286%
4868 | 18-59.5 | -59.5333 | 17.7141 | 174.384 | 166.9161 | 193.8558 | 234.794 | 271.4168 | 313.7551 | 3.354%
4869 | 18-60 | -59.8046 | 17.7141 | 167.629 | 167.7213 | 194.5743 | 235.5744 | 272.2406 | 314.617 | 3.431%
4870 | 18-60 | -60.076 | 17.7141 | 162.5877 | 168.5498 | 195.3289 | 236.3981 | 273.114 | 315.5359 | 3.514%
4871 | 18-60.5 | -60.3473 | 17.7141 | 159.4228 | 169.2908 | 195.9784 | 237.0719 | 273.7946 | 316.2092 | 3.59%
4872 | 18-60.5 | -60.6186 | 17.7141 | 158.247 | 169.9785 | 196.5727 | 237.6744 | 274.3889 | 316.7786 | 3.664%
4873 | 18-61 | -60.8899 | 17.7141 | 159.1043 | 170.6141 | 197.1209 | 238.2156 | 274.9077 | 317.2555 | 3.734%
4874 | 18-61 | -61.1613 | 17.7141 | 161.9625 | 171.2115 | 197.6461 | 238.7262 | 275.3888 | 317.6859 | 3.803%
4875 | 18-61.5 | -61.4326 | 17.7141 | 166.7186 | 171.7981 | 198.1876 | 239.2703 | 275.9204 | 318.1885 | 3.871%
4876 | 18-61.5 | -61.7039 | 17.7141 | 173.2165 | 172.3428 | 198.712 | 239.8043 | 276.4498 | 318.6992 | 3.936%
4877 | 18-62 | -61.9752 | 17.7141 | 181.2688 | 172.8374 | 199.2032 | 240.3099 | 276.9565 | 319.1953 | 3.996%
4878 | 18-62 | -62.2465 | 17.7141 | 190.6787 | 173.3204 | 199.7093 | 240.8599 | 277.5373 | 319.8033 | 4.054%
4879 | 18-62.5 | -62.5179 | 17.7141 | 201.256 | 173.8172 | 200.2627 | 241.4989 | 278.2484 | 320.5936 | 4.113%
4880 | 18-63 | -62.7892 | 17.7141 | 212.8265 | 174.358 | 200.891 | 242.2648 | 279.1382 | 321.6269 | 4.176%
4881 | 18-63 | -63.0605 | 17.7141 | 225.2373 | 174.9376 | 201.5882 | 243.153 | 280.203 | 322.9022 | 4.241%
4882 | 18-63.5 | -63.3318 | 17.7141 | 238.3571 | 175.3953 | 202.1433 | 243.8669 | 281.0648 | 323.9406 | 4.292%
4883 | 18-63.5 | -63.6031 | 17.7141 | 252.0752 | 175.6918 | 202.5041 | 244.3326 | 281.6281 | 324.6206 | 4.326%
4884 | 18-64 | -63.8745 | 17.7141 | 266.2991 | 175.9439 | 202.8232 | 244.7633 | 282.1645 | 325.285 | 4.353%
4885 | 18-64 | -64.1458 | 17.7141 | 280.952 | 176.1767 | 203.1311 | 245.1981 | 282.7209 | 325.9899 | 4.376%
4886 | 18-64.5 | -64.4171 | 17.7141 | 295.9702 | 176.3927 | 203.4311 | 245.6417 | 283.3036 | 326.7439 | 4.396%
4887 | 18-64.5 | -64.6884 | 17.7141 | 311.3008 | 176.5771 | 203.707 | 246.0756 | 283.8921 | 327.5244 | 4.411%
4888 | 18-65 | -64.9598 | 17.7141 | 326.8998 | 176.6978 | 203.9076 | 246.4163 | 284.3709 | 328.1758 | 4.418%
4889 | 18-65 | -65.2311 | 17.7141 | 342.7305 | 176.7644 | 204.0408 | 246.6673 | 284.7393 | 328.6918 | 4.419%
4890 | 18-65.5 | -65.5024 | 17.7141 | 358.7622 | 176.8029 | 204.1394 | 246.873 | 285.0522 | 329.1404 | 4.418%
4891 | 18-66 | -65.7737 | 17.7141 | 374.9692 | 176.7811 | 204.1631 | 246.9798 | 285.2439 | 329.4406 | 4.409%
4892 | 18-66 | -66.045 | 17.7141 | 391.3295 | 176.6584 | 204.0628 | 246.9247 | 285.2382 | 329.5011 | 4.39%
4893 | 18-66.5 | -66.3164 | 17.7141 | 407.8248 | 176.4075 | 203.8067 | 246.6689 | 284.99 | 329.269 | 4.356%
4894 | 18-66.5 | -66.5877 | 17.7141 | 424.4393 | 175.9167 | 203.2402 | 245.9838 | 284.1985 | 328.3544 | 4.298%
4895 | 18-67 | -66.859 | 17.7141 | 441.1595 | 175.3069 | 202.5304 | 245.1033 | 283.1622 | 327.1348 | 4.228%
4896 | 18-67 | -67.1303 | 17.7141 | 457.9737 | 174.6367 | 201.8217 | 244.2331 | 282.1459 | 325.9478 | 4.154%
4897 | 18-67.5 | -67.4016 | 17.7141 | 474.872 | 173.9845 | 201.1581 | 243.4242 | 281.2063 | 324.8562 | 4.082%
4898 | 18-67.5 | -67.673 | 17.7141 | 491.8456 | 173.3395 | 200.5125 | 242.6414 | 280.3005 | 323.808 | 4.012%
4899 | 18-68 | -67.9443 | 17.7141 | 508.887 | 172.6886 | 199.8665 | 241.8627 | 279.4035 | 322.7746 | 3.942%
4900 | 18-68 | -68.2156 | 17.7141 | 525.9896 | 171.9049 | 199.0822 | 240.888 | 278.2549 | 321.4214 | 3.862%
4901 | 18-68.5 | -68.4869 | 17.7141 | 543.1476 | 170.9755 | 198.1964 | 239.7828 | 276.9491 | 319.8791 | 3.769%
4902 | 18-69 | -68.7583 | 17.7141 | 560.3558 | 169.916 | 197.2336 | 238.5912 | 275.5494 | 318.2355 | 3.666%
4903 | 18-69 | -69.0296 | 17.7141 | 577.6097 | 168.7491 | 196.181 | 237.2754 | 273.9927 | 316.395 | 3.556%
4904 | 18-69.5 | -69.3009 | 17.7141 | 594.9054 | 167.5113 | 195.0773 | 235.8866 | 272.342 | 314.4345 | 3.443%
4905 | 18-69.5 | -69.5722 | 17.7141 | 612.2392 | 166.2186 | 193.9357 | 234.4426 | 270.6192 | 312.3813 | 3.329%
4906 | 18-70 | -69.8435 | 17.7141 | 629.608 | 164.8335 | 192.7116 | 232.8681 | 268.7191 | 310.0927 | 3.211%
4907 | 18-70 | -70.1149 | 17.7141 | 647.0088 | 163.4737 | 191.5581 | 231.3908 | 266.9417 | 307.9581 | 3.099%
4908 | 18-70.5 | -70.3862 | 17.7141 | 664.4393 | 162.1955 | 190.5229 | 230.0789 | 265.3751 | 306.0897 | 2.998%
4909 | 18-70.5 | -70.6575 | 17.7141 | 681.897 | 161.3213 | 189.7837 | 229.1422 | 264.2564 | 304.7552 | 2.929%
4910 | 18-71 | -70.9288 | 17.7141 | 699.3799 | 160.7982 | 189.2991 | 228.5372 | 263.5415 | 303.9114 | 2.888%
4911 | 18-71 | -71.2001 | 17.7141 | 716.8862 | 160.5885 | 189.0367 | 228.2222 | 263.1809 | 303.4994 | 2.87%
4912 | 18-71.5 | -71.4715 | 17.7141 | 734.414 | 160.3475 | 188.7397 | 227.8282 | 262.6963 | 302.9066 | 2.85%
4913 | 18-71.5 | -71.7428 | 17.7141 | 751.962 | 160.2109 | 188.5481 | 227.5613 | 262.3584 | 302.4831 | 2.84%
4914 | 18-72 | -72.0141 | 17.7141 | 769.5286 | 160.1976 | 188.4508 | 227.4062 | 262.1477 | 302.204 | 2.838%
4915 | 18-72.5 | -72.2854 | 17.7141 | 787.1126 | 160.1028 | 188.2995 | 227.1511 | 261.7908 | 301.7209 | 2.832%
4916 | 18-72.5 | -72.5568 | 17.7141 | 804.7128 | 159.9244 | 188.11 | 226.8411 | 261.3633 | 301.1478 | 2.82%
4917 | 18-73 | -72.8281 | 17.7141 | 822.3282 | 159.7318 | 187.9233 | 226.5322 | 260.9351 | 300.572 | 2.808%
4918 | 18-73 | -73.0994 | 17.7141 | 839.9578 | 159.7419 | 187.8826 | 226.4084 | 260.728 | 300.2598 | 2.81%
4919 | 18-73.5 | -73.3707 | 17.7141 | 857.6006 | 160.0126 | 188.0319 | 226.5435 | 260.845 | 300.3504 | 2.831%
4920 | 18-73.5 | -73.642 | 17.7141 | 875.2558 | 160.4942 | 188.3303 | 226.8804 | 261.2133 | 300.752 | 2.867%
4921 | 18-74 | -73.9134 | 17.7141 | 892.9227 | 161.0042 | 188.6523 | 227.2438 | 261.6103 | 301.1844 | 2.906%
4922 | 18-74 | -74.1847 | 17.7141 | 910.6005 | 161.2834 | 188.8201 | 227.4254 | 261.8014 | 301.3839 | 2.928%
4923 | 18-74.5 | -74.456 | 17.7141 | 928.2886 | 161.3015 | 188.8156 | 227.3921 | 261.7386 | 301.2831 | 2.93%
4924 | 18-74.5 | -74.7273 | 17.7141 | 945.9864 | 161.0553 | 188.6322 | 227.1202 | 261.38 | 300.8167 | 2.913%
4925 | 18-75 | -74.9986 | 17.7141 | 963.6933 | 160.903 | 188.5294 | 226.9829 | 261.2092 | 300.6044 | 2.902%
4926 | 18-75.5 | -75.27 | 17.7141 | 981.4087 | 160.8271 | 188.4851 | 226.938 | 261.1641 | 300.5591 | 2.896%
4927 | 18-75.5 | -75.5413 | 17.7141 | 999.1323 | 160.8291 | 188.4885 | 226.9539 | 261.1917 | 300.6006 | 2.896%
4928 | 18-76 | -75.8126 | 17.7141 | 1016.8635 | 161.1304 | 188.6906 | 227.2449 | 261.5673 | 301.0791 | 2.917%
4929 | 18-76 | -76.0839 | 17.7141 | 1034.602 | 161.6866 | 189.0626 | 227.7618 | 262.2216 | 301.8996 | 2.957%
4930 | 18-76.5 | -76.3553 | 17.7141 | 1052.3472 | 162.3785 | 189.5261 | 228.3869 | 262.9984 | 302.859 | 3.009%
4931 | 18-76.5 | -76.6266 | 17.7141 | 1070.0989 | 162.9876 | 189.943 | 228.9436 | 263.6862 | 303.7039 | 3.055%
4932 | 18-77 | -76.8979 | 17.7141 | 1087.8567 | 163.4809 | 190.2948 | 229.4043 | 264.2481 | 304.3867 | 3.094%
4933 | 18-77 | -77.1692 | 17.7141 | 1105.6203 | 163.8828 | 190.5997 | 229.7931 | 264.714 | 304.9436 | 3.126%
4934 | 18-77.5 | -77.4405 | 17.7141 | 1123.3893 | 164.3606 | 190.9787 | 230.2797 | 265.3001 | 305.6479 | 3.165%
4935 | 18-77.5 | -77.7119 | 17.7141 | 1141.1636 | 164.8805 | 191.4001 | 230.8108 | 265.9317 | 306.3979 | 3.209%
4936 | 18-78 | -77.9832 | 17.7141 | 1158.9427 | 165.4277 | 191.85 | 231.3661 | 266.5823 | 307.1598 | 3.256%
4937 | 18-78.5 | -78.2545 | 17.7141 | 1176.7264 | 166.0314 | 192.3654 | 232.0105 | 267.3444 | 308.0605 | 3.309%
4938 | 18-78.5 | -78.5258 | 17.7141 | 1194.5146 | 166.6465 | 192.9046 | 232.6737 | 268.1199 | 308.9669 | 3.365%
4939 | 18-79 | -78.7971 | 17.7141 | 1212.307 | 167.2607 | 193.4571 | 233.3421 | 268.8919 | 309.8585 | 3.422%
4940 | 18-79 | -79.0685 | 17.7141 | 1230.1033 | 167.9003 | 194.0617 | 234.0847 | 269.7591 | 310.8712 | 3.482%
4941 | 18-79.5 | -79.3398 | 17.7141 | 1247.9034 | 168.5199 | 194.6741 | 234.8289 | 270.6216 | 311.8708 | 3.543%
4942 | 18-79.5 | -79.6111 | 17.7141 | 1265.7071 | 169.1251 | 195.2965 | 235.5815 | 271.4907 | 312.8744 | 3.603%
4943 | 18-80 | -79.8824 | 17.7141 | 1283.5141 | 169.762 | 195.9713 | 236.4145 | 272.4673 | 314.0191 | 3.667%
4944 | 18-80 | -80.1537 | 17.7141 | 1301.3244 | 170.3798 | 196.6311 | 237.2319 | 273.4281 | 315.1482 | 3.73%
4945 | 18-80.5 | -80.4251 | 17.7141 | 1319.1377 | 170.9672 | 197.2623 | 238.0151 | 274.3497 | 316.2323 | 3.791%
4946 | 18-80.5 | -80.6964 | 17.7141 | 1336.9539 | 171.5406 | 197.8868 | 238.7963 | 275.2744 | 317.3261 | 3.851%
4947 | 18-81 | -80.9677 | 17.7141 | 1354.7729 | 172.0695 | 198.4707 | 239.5314 | 276.1485 | 318.3646 | 3.906%
4948 | 18-81 | -81.239 | 17.7141 | 1372.5945 | 172.5636 | 199.0328 | 240.2556 | 277.0235 | 319.4197 | 3.957%
4949 | 18-81.5 | -81.5104 | 17.7141 | 1390.4186 | 173.0384 | 199.6 | 241.0125 | 277.9597 | 320.5727 | 4.006%
4950 | 18-82 | -81.7817 | 17.7141 | 1408.245 | 173.4298 | 200.0886 | 241.6754 | 278.788 | 321.6021 | 4.045%
4951 | 18-82 | -82.053 | 17.7141 | 1426.0736 | 173.7516 | 200.5175 | 242.2805 | 279.5624 | 322.5838 | 4.076%
4952 | 18-82.5 | -82.3243 | 17.7141 | 1443.9043 | 174.0237 | 200.9201 | 242.8853 | 280.364 | 323.629 | 4.1%
4953 | 18-82.5 | -82.5956 | 17.7141 | 1461.7371 | 174.1828 | 201.2069 | 243.3546 | 281.0133 | 324.503 | 4.111%
4954 | 18-83 | -82.867 | 17.7141 | 1479.5717 | 174.2465 | 201.4035 | 243.7324 | 281.5724 | 325.2908 | 4.11%
4955 | 18-83 | -83.1383 | 17.7141 | 1497.4081 | 174.2368 | 201.5386 | 244.0649 | 282.1046 | 326.0773 | 4.099%
4956 | 18-83.5 | -83.4096 | 17.7141 | 1515.2462 | 174.0851 | 201.5209 | 244.2055 | 282.409 | 326.5935 | 4.073%
4957 | 18-83.5 | -83.6809 | 17.7141 | 1533.0859 | 173.8309 | 201.403 | 244.226 | 282.5757 | 326.9519 | 4.036%
4958 | 18-84 | -83.9522 | 17.7141 | 1550.9271 | 173.5015 | 201.2195 | 244.1771 | 282.6712 | 327.2383 | 3.992%
4959 | 18-84 | -84.2236 | 17.7141 | 1568.7698 | 173.0256 | 200.9017 | 243.967 | 282.5818 | 327.3129 | 3.933%
4960 | 18-84.5 | -84.4949 | 17.7141 | 1586.6138 | 172.4187 | 200.4724 | 243.6259 | 282.3448 | 327.2213 | 3.862%
4961 | 18-85 | -84.7662 | 17.7141 | 1604.459 | 171.6908 | 199.9416 | 243.1675 | 281.9772 | 326.9851 | 3.781%
4962 | 18-85 | -85.0375 | 17.7141 | 1622.3054 | 170.7669 | 199.2269 | 242.4612 | 281.301 | 326.3665 | 3.685%
4963 | 18-85.5 | -85.3089 | 17.7141 | 1640.153 | 169.7006 | 198.404 | 241.625 | 280.4759 | 325.5775 | 3.578%
4964 | 18-85.5 | -85.5802 | 17.7141 | 1658.0015 | 168.4979 | 197.4844 | 240.6797 | 279.5319 | 324.6597 | 3.464%
4965 | 18-86 | -85.8515 | 17.7141 | 1675.8511 | 166.8374 | 196.1903 | 239.2161 | 277.9317 | 322.9168 | 3.318%
4966 | 18-86 | -86.1228 | 17.7141 | 1693.7015 | 164.7238 | 194.6115 | 237.376 | 275.8684 | 320.6064 | 3.145%
4967 | 18-86.5 | -86.3941 | 17.7141 | 1711.5528 | 162.1772 | 192.748 | 235.1631 | 273.3498 | 317.7412 | 2.95%
4968 | 18-86.5 | -86.6655 | 17.7141 | 1729.4049 | 158.9749 | 190.356 | 232.2522 | 269.9345 | 313.7347 | 2.725%
4969 | 18-87 | -86.9368 | 17.7141 | 1747.2577 | 155.2333 | 187.3352 | 228.8015 | 265.8447 | 308.89 | 2.479%
4970 | 18-87 | -87.2081 | 17.7141 | 1765.1112 | 151.044 | 183.7006 | 224.8878 | 261.1859 | 303.3486 | 2.223%
4971 | 18-87.5 | -87.4794 | 17.7141 | 1782.9652 | 146.6606 | 179.7662 | 220.7657 | 256.2634 | 297.4763 | 1.982%
4972 | 18-88 | -87.7507 | 17.7141 | 1800.8199 | 142.1662 | 175.6052 | 216.5228 | 251.1882 | 291.4124 | 1.759%
4973 | 18-88 | -88.0221 | 17.7141 | 1818.675 | 137.597 | 171.2655 | 212.1825 | 245.9934 | 285.2017 | 1.557%
4974 | 18-88.5 | -88.2934 | 17.7141 | 1836.5306 | 133.02 | 166.8458 | 207.7995 | 240.7394 | 278.9107 | 1.377%
4975 | 18-88.5 | -88.5647 | 17.7141 | 1854.3866 | 128.5278 | 162.4523 | 203.5057 | 235.5985 | 272.762 | 1.22%
4976 | 18-89 | -88.836 | 17.7141 | 1872.2429 | 124.1251 | 158.088 | 199.2846 | 230.5445 | 266.717 | 1.084%
4977 | 18-89 | -89.1074 | 17.7141 | 1890.0996 | 119.7879 | 153.7101 | 195.0737 | 225.4889 | 260.6542 | 0.9643%
4978 | 18-89.5 | -89.3787 | 17.7141 | 1907.9565 | 115.8536 | 149.6213 | 191.2722 | 220.9915 | 255.3167 | 0.8672%
4979 | 18-89.5 | -89.65 | 17.7141 | 1925.8137 | 112.3723 | 145.7947 | 187.8051 | 216.953 | 250.546 | 0.7885%
4980 | 18-90 | -89.9213 | 17.7141 | 1943.671 | 109.3222 | 142.2388 | 184.6708 | 213.3527 | 246.3111 | 0.7246%
4981 | 18-90 | -90.1926 | 17.7141 | 1961.5285 | 106.9475 | 139.2304 | 182.2205 | 210.6686 | 243.2563 | 0.6781%
4982 | 18-90.5 | -90.464 | 17.7141 | 1979.386 | 105.2289 | 136.9998 | 180.5104 | 208.9021 | 241.3623 | 0.6471%
4983 | 18-90.5 | -90.7353 | 17.7141 | 1997.2437 | 104.107 | 135.566 | 179.5314 | 207.9615 | 240.4763 | 0.6289%
4984 | 18-50 | -50.0371 | 17.9854 | 723.4952 | 151.2751 | 181.9353 | 217.0762 | 248.1039 | 283.5684 | 2.285%
4985 | 18-50.5 | -50.3084 | 17.9854 | 706.1069 | 151.9316 | 182.3731 | 217.7319 | 248.9688 | 284.6891 | 2.324%
4986 | 18-50.5 | -50.5797 | 17.9854 | 688.747 | 152.522 | 182.7752 | 218.3482 | 249.7913 | 285.7645 | 2.359%
4987 | 18-51 | -50.851 | 17.9854 | 671.4177 | 153.0787 | 183.1607 | 218.9485 | 250.5992 | 286.8274 | 2.393%
4988 | 18-51 | -51.1224 | 17.9854 | 654.1214 | 153.642 | 183.5549 | 219.5667 | 251.4341 | 287.929 | 2.427%
4989 | 18-51.5 | -51.3937 | 17.9854 | 636.8609 | 154.1498 | 183.9124 | 220.1303 | 252.1974 | 288.9383 | 2.457%
4990 | 18-51.5 | -51.665 | 17.9854 | 619.6392 | 154.6335 | 184.2558 | 220.6783 | 252.9444 | 289.9306 | 2.487%
4991 | 18-52 | -51.9363 | 17.9854 | 602.4598 | 155.1246 | 184.608 | 221.2495 | 253.7287 | 290.9785 | 2.517%
4992 | 18-52 | -52.2077 | 17.9854 | 585.3262 | 155.553 | 184.9192 | 221.7661 | 254.4459 | 291.9442 | 2.543%
4993 | 18-52.5 | -52.479 | 17.9854 | 568.2428 | 155.9617 | 185.2192 | 222.2742 | 255.1576 | 292.9087 | 2.567%
4994 | 18-53 | -52.7503 | 17.9854 | 551.2142 | 156.3778 | 185.5279 | 222.8044 | 255.9051 | 293.9261 | 2.592%
4995 | 18-53 | -53.0216 | 17.9854 | 534.2457 | 156.7392 | 185.8016 | 223.29 | 256.599 | 294.8794 | 2.613%
4996 | 18-53.5 | -53.2929 | 17.9854 | 517.3432 | 157.0916 | 186.0708 | 223.7738 | 257.2943 | 295.8384 | 2.634%
4997 | 18-53.5 | -53.5643 | 17.9854 | 500.5135 | 157.4543 | 186.3486 | 224.2736 | 258.0129 | 296.83 | 2.655%
4998 | 18-54 | -53.8356 | 17.9854 | 483.7641 | 157.7618 | 186.5871 | 224.7127 | 258.6502 | 297.7151 | 2.673%
4999 | 18-54 | -54.1069 | 17.9854 | 467.1038 | 158.0642 | 186.821 | 225.1423 | 259.2733 | 298.5803 | 2.69%
5000 | 18-54.5 | -54.3782 | 17.9854 | 450.5425 | 158.3793 | 187.0628 | 225.5792 | 259.9031 | 299.4512 | 2.708%
5001 | 18-54.5 | -54.6495 | 17.9854 | 434.0915 | 158.6665 | 187.287 | 225.9871 | 260.493 | 300.269 | 2.725%
5002 | 18-55 | -54.9209 | 17.9854 | 417.764 | 158.995 | 187.5444 | 226.4447 | 261.1487 | 301.1726 | 2.745%
5003 | 18-55 | -55.1922 | 17.9854 | 401.5749 | 159.375 | 187.8441 | 226.9635 | 261.8838 | 302.1784 | 2.768%
5004 | 18-55.5 | -55.4635 | 17.9854 | 385.5418 | 159.7356 | 188.1289 | 227.4491 | 262.5678 | 303.1104 | 2.79%
5005 | 18-55.5 | -55.7348 | 17.9854 | 369.685 | 160.1481 | 188.4543 | 227.9857 | 263.3125 | 304.1146 | 2.815%
5006 | 18-56 | -56.0061 | 17.9854 | 354.0282 | 160.6062 | 188.8217 | 228.5739 | 264.1174 | 305.1894 | 2.845%
5007 | 18-56.5 | -56.2775 | 17.9854 | 338.5992 | 161.0409 | 189.17 | 229.1152 | 264.8476 | 306.1542 | 2.874%
5008 | 18-56.5 | -56.5488 | 17.9854 | 323.4306 | 161.5132 | 189.5476 | 229.6815 | 265.5974 | 307.131 | 2.906%
5009 | 18-57 | -56.8201 | 17.9854 | 308.5609 | 162.0132 | 189.9528 | 230.2686 | 266.3605 | 308.1108 | 2.941%
5010 | 18-57 | -57.0914 | 17.9854 | 294.0355 | 162.4972 | 190.3395 | 230.8067 | 267.0435 | 308.9709 | 2.976%
5011 | 18-57.5 | -57.3628 | 17.9854 | 279.9079 | 163.0289 | 190.7635 | 231.3823 | 267.7632 | 309.8657 | 3.015%
5012 | 18-57.5 | -57.6341 | 17.9854 | 266.2415 | 163.5965 | 191.2193 | 231.987 | 268.5083 | 310.7805 | 3.058%
5013 | 18-58 | -57.9054 | 17.9854 | 253.1111 | 164.1586 | 191.6663 | 232.5566 | 269.1916 | 311.5991 | 3.102%
5014 | 18-58 | -58.1767 | 17.9854 | 240.6045 | 164.753 | 192.137 | 233.1343 | 269.8661 | 312.3868 | 3.15%
5015 | 18-58.5 | -58.448 | 17.9854 | 228.824 | 165.3504 | 192.616 | 233.6966 | 270.5008 | 313.1028 | 3.2%
5016 | 18-58.5 | -58.7194 | 17.9854 | 217.8875 | 165.9088 | 193.0606 | 234.1815 | 271.0147 | 313.6431 | 3.25%
5017 | 18-59 | -58.9907 | 17.9854 | 207.9281 | 166.4927 | 193.5348 | 234.6898 | 271.5445 | 314.1891 | 3.303%
5018 | 18-59.5 | -59.262 | 17.9854 | 199.0927 | 167.0852 | 194.032 | 235.2108 | 272.076 | 314.7218 | 3.359%
5019 | 18-59.5 | -59.5333 | 17.9854 | 191.5367 | 167.6804 | 194.543 | 235.7326 | 272.5945 | 315.2234 | 3.417%
5020 | 18-60 | -59.8046 | 17.9854 | 185.4167 | 168.3424 | 195.1373 | 236.3644 | 273.248 | 315.8902 | 3.483%
5021 | 18-60 | -60.076 | 17.9854 | 180.8786 | 169.02 | 195.7559 | 237.0231 | 273.9305 | 316.5881 | 3.552%
5022 | 18-60.5 | -60.3473 | 17.9854 | 178.0434 | 169.645 | 196.3098 | 237.5848 | 274.4847 | 317.1192 | 3.618%
5023 | 18-60.5 | -60.6186 | 17.9854 | 176.9928 | 170.2538 | 196.8508 | 238.1294 | 275.0179 | 317.6246 | 3.684%
5024 | 18-61 | -60.8899 | 17.9854 | 177.7586 | 170.8339 | 197.3695 | 238.6415 | 275.5089 | 318.0761 | 3.749%
5025 | 18-61 | -61.1613 | 17.9854 | 180.3176 | 171.3817 | 197.866 | 239.1212 | 275.9577 | 318.4731 | 3.813%
5026 | 18-61.5 | -61.4326 | 17.9854 | 184.5953 | 171.9275 | 198.3836 | 239.6381 | 276.4595 | 318.9432 | 3.877%
5027 | 18-61.5 | -61.7039 | 17.9854 | 190.4759 | 172.4404 | 198.8876 | 240.1476 | 276.9605 | 319.4212 | 3.938%
5028 | 18-62 | -61.9752 | 17.9854 | 197.8164 | 172.9114 | 199.3615 | 240.6307 | 277.44 | 319.8843 | 3.996%
5029 | 18-62 | -62.2465 | 17.9854 | 206.4612 | 173.3781 | 199.8536 | 241.1609 | 277.9955 | 320.4603 | 4.053%
5030 | 18-62.5 | -62.5179 | 17.9854 | 216.254 | 173.8663 | 200.3963 | 241.7835 | 278.6847 | 321.2216 | 4.111%
5031 | 18-63 | -62.7892 | 17.9854 | 227.0461 | 174.413 | 201.0304 | 242.5548 | 279.5791 | 322.2586 | 4.174%
5032 | 18-63 | -63.0605 | 17.9854 | 238.7022 | 175.0332 | 201.7769 | 243.5064 | 280.7205 | 323.6261 | 4.243%
5033 | 18-63.5 | -63.3318 | 17.9854 | 251.1018 | 175.566 | 202.425 | 244.3428 | 281.7325 | 324.8479 | 4.303%
5034 | 18-63.5 | -63.6031 | 17.9854 | 264.1404 | 175.9466 | 202.8908 | 244.9482 | 282.4681 | 325.7395 | 4.345%
5035 | 18-64 | -63.8745 | 17.9854 | 277.7277 | 176.251 | 203.2758 | 245.4675 | 283.1143 | 326.5396 | 4.378%
5036 | 18-64 | -64.1458 | 17.9854 | 291.7873 | 176.5049 | 203.6109 | 245.9394 | 283.7175 | 327.303 | 4.404%
5037 | 18-64.5 | -64.4171 | 17.9854 | 306.254 | 176.7256 | 203.9178 | 246.3938 | 284.3146 | 328.076 | 4.424%
5038 | 18-64.5 | -64.6884 | 17.9854 | 321.0729 | 176.9176 | 204.2044 | 246.8439 | 284.9248 | 328.885 | 4.439%
5039 | 18-65 | -64.9598 | 17.9854 | 336.1972 | 177.0464 | 204.4173 | 247.204 | 285.4301 | 329.5718 | 4.447%
5040 | 18-65 | -65.2311 | 17.9854 | 351.5875 | 177.1215 | 204.564 | 247.4774 | 285.8297 | 330.1301 | 4.449%
5041 | 18-65.5 | -65.5024 | 17.9854 | 367.2105 | 177.1693 | 204.6778 | 247.7088 | 286.179 | 330.6283 | 4.448%
5042 | 18-66 | -65.7737 | 17.9854 | 383.0375 | 177.1555 | 204.7147 | 247.838 | 286.4021 | 330.9715 | 4.44%
5043 | 18-66 | -66.045 | 17.9854 | 399.0443 | 177.0391 | 204.624 | 247.7986 | 286.4182 | 331.0614 | 4.421%
5044 | 18-66.5 | -66.3164 | 17.9854 | 415.2101 | 176.793 | 204.3741 | 247.5512 | 286.1807 | 330.8429 | 4.387%
5045 | 18-66.5 | -66.5877 | 17.9854 | 431.517 | 176.3067 | 203.8134 | 246.8741 | 285.3995 | 329.9414 | 4.33%
5046 | 18-67 | -66.859 | 17.9854 | 447.9495 | 175.7018 | 203.11 | 246.0029 | 284.3753 | 328.7374 | 4.261%
5047 | 18-67 | -67.1303 | 17.9854 | 464.4942 | 175.0371 | 202.4086 | 245.1432 | 283.3726 | 327.568 | 4.186%
5048 | 18-67.5 | -67.4016 | 17.9854 | 481.1396 | 174.3891 | 201.7505 | 244.3417 | 282.4423 | 326.4882 | 4.115%
5049 | 18-67.5 | -67.673 | 17.9854 | 497.8756 | 173.7466 | 201.1082 | 243.5638 | 281.543 | 325.4485 | 4.045%
5050 | 18-68 | -67.9443 | 17.9854 | 514.6932 | 173.0964 | 200.4639 | 242.7887 | 280.6515 | 324.4231 | 3.975%
5051 | 18-68 | -68.2156 | 17.9854 | 531.5847 | 172.2908 | 199.6522 | 241.7774 | 279.4576 | 323.0141 | 3.892%
5052 | 18-68.5 | -68.4869 | 17.9854 | 548.5433 | 171.3116 | 198.7094 | 240.5944 | 278.054 | 321.3496 | 3.794%
5053 | 18-69 | -68.7583 | 17.9854 | 565.5628 | 170.1599 | 197.6619 | 239.2859 | 276.5067 | 319.5209 | 3.683%
5054 | 18-69 | -69.0296 | 17.9854 | 582.638 | 168.8983 | 196.5245 | 237.8523 | 274.8006 | 317.4921 | 3.565%
5055 | 18-69.5 | -69.3009 | 17.9854 | 599.7639 | 167.5707 | 195.3411 | 236.3536 | 273.0109 | 315.3573 | 3.444%
5056 | 18-69.5 | -69.5722 | 17.9854 | 616.9364 | 166.1937 | 194.1257 | 234.8097 | 271.1635 | 313.1494 | 3.324%
5057 | 18-70 | -69.8435 | 17.9854 | 634.1517 | 164.7027 | 192.8155 | 233.1218 | 269.1243 | 310.6905 | 3.198%
5058 | 18-70 | -70.1149 | 17.9854 | 651.4063 | 163.2147 | 191.5596 | 231.5095 | 267.1813 | 308.3533 | 3.077%
5059 | 18-70.5 | -70.3862 | 17.9854 | 668.6971 | 161.7899 | 190.4075 | 230.0428 | 265.4239 | 306.2508 | 2.966%
5060 | 18-70.5 | -70.6575 | 17.9854 | 686.0214 | 160.8183 | 189.5868 | 229.0018 | 264.1797 | 304.7654 | 2.891%
5061 | 18-71 | -70.9288 | 17.9854 | 703.3767 | 160.2512 | 189.0593 | 228.3488 | 263.4127 | 303.8648 | 2.846%
5062 | 18-71 | -71.2001 | 17.9854 | 720.7607 | 160.0453 | 188.7895 | 228.0375 | 263.0671 | 303.4827 | 2.828%
5063 | 18-71.5 | -71.4715 | 17.9854 | 738.1714 | 159.8063 | 188.4823 | 227.6433 | 262.5929 | 302.914 | 2.809%
5064 | 18-71.5 | -71.7428 | 17.9854 | 755.6068 | 159.6893 | 188.3055 | 227.4119 | 262.3113 | 302.5733 | 2.799%
5065 | 18-72 | -72.0141 | 17.9854 | 773.0652 | 159.717 | 188.248 | 227.3272 | 262.2013 | 302.433 | 2.8%
5066 | 18-72.5 | -72.2854 | 17.9854 | 790.5452 | 159.6823 | 188.1463 | 227.1528 | 261.9559 | 302.0996 | 2.797%
5067 | 18-72.5 | -72.5568 | 17.9854 | 808.0453 | 159.5443 | 187.9887 | 226.8965 | 261.6035 | 301.6285 | 2.788%
5068 | 18-73 | -72.8281 | 17.9854 | 825.5641 | 159.3806 | 187.8241 | 226.6248 | 261.2275 | 301.1237 | 2.778%
5069 | 18-73 | -73.0994 | 17.9854 | 843.1004 | 159.4602 | 187.8318 | 226.571 | 261.1112 | 300.9279 | 2.784%
5070 | 18-73.5 | -73.3707 | 17.9854 | 860.6533 | 159.8595 | 188.0739 | 226.8329 | 261.3875 | 301.2174 | 2.814%
5071 | 18-73.5 | -73.642 | 17.9854 | 878.2216 | 160.5025 | 188.4926 | 227.3301 | 261.9542 | 301.8636 | 2.862%
5072 | 18-74 | -73.9134 | 17.9854 | 895.8044 | 161.1577 | 188.9095 | 227.8146 | 262.4965 | 302.4702 | 2.911%
5073 | 18-74 | -74.1847 | 17.9854 | 913.4008 | 161.4807 | 189.0981 | 228.0088 | 262.6912 | 302.6613 | 2.937%
5074 | 18-74.5 | -74.456 | 17.9854 | 931.01 | 161.4578 | 189.0524 | 227.8971 | 262.5131 | 302.3986 | 2.937%
5075 | 18-74.5 | -74.7273 | 17.9854 | 948.6313 | 161.1289 | 188.7962 | 227.4999 | 261.9773 | 301.6901 | 2.914%
5076 | 18-75 | -74.9986 | 17.9854 | 966.264 | 160.9022 | 188.6276 | 227.2462 | 261.6398 | 301.2483 | 2.898%
5077 | 18-75.5 | -75.27 | 17.9854 | 983.9074 | 160.7674 | 188.5274 | 227.0972 | 261.4426 | 300.9904 | 2.889%
5078 | 18-75.5 | -75.5413 | 17.9854 | 1001.561 | 160.7386 | 188.4927 | 227.0316 | 261.3451 | 300.8518 | 2.887%
5079 | 18-76 | -75.8126 | 17.9854 | 1019.2242 | 161.0558 | 188.6889 | 227.2869 | 261.6548 | 301.2256 | 2.911%
5080 | 18-76 | -76.0839 | 17.9854 | 1036.8964 | 161.668 | 189.0831 | 227.8093 | 262.2965 | 302.0099 | 2.956%
5081 | 18-76.5 | -76.3553 | 17.9854 | 1054.5772 | 162.4333 | 189.5822 | 228.4615 | 263.0908 | 302.9733 | 3.013%
5082 | 18-76.5 | -76.6266 | 17.9854 | 1072.2661 | 163.0772 | 190.0126 | 229.0183 | 263.7645 | 303.7855 | 3.063%
5083 | 18-77 | -76.8979 | 17.9854 | 1089.9626 | 163.5725 | 190.3539 | 229.449 | 264.2766 | 304.3931 | 3.102%
5084 | 18-77 | -77.1692 | 17.9854 | 1107.6665 | 163.9675 | 190.6399 | 229.7991 | 264.6837 | 304.8658 | 3.135%
5085 | 18-77.5 | -77.4405 | 17.9854 | 1125.3772 | 164.4732 | 191.0421 | 230.3083 | 265.2909 | 305.5886 | 3.177%
5086 | 18-77.5 | -77.7119 | 17.9854 | 1143.0946 | 165.0717 | 191.5254 | 230.9174 | 266.0154 | 306.4492 | 3.227%
5087 | 18-78 | -77.9832 | 17.9854 | 1160.8181 | 165.7272 | 192.0606 | 231.5837 | 266.8011 | 307.3752 | 3.284%
5088 | 18-78.5 | -78.2545 | 17.9854 | 1178.5475 | 166.43 | 192.6577 | 232.3336 | 267.6911 | 308.4303 | 3.346%
5089 | 18-78.5 | -78.5258 | 17.9854 | 1196.2826 | 167.1369 | 193.2769 | 233.1007 | 268.5927 | 309.4895 | 3.41%
5090 | 18-79 | -78.7971 | 17.9854 | 1214.0229 | 167.832 | 193.9063 | 233.871 | 269.4901 | 310.5347 | 3.475%
5091 | 18-79 | -79.0685 | 17.9854 | 1231.7684 | 168.5313 | 194.58 | 234.7084 | 270.4766 | 311.6964 | 3.542%
5092 | 18-79.5 | -79.3398 | 17.9854 | 1249.5186 | 169.1882 | 195.2505 | 235.5336 | 271.442 | 312.8255 | 3.607%
5093 | 18-79.5 | -79.6111 | 17.9854 | 1267.2734 | 169.8148 | 195.922 | 236.3541 | 272.3967 | 313.9364 | 3.671%
5094 | 18-80 | -79.8824 | 17.9854 | 1285.0326 | 170.4664 | 196.6421 | 237.248 | 273.4489 | 315.1744 | 3.737%
5095 | 18-80 | -80.1537 | 17.9854 | 1302.7959 | 171.0961 | 197.3427 | 238.1172 | 274.4716 | 316.3774 | 3.803%
5096 | 18-80.5 | -80.4251 | 17.9854 | 1320.5632 | 171.6951 | 198.0117 | 238.9449 | 275.4436 | 317.5186 | 3.867%
5097 | 18-80.5 | -80.6964 | 17.9854 | 1338.3342 | 172.2822 | 198.6732 | 239.7667 | 276.4116 | 318.6583 | 3.929%
5098 | 18-81 | -80.9677 | 17.9854 | 1356.1088 | 172.8275 | 199.2927 | 240.5376 | 277.3207 | 319.7299 | 3.988%
5099 | 18-81 | -81.239 | 17.9854 | 1373.8868 | 173.343 | 199.8915 | 241.2963 | 278.2271 | 320.8115 | 4.044%
5100 | 18-81.5 | -81.5104 | 17.9854 | 1391.668 | 173.8479 | 200.499 | 242.0904 | 279.1957 | 321.9899 | 4.097%
5101 | 18-82 | -81.7817 | 17.9854 | 1409.4523 | 174.283 | 201.0328 | 242.795 | 280.061 | 323.0488 | 4.143%
5102 | 18-82 | -82.053 | 17.9854 | 1427.2395 | 174.6601 | 201.5104 | 243.4437 | 280.8724 | 324.0578 | 4.182%
5103 | 18-82.5 | -82.3243 | 17.9854 | 1445.0295 | 174.9972 | 201.9637 | 244.0907 | 281.706 | 325.1205 | 4.215%
5104 | 18-82.5 | -82.5956 | 17.9854 | 1462.8221 | 175.2278 | 202.2991 | 244.5965 | 282.3778 | 325.9977 | 4.235%
5105 | 18-83 | -82.867 | 17.9854 | 1480.6173 | 175.368 | 202.5444 | 245.0106 | 282.9588 | 326.7878 | 4.243%
5106 | 18-83 | -83.1383 | 17.9854 | 1498.4148 | 175.4384 | 202.7301 | 245.3828 | 283.518 | 327.5834 | 4.242%
5107 | 18-83.5 | -83.4096 | 17.9854 | 1516.2147 | 175.3698 | 202.7623 | 245.564 | 283.8519 | 328.1133 | 4.225%
5108 | 18-83.5 | -83.6809 | 17.9854 | 1534.0167 | 175.2018 | 202.694 | 245.6274 | 284.0529 | 328.4934 | 4.196%
5109 | 18-84 | -83.9522 | 17.9854 | 1551.8207 | 174.9608 | 202.5603 | 245.6237 | 284.1873 | 328.8091 | 4.16%
5110 | 18-84 | -84.2236 | 17.9854 | 1569.6267 | 174.5794 | 202.292 | 245.4617 | 284.1427 | 328.9229 | 4.108%
5111 | 18-84.5 | -84.4949 | 17.9854 | 1587.4345 | 174.0726 | 201.9125 | 245.1719 | 283.9568 | 328.8809 | 4.044%
5112 | 18-85 | -84.7662 | 17.9854 | 1605.2441 | 173.4489 | 201.4317 | 244.7684 | 283.6475 | 328.7057 | 3.968%
5113 | 18-85 | -85.0375 | 17.9854 | 1623.0553 | 172.6328 | 200.7682 | 244.1269 | 283.0486 | 328.1791 | 3.876%
5114 | 18-85.5 | -85.3089 | 17.9854 | 1640.8681 | 171.6738 | 199.9962 | 243.362 | 282.3141 | 327.5042 | 3.773%
5115 | 18-85.5 | -85.5802 | 17.9854 | 1658.6824 | 170.5751 | 199.1253 | 242.4902 | 281.468 | 326.7145 | 3.659%
5116 | 18-86 | -85.8515 | 17.9854 | 1676.4981 | 168.9762 | 197.8296 | 241.0328 | 279.8819 | 324.9959 | 3.508%
5117 | 18-86 | -86.1228 | 17.9854 | 1694.3151 | 166.8551 | 196.204 | 239.1363 | 277.7537 | 322.6105 | 3.324%
5118 | 18-86.5 | -86.3941 | 17.9854 | 1712.1333 | 164.2458 | 194.2559 | 236.815 | 275.1045 | 319.5881 | 3.113%
5119 | 18-86.5 | -86.6655 | 17.9854 | 1729.9527 | 161.009 | 191.8177 | 233.836 | 271.6129 | 315.4964 | 2.872%
5120 | 18-87 | -86.9368 | 17.9854 | 1747.7732 | 157.2581 | 188.8137 | 230.3572 | 267.4995 | 310.6347 | 2.611%
5121 | 18-87 | -87.2081 | 17.9854 | 1765.5947 | 153.0784 | 185.2462 | 226.4499 | 262.8623 | 305.1353 | 2.343%
5122 | 18-87.5 | -87.4794 | 17.9854 | 1783.4172 | 148.7069 | 181.4004 | 222.3461 | 257.9793 | 299.3298 | 2.09%
5123 | 18-88 | -87.7507 | 17.9854 | 1801.2406 | 144.2222 | 177.3406 | 218.1317 | 252.958 | 293.3527 | 1.856%
5124 | 18-88 | -88.0221 | 17.9854 | 1819.0648 | 139.6561 | 173.1028 | 213.8225 | 247.8218 | 287.2361 | 1.643%
5125 | 18-88.5 | -88.2934 | 17.9854 | 1836.8898 | 135.0591 | 168.759 | 209.4467 | 242.5955 | 280.9998 | 1.453%
5126 | 18-88.5 | -88.5647 | 17.9854 | 1854.7155 | 130.5205 | 164.4109 | 205.1267 | 237.4362 | 274.8438 | 1.286%
5127 | 18-89 | -88.836 | 17.9854 | 1872.5419 | 126.0539 | 160.0732 | 200.8555 | 232.3304 | 268.7459 | 1.141%
5128 | 18-89 | -89.1074 | 17.9854 | 1890.3688 | 121.6665 | 155.7494 | 196.6099 | 227.2402 | 262.6496 | 1.014%
5129 | 18-89.5 | -89.3787 | 17.9854 | 1908.1963 | 117.7343 | 151.7871 | 192.8565 | 222.8131 | 257.4104 | 0.9122%
5130 | 18-89.5 | -89.65 | 17.9854 | 1926.0244 | 114.3347 | 148.1456 | 189.518 | 218.948 | 252.8694 | 0.8316%
5131 | 18-90 | -89.9213 | 17.9854 | 1943.8528 | 111.419 | 144.8206 | 186.5639 | 215.5845 | 248.9414 | 0.7673%
5132 | 18-90 | -90.1926 | 17.9854 | 1961.6817 | 109.1431 | 142.0019 | 184.2447 | 213.0677 | 246.0985 | 0.7202%
5133 | 18-90.5 | -90.464 | 17.9854 | 1979.5109 | 107.4785 | 139.8747 | 182.6033 | 211.3842 | 244.3043 | 0.6883%
5134 | 18-90.5 | -90.7353 | 17.9854 | 1997.3404 | 106.3554 | 138.4484 | 181.6203 | 210.4322 | 243.3974 | 0.6686%
5135 | 18-50 | -50.0371 | 18.2568 | 727.8085 | 150.7633 | 181.7024 | 216.7843 | 247.7578 | 283.1585 | 2.255%
5136 | 18-50.5 | -50.3084 | 18.2568 | 710.5516 | 151.4983 | 182.1795 | 217.479 | 248.6605 | 284.3146 | 2.299%
5137 | 18-50.5 | -50.5797 | 18.2568 | 693.3289 | 152.1636 | 182.6185 | 218.1301 | 249.5148 | 285.4172 | 2.338%
5138 | 18-51 | -50.851 | 18.2568 | 676.1428 | 152.7919 | 183.0389 | 218.7627 | 250.3516 | 286.5038 | 2.376%
5139 | 18-51 | -51.1224 | 18.2568 | 658.9963 | 153.4249 | 183.4673 | 219.4134 | 251.2164 | 287.6312 | 2.414%
5140 | 18-51.5 | -51.3937 | 18.2568 | 641.8926 | 154.0006 | 183.8586 | 220.0093 | 252.0098 | 288.667 | 2.45%
5141 | 18-51.5 | -51.665 | 18.2568 | 624.8353 | 154.5538 | 184.2371 | 220.5922 | 252.7901 | 289.6901 | 2.484%
5142 | 18-52 | -51.9363 | 18.2568 | 607.8283 | 155.1179 | 184.6274 | 221.2025 | 253.6136 | 290.7761 | 2.519%
5143 | 18-52 | -52.2077 | 18.2568 | 590.8759 | 155.6196 | 184.9778 | 221.7606 | 254.3736 | 291.7854 | 2.549%
5144 | 18-52.5 | -52.479 | 18.2568 | 573.9831 | 156.102 | 185.3181 | 222.3124 | 255.1315 | 292.7982 | 2.579%
5145 | 18-53 | -52.7503 | 18.2568 | 557.1552 | 156.5923 | 185.6683 | 222.8888 | 255.9288 | 293.8689 | 2.609%
5146 | 18-53 | -53.0216 | 18.2568 | 540.3985 | 157.0274 | 185.9846 | 223.4236 | 256.6775 | 294.8831 | 2.636%
5147 | 18-53.5 | -53.2929 | 18.2568 | 523.7197 | 157.4527 | 186.2966 | 223.9575 | 257.4288 | 295.9048 | 2.661%
5148 | 18-53.5 | -53.5643 | 18.2568 | 507.1266 | 157.8866 | 186.6167 | 224.5067 | 258.203 | 296.9587 | 2.688%
5149 | 18-54 | -53.8356 | 18.2568 | 490.6279 | 158.2614 | 186.895 | 224.9908 | 258.8896 | 297.8976 | 2.71%
5150 | 18-54 | -54.1069 | 18.2568 | 474.2335 | 158.6285 | 187.1675 | 225.464 | 259.5603 | 298.8146 | 2.733%
5151 | 18-54.5 | -54.3782 | 18.2568 | 457.9546 | 159.0059 | 187.4469 | 225.9435 | 260.2367 | 299.7364 | 2.756%
5152 | 18-54.5 | -54.6495 | 18.2568 | 441.8041 | 159.3501 | 187.7058 | 226.3911 | 260.8702 | 300.6019 | 2.777%
5153 | 18-55 | -54.9209 | 18.2568 | 425.7965 | 159.7307 | 187.9951 | 226.8857 | 261.5671 | 301.5514 | 2.8%
5154 | 18-55 | -55.1922 | 18.2568 | 409.9487 | 160.1579 | 188.3241 | 227.4393 | 262.3421 | 302.6025 | 2.827%
5155 | 18-55.5 | -55.4635 | 18.2568 | 394.2799 | 160.5601 | 188.6366 | 227.9601 | 263.068 | 303.5844 | 2.852%
5156 | 18-55.5 | -55.7348 | 18.2568 | 378.8124 | 161.0112 | 188.99 | 228.534 | 263.8586 | 304.645 | 2.881%
5157 | 18-56 | -56.0061 | 18.2568 | 363.5719 | 161.5045 | 189.3861 | 229.1619 | 264.7138 | 305.7829 | 2.914%
5158 | 18-56.5 | -56.2775 | 18.2568 | 348.5882 | 161.9721 | 189.7638 | 229.7459 | 265.4994 | 306.8186 | 2.945%
5159 | 18-56.5 | -56.5488 | 18.2568 | 333.8959 | 162.4746 | 190.1715 | 230.3567 | 266.3078 | 307.8712 | 2.98%
5160 | 18-57 | -56.8201 | 18.2568 | 319.5353 | 163.0007 | 190.6066 | 230.9892 | 267.1313 | 308.9301 | 3.018%
5161 | 18-57 | -57.0914 | 18.2568 | 305.5532 | 163.5043 | 191.0204 | 231.5698 | 267.8718 | 309.8664 | 3.055%
5162 | 18-57.5 | -57.3628 | 18.2568 | 292.0039 | 164.0495 | 191.4701 | 232.1883 | 268.6514 | 310.8423 | 3.096%
5163 | 18-57.5 | -57.6341 | 18.2568 | 278.9505 | 164.6226 | 191.9489 | 232.8348 | 269.457 | 311.8409 | 3.141%
5164 | 18-58 | -57.9054 | 18.2568 | 266.4661 | 165.1786 | 192.4121 | 233.4398 | 270.1949 | 312.7385 | 3.185%
5165 | 18-58 | -58.1767 | 18.2568 | 254.6342 | 165.7563 | 192.894 | 234.0485 | 270.9204 | 313.6026 | 3.232%
5166 | 18-58.5 | -58.448 | 18.2568 | 243.5501 | 166.326 | 193.3788 | 234.6369 | 271.6018 | 314.3917 | 3.281%
5167 | 18-58.5 | -58.7194 | 18.2568 | 233.3203 | 166.8462 | 193.8235 | 235.142 | 272.1565 | 314.9993 | 3.328%
5168 | 18-59 | -58.9907 | 18.2568 | 224.062 | 167.3813 | 194.2913 | 235.6624 | 272.7178 | 315.6018 | 3.378%
5169 | 18-59.5 | -59.262 | 18.2568 | 215.9001 | 167.9131 | 194.7669 | 236.1758 | 273.2567 | 316.1617 | 3.43%
5170 | 18-59.5 | -59.5333 | 18.2568 | 208.9632 | 168.422 | 195.2226 | 236.6451 | 273.727 | 316.6219 | 3.481%
5171 | 18-60 | -59.8046 | 18.2568 | 203.3767 | 168.9708 | 195.7278 | 237.1785 | 274.2753 | 317.1771 | 3.537%
5172 | 18-60 | -60.076 | 18.2568 | 199.2542 | 169.5277 | 196.2465 | 237.7241 | 274.8339 | 317.7398 | 3.595%
5173 | 18-60.5 | -60.3473 | 18.2568 | 196.6878 | 170.056 | 196.7277 | 238.2082 | 275.3076 | 318.1883 | 3.652%
5174 | 18-60.5 | -60.6186 | 18.2568 | 195.7388 | 170.5944 | 197.2265 | 238.7147 | 275.8082 | 318.6693 | 3.711%
5175 | 18-61 | -60.8899 | 18.2568 | 196.4305 | 171.121 | 197.7195 | 239.2092 | 276.2907 | 319.1245 | 3.77%
5176 | 18-61 | -61.1613 | 18.2568 | 198.7458 | 171.6202 | 198.1903 | 239.6691 | 276.7262 | 319.5176 | 3.829%
5177 | 18-61.5 | -61.4326 | 18.2568 | 202.6292 | 172.1257 | 198.6868 | 240.1698 | 277.2175 | 319.985 | 3.888%
5178 | 18-61.5 | -61.7039 | 18.2568 | 207.9927 | 172.6067 | 199.1729 | 240.6645 | 277.7077 | 320.4575 | 3.946%
5179 | 18-62 | -61.9752 | 18.2568 | 214.7255 | 173.0535 | 199.6306 | 241.1327 | 278.1738 | 320.9099 | 4.001%
5180 | 18-62 | -62.2465 | 18.2568 | 222.7034 | 173.503 | 200.1097 | 241.6496 | 278.7161 | 321.473 | 4.056%
5181 | 18-62.5 | -62.5179 | 18.2568 | 231.7978 | 173.982 | 200.6422 | 242.2605 | 279.3925 | 322.2204 | 4.113%
5182 | 18-63 | -62.7892 | 18.2568 | 241.8829 | 174.5295 | 201.2778 | 243.0347 | 280.291 | 323.2629 | 4.175%
5183 | 18-63 | -63.0605 | 18.2568 | 252.8401 | 175.1757 | 202.0569 | 244.0294 | 281.4856 | 324.6956 | 4.247%
5184 | 18-63.5 | -63.3318 | 18.2568 | 264.5611 | 175.7598 | 202.7689 | 244.9508 | 282.6022 | 326.0458 | 4.312%
5185 | 18-63.5 | -63.6031 | 18.2568 | 276.9488 | 176.1985 | 203.3075 | 245.653 | 283.4574 | 327.0842 | 4.361%
5186 | 18-64 | -63.8745 | 18.2568 | 289.9178 | 176.5384 | 203.7372 | 246.2321 | 284.1777 | 327.9756 | 4.397%
5187 | 18-64 | -64.1458 | 18.2568 | 303.3936 | 176.8061 | 204.0893 | 246.7265 | 284.8083 | 328.7725 | 4.424%
5188 | 18-64.5 | -64.4171 | 18.2568 | 317.3116 | 177.0298 | 204.3996 | 247.185 | 285.4102 | 329.5511 | 4.445%
5189 | 18-64.5 | -64.6884 | 18.2568 | 331.616 | 177.228 | 204.694 | 247.6458 | 286.0339 | 330.3771 | 4.461%
5190 | 18-65 | -64.9598 | 18.2568 | 346.2589 | 177.3634 | 204.9161 | 248.0196 | 286.5573 | 331.0876 | 4.47%
5191 | 18-65 | -65.2311 | 18.2568 | 361.1992 | 177.4454 | 205.0736 | 248.3104 | 286.981 | 331.6783 | 4.472%
5192 | 18-65.5 | -65.5024 | 18.2568 | 376.4014 | 177.5013 | 205.2009 | 248.565 | 287.363 | 332.2213 | 4.471%
5193 | 18-66 | -65.7737 | 18.2568 | 391.8351 | 177.4954 | 205.2509 | 248.7166 | 287.618 | 332.6085 | 4.463%
5194 | 18-66 | -66.045 | 18.2568 | 407.4738 | 177.3865 | 205.1722 | 248.6971 | 287.662 | 332.7361 | 4.445%
5195 | 18-66.5 | -66.3164 | 18.2568 | 423.2948 | 177.1482 | 204.9335 | 248.4671 | 287.4479 | 332.5488 | 4.412%
5196 | 18-66.5 | -66.5877 | 18.2568 | 439.2785 | 176.6703 | 204.3847 | 247.808 | 286.6909 | 331.6792 | 4.355%
5197 | 18-67 | -66.859 | 18.2568 | 455.4076 | 176.0744 | 203.6938 | 246.9552 | 285.691 | 330.507 | 4.287%
5198 | 18-67 | -67.1303 | 18.2568 | 471.6672 | 175.4198 | 203.0054 | 246.1138 | 284.7118 | 329.3677 | 4.214%
5199 | 18-67.5 | -67.4016 | 18.2568 | 488.0442 | 174.7802 | 202.3575 | 245.3258 | 283.7982 | 328.3086 | 4.143%
5200 | 18-67.5 | -67.673 | 18.2568 | 504.5272 | 174.1435 | 201.7223 | 244.557 | 282.91 | 327.2825 | 4.074%
5201 | 18-68 | -67.9443 | 18.2568 | 521.1061 | 173.4964 | 201.082 | 243.7874 | 282.0256 | 326.2661 | 4.004%
5202 | 18-68 | -68.2156 | 18.2568 | 537.7719 | 172.6812 | 200.2574 | 242.7578 | 280.808 | 324.8269 | 3.92%
5203 | 18-68.5 | -68.4869 | 18.2568 | 554.5169 | 171.681 | 199.2863 | 241.5338 | 279.3512 | 323.0941 | 3.821%
5204 | 18-69 | -68.7583 | 18.2568 | 571.334 | 170.4984 | 198.1965 | 240.1637 | 277.7234 | 321.1616 | 3.706%
5205 | 18-69 | -69.0296 | 18.2568 | 588.217 | 169.2056 | 197.0152 | 238.6642 | 275.9299 | 319.0187 | 3.586%
5206 | 18-69.5 | -69.3009 | 18.2568 | 605.1603 | 167.8481 | 195.7898 | 237.1025 | 274.0569 | 316.7751 | 3.463%
5207 | 18-69.5 | -69.5722 | 18.2568 | 622.1591 | 166.4435 | 194.5351 | 235.5008 | 272.1336 | 314.469 | 3.34%
5208 | 18-70 | -69.8435 | 18.2568 | 639.2087 | 164.913 | 193.1794 | 233.7491 | 270.0128 | 311.9066 | 3.211%
5209 | 18-70 | -70.1149 | 18.2568 | 656.3054 | 163.3736 | 191.8703 | 232.0635 | 267.9771 | 309.453 | 3.087%
5210 | 18-70.5 | -70.3862 | 18.2568 | 673.4454 | 161.8875 | 190.6581 | 230.5151 | 266.1176 | 307.2232 | 2.97%
5211 | 18-70.5 | -70.6575 | 18.2568 | 690.6254 | 160.8758 | 189.7923 | 229.4164 | 264.8034 | 305.6532 | 2.892%
5212 | 18-71 | -70.9288 | 18.2568 | 707.8426 | 160.2932 | 189.2386 | 228.7346 | 264.0056 | 304.7197 | 2.847%
5213 | 18-71 | -71.2001 | 18.2568 | 725.0942 | 160.0903 | 188.96 | 228.4216 | 263.6657 | 304.3528 | 2.828%
5214 | 18-71.5 | -71.4715 | 18.2568 | 742.3779 | 159.854 | 188.643 | 228.0254 | 263.1978 | 303.801 | 2.808%
5215 | 18-71.5 | -71.7428 | 18.2568 | 759.6914 | 159.7486 | 188.4695 | 227.8125 | 262.9502 | 303.5138 | 2.799%
5216 | 18-72 | -72.0141 | 18.2568 | 777.0326 | 159.7912 | 188.4248 | 227.761 | 262.8939 | 303.4535 | 2.8%
5217 | 18-72.5 | -72.2854 | 18.2568 | 794.3998 | 159.7389 | 188.318 | 227.5925 | 262.6658 | 303.1521 | 2.796%
5218 | 18-72.5 | -72.5568 | 18.2568 | 811.7912 | 159.5426 | 188.1255 | 227.2992 | 262.2751 | 302.642 | 2.783%
5219 | 18-73 | -72.8281 | 18.2568 | 829.2052 | 159.3054 | 187.9137 | 226.9714 | 261.8352 | 302.0643 | 2.767%
5220 | 18-73 | -73.0994 | 18.2568 | 846.6406 | 159.3928 | 187.93 | 226.9358 | 261.7469 | 301.9089 | 2.774%
5221 | 18-73.5 | -73.3707 | 18.2568 | 864.0958 | 159.8727 | 188.2467 | 227.304 | 262.1601 | 302.3732 | 2.809%
5222 | 18-73.5 | -73.642 | 18.2568 | 881.5697 | 160.6289 | 188.7735 | 227.9507 | 262.9161 | 303.2575 | 2.865%
5223 | 18-74 | -73.9134 | 18.2568 | 899.0613 | 161.3555 | 189.2359 | 228.493 | 263.5278 | 303.9474 | 2.919%
5224 | 18-74 | -74.1847 | 18.2568 | 916.5693 | 161.6354 | 189.388 | 228.6257 | 263.6364 | 304.0218 | 2.942%
5225 | 18-74.5 | -74.456 | 18.2568 | 934.093 | 161.4894 | 189.2464 | 228.3657 | 263.2588 | 303.4963 | 2.933%
5226 | 18-74.5 | -74.7273 | 18.2568 | 951.6313 | 161.0291 | 188.8848 | 227.8031 | 262.499 | 302.4911 | 2.902%
5227 | 18-75 | -74.9986 | 18.2568 | 969.1835 | 160.682 | 188.6193 | 227.394 | 261.9489 | 301.7654 | 2.879%
5228 | 18-75.5 | -75.27 | 18.2568 | 986.7488 | 160.4474 | 188.4362 | 227.1066 | 261.5585 | 301.2462 | 2.863%
5229 | 18-75.5 | -75.5413 | 18.2568 | 1004.3265 | 160.3608 | 188.3468 | 226.9389 | 261.312 | 300.8993 | 2.858%
5230 | 18-76 | -75.8126 | 18.2568 | 1021.9158 | 160.7 | 188.5437 | 227.1706 | 261.5729 | 301.192 | 2.883%
5231 | 18-76 | -76.0839 | 18.2568 | 1039.5162 | 161.4004 | 188.9851 | 227.7351 | 262.2504 | 302.003 | 2.935%
5232 | 18-76.5 | -76.3553 | 18.2568 | 1057.1271 | 162.2762 | 189.548 | 228.4547 | 263.1139 | 303.0364 | 3.001%
5233 | 18-76.5 | -76.6266 | 18.2568 | 1074.7479 | 162.9517 | 189.9905 | 229.0103 | 263.7722 | 303.8148 | 3.053%
5234 | 18-77 | -76.8979 | 18.2568 | 1092.3782 | 163.4205 | 190.2896 | 229.3663 | 264.1773 | 304.2745 | 3.091%
5235 | 18-77 | -77.1692 | 18.2568 | 1110.0174 | 163.7695 | 190.5102 | 229.6107 | 264.4388 | 304.5515 | 3.12%
5236 | 18-77.5 | -77.4405 | 18.2568 | 1127.665 | 164.2808 | 190.9189 | 230.1165 | 265.0322 | 305.247 | 3.163%
5237 | 18-77.5 | -77.7119 | 18.2568 | 1145.3207 | 164.9766 | 191.4758 | 230.8168 | 265.8638 | 306.2333 | 3.222%
5238 | 18-78 | -77.9832 | 18.2568 | 1162.9841 | 165.7839 | 192.1261 | 231.6316 | 266.8293 | 307.3763 | 3.291%
5239 | 18-78.5 | -78.2545 | 18.2568 | 1180.6547 | 166.6263 | 192.8321 | 232.5212 | 267.8873 | 308.6334 | 3.365%
5240 | 18-78.5 | -78.5258 | 18.2568 | 1198.3323 | 167.4619 | 193.5554 | 233.4218 | 268.9497 | 309.8859 | 3.441%
5241 | 18-79 | -78.7971 | 18.2568 | 1216.0165 | 168.2677 | 194.2807 | 234.3164 | 269.9977 | 311.1134 | 3.517%
5242 | 18-79 | -79.0685 | 18.2568 | 1233.7069 | 169.0468 | 195.0333 | 235.2581 | 271.1125 | 312.4321 | 3.592%
5243 | 18-79.5 | -79.3398 | 18.2568 | 1251.4033 | 169.7495 | 195.7627 | 236.1617 | 272.1747 | 313.6801 | 3.662%
5244 | 18-79.5 | -79.6111 | 18.2568 | 1269.1054 | 170.3985 | 196.4797 | 237.0424 | 273.2034 | 314.8816 | 3.729%
5245 | 18-80 | -79.8824 | 18.2568 | 1286.8129 | 171.0678 | 197.244 | 237.9947 | 274.3273 | 316.2075 | 3.799%
5246 | 18-80 | -80.1537 | 18.2568 | 1304.5255 | 171.7138 | 197.9859 | 238.9167 | 275.4135 | 317.4865 | 3.867%
5247 | 18-80.5 | -80.4251 | 18.2568 | 1322.2431 | 172.3296 | 198.6944 | 239.7928 | 276.442 | 318.6936 | 3.934%
5248 | 18-80.5 | -80.6964 | 18.2568 | 1339.9654 | 172.9358 | 199.3958 | 240.6622 | 277.4642 | 319.8952 | 4%
5249 | 18-81 | -80.9677 | 18.2568 | 1357.6921 | 173.5018 | 200.0526 | 241.4747 | 278.4185 | 321.0155 | 4.063%
5250 | 18-81 | -81.239 | 18.2568 | 1375.4231 | 174.0408 | 200.6875 | 242.2711 | 279.3632 | 322.1353 | 4.123%
5251 | 18-81.5 | -81.5104 | 18.2568 | 1393.1582 | 174.5744 | 201.3327 | 243.1026 | 280.3678 | 323.347 | 4.181%
5252 | 18-82 | -81.7817 | 18.2568 | 1410.8971 | 175.0443 | 201.9061 | 243.8456 | 281.2691 | 324.4379 | 4.232%
5253 | 18-82 | -82.053 | 18.2568 | 1428.6397 | 175.4607 | 202.424 | 244.5312 | 282.1125 | 325.4717 | 4.277%
5254 | 18-82.5 | -82.3243 | 18.2568 | 1446.3859 | 175.843 | 202.9171 | 245.2102 | 282.9691 | 326.5446 | 4.316%
5255 | 18-82.5 | -82.5956 | 18.2568 | 1464.1354 | 176.1219 | 203.2894 | 245.741 | 283.6525 | 327.4152 | 4.344%
5256 | 18-83 | -82.867 | 18.2568 | 1481.8882 | 176.3141 | 203.5715 | 246.1788 | 284.2425 | 328.1944 | 4.36%
5257 | 18-83 | -83.1383 | 18.2568 | 1499.644 | 176.4397 | 203.7957 | 246.5767 | 284.813 | 328.9818 | 4.365%
5258 | 18-83.5 | -83.4096 | 18.2568 | 1517.4027 | 176.4313 | 203.8664 | 246.7842 | 285.1596 | 329.5056 | 4.356%
5259 | 18-83.5 | -83.6809 | 18.2568 | 1535.1642 | 176.3284 | 203.8383 | 246.8782 | 285.3801 | 329.8898 | 4.335%
5260 | 18-84 | -83.9522 | 18.2568 | 1552.9284 | 176.157 | 203.7467 | 246.9102 | 285.5421 | 330.2216 | 4.305%
5261 | 18-84 | -84.2236 | 18.2568 | 1570.695 | 175.85 | 203.5183 | 246.7823 | 285.5244 | 330.3518 | 4.26%
5262 | 18-84.5 | -84.4949 | 18.2568 | 1588.4641 | 175.4236 | 203.1789 | 246.5291 | 285.3701 | 330.3336 | 4.202%
5263 | 18-85 | -84.7662 | 18.2568 | 1606.2355 | 174.8856 | 202.7396 | 246.1667 | 285.1002 | 330.1943 | 4.132%
5264 | 18-85 | -85.0375 | 18.2568 | 1624.009 | 174.1614 | 202.1203 | 245.5784 | 284.5623 | 329.7375 | 4.044%
5265 | 18-85.5 | -85.3089 | 18.2568 | 1641.7846 | 173.3 | 201.3947 | 244.8763 | 283.9062 | 329.1599 | 3.945%
5266 | 18-85.5 | -85.5802 | 18.2568 | 1659.5622 | 172.3027 | 200.5704 | 244.0737 | 283.151 | 328.4879 | 3.833%
5267 | 18-86 | -85.8515 | 18.2568 | 1677.3417 | 170.7786 | 199.2799 | 242.6307 | 281.5887 | 326.8051 | 3.68%
5268 | 18-86 | -86.1228 | 18.2568 | 1695.1229 | 168.6716 | 197.6207 | 240.6964 | 279.4191 | 324.3745 | 3.487%
5269 | 18-86.5 | -86.3941 | 18.2568 | 1712.9058 | 166.0285 | 195.607 | 238.2944 | 276.6754 | 321.2415 | 3.262%
5270 | 18-86.5 | -86.6655 | 18.2568 | 1730.6903 | 162.794 | 193.1472 | 235.281 | 273.151 | 317.1197 | 3.009%
5271 | 18-87 | -86.9368 | 18.2568 | 1748.4763 | 159.0756 | 190.1923 | 231.8123 | 269.0621 | 312.3015 | 2.738%
5272 | 18-87 | -87.2081 | 18.2568 | 1766.2638 | 154.9509 | 186.7289 | 227.9507 | 264.4957 | 306.9045 | 2.461%
5273 | 18-87.5 | -87.4794 | 18.2568 | 1784.0526 | 150.6277 | 182.9963 | 223.8924 | 259.6845 | 301.2046 | 2.199%
5274 | 18-88 | -87.7507 | 18.2568 | 1801.8426 | 146.1839 | 179.0606 | 219.7283 | 254.743 | 295.3445 | 1.955%
5275 | 18-88 | -88.0221 | 18.2568 | 1819.6339 | 141.6494 | 174.9443 | 215.4699 | 249.6881 | 289.3483 | 1.733%
5276 | 18-88.5 | -88.2934 | 18.2568 | 1837.4263 | 137.0649 | 170.7017 | 211.1276 | 244.5207 | 283.2036 | 1.533%
5277 | 18-88.5 | -88.5647 | 18.2568 | 1855.2197 | 132.5166 | 166.4299 | 206.8132 | 239.381 | 277.0855 | 1.358%
5278 | 18-89 | -88.836 | 18.2568 | 1873.0142 | 128.0278 | 162.1574 | 202.5305 | 234.2693 | 270.9896 | 1.204%
5279 | 18-89 | -89.1074 | 18.2568 | 1890.8096 | 123.6405 | 157.9381 | 198.299 | 229.2028 | 264.9292 | 1.07%
5280 | 18-89.5 | -89.3787 | 18.2568 | 1908.6058 | 119.7572 | 154.1509 | 194.6435 | 224.9039 | 259.8559 | 0.9643%
5281 | 18-89.5 | -89.65 | 18.2568 | 1926.4028 | 116.484 | 150.7443 | 191.4814 | 221.2665 | 255.6059 | 0.8827%
5282 | 18-90 | -89.9213 | 18.2568 | 1944.2006 | 113.7405 | 147.6947 | 188.7477 | 218.1821 | 252.0289 | 0.8187%
5283 | 18-90 | -90.1926 | 18.2568 | 1961.9991 | 111.5955 | 145.1075 | 186.6011 | 215.8713 | 249.4376 | 0.7715%
5284 | 18-90.5 | -90.464 | 18.2568 | 1979.7982 | 110.0123 | 143.1238 | 185.0626 | 214.3065 | 247.7805 | 0.7389%
5285 | 18-90.5 | -90.7353 | 18.2568 | 1997.5979 | 108.9117 | 141.744 | 184.1055 | 213.3759 | 246.8881 | 0.718%
5286 | 19-50 | -50.0371 | 18.5281 | 732.5711 | 150.0403 | 181.3505 | 216.3737 | 247.2965 | 282.64 | 2.213%
5287 | 19-50.5 | -50.3084 | 18.5281 | 715.4551 | 150.8565 | 181.8682 | 217.107 | 248.2347 | 283.8269 | 2.261%
5288 | 19-50.5 | -50.5797 | 18.5281 | 698.3792 | 151.5998 | 182.345 | 217.7913 | 249.1167 | 284.9494 | 2.305%
5289 | 19-51 | -50.851 | 18.5281 | 681.3465 | 152.3037 | 182.802 | 218.4557 | 249.9793 | 286.0536 | 2.347%
5290 | 19-51 | -51.1224 | 18.5281 | 664.3601 | 153.0116 | 183.2673 | 219.1405 | 250.8745 | 287.2058 | 2.39%
5291 | 19-51.5 | -51.3937 | 18.5281 | 647.4239 | 153.6617 | 183.6963 | 219.7731 | 251.7026 | 288.2729 | 2.429%
5292 | 19-51.5 | -51.665 | 18.5281 | 630.5419 | 154.292 | 184.1151 | 220.3972 | 252.5242 | 289.3363 | 2.468%
5293 | 19-52 | -51.9363 | 18.5281 | 613.7186 | 154.9378 | 184.5493 | 221.0549 | 253.3973 | 290.4739 | 2.509%
5294 | 19-52 | -52.2077 | 18.5281 | 596.959 | 155.5218 | 184.9447 | 221.6622 | 254.2095 | 291.5383 | 2.545%
5295 | 19-52.5 | -52.479 | 18.5281 | 580.2686 | 156.0868 | 185.3309 | 222.2653 | 255.023 | 292.6109 | 2.58%
5296 | 19-53 | -52.7503 | 18.5281 | 563.6538 | 156.6603 | 185.728 | 222.8954 | 255.8797 | 293.7473 | 2.616%
5297 | 19-53 | -53.0216 | 18.5281 | 547.1212 | 157.177 | 186.0913 | 223.4849 | 256.6896 | 294.8299 | 2.648%
5298 | 19-53.5 | -53.2929 | 18.5281 | 530.6788 | 157.6831 | 186.4499 | 224.0728 | 257.5012 | 295.9188 | 2.68%
5299 | 19-53.5 | -53.5643 | 18.5281 | 514.3351 | 158.1968 | 186.8161 | 224.675 | 258.3341 | 297.0377 | 2.712%
5300 | 19-54 | -53.8356 | 18.5281 | 498.1 | 158.6467 | 187.1375 | 225.2076 | 259.0734 | 298.0337 | 2.74%
5301 | 19-54 | -54.1069 | 18.5281 | 481.9843 | 159.0852 | 187.4513 | 225.7271 | 259.7945 | 299.0051 | 2.768%
5302 | 19-54.5 | -54.3782 | 18.5281 | 466.0007 | 159.5301 | 187.7697 | 226.2505 | 260.5188 | 299.9788 | 2.796%
5303 | 19-54.5 | -54.6495 | 18.5281 | 450.163 | 159.9346 | 188.0628 | 226.7353 | 261.1916 | 300.8854 | 2.822%
5304 | 19-55 | -54.9209 | 18.5281 | 434.4874 | 160.3678 | 188.3813 | 227.2604 | 261.9196 | 301.8659 | 2.849%
5305 | 19-55 | -55.1922 | 18.5281 | 418.992 | 160.8391 | 188.7345 | 227.8382 | 262.7179 | 302.9388 | 2.88%
5306 | 19-55.5 | -55.4635 | 18.5281 | 403.6977 | 161.2778 | 189.0676 | 228.3789 | 263.4623 | 303.9368 | 2.908%
5307 | 19-55.5 | -55.7348 | 18.5281 | 388.6282 | 161.761 | 189.4409 | 228.9728 | 264.2724 | 305.0156 | 2.94%
5308 | 19-56 | -56.0061 | 18.5281 | 373.8108 | 162.282 | 189.8569 | 229.6221 | 265.1499 | 306.1764 | 2.976%
5309 | 19-56.5 | -56.2775 | 18.5281 | 359.2765 | 162.7755 | 190.2566 | 230.233 | 265.9668 | 307.2485 | 3.01%
5310 | 19-56.5 | -56.5488 | 18.5281 | 345.0614 | 163.3028 | 190.6893 | 230.8778 | 266.8177 | 308.354 | 3.048%
5311 | 19-57 | -56.8201 | 18.5281 | 331.2065 | 163.8511 | 191.1515 | 231.55 | 267.6929 | 309.4793 | 3.088%
5312 | 19-57 | -57.0914 | 18.5281 | 317.7588 | 164.3707 | 191.5909 | 232.1699 | 268.4862 | 310.485 | 3.127%
5313 | 19-57.5 | -57.3628 | 18.5281 | 304.7725 | 164.9279 | 192.0665 | 232.8302 | 269.3231 | 311.5376 | 3.17%
5314 | 19-57.5 | -57.6341 | 18.5281 | 292.309 | 165.5065 | 192.57 | 233.5188 | 270.188 | 312.617 | 3.215%
5315 | 19-58 | -57.9054 | 18.5281 | 280.438 | 166.0584 | 193.0528 | 234.1614 | 270.9815 | 313.5928 | 3.26%
5316 | 19-58 | -58.1767 | 18.5281 | 269.238 | 166.6237 | 193.5513 | 234.8069 | 271.7643 | 314.5399 | 3.307%
5317 | 19-58.5 | -58.448 | 18.5281 | 258.796 | 167.1719 | 194.0497 | 235.431 | 272.5037 | 315.4154 | 3.355%
5318 | 19-58.5 | -58.7194 | 18.5281 | 249.2075 | 167.6629 | 194.5031 | 235.9678 | 273.1133 | 316.1077 | 3.4%
5319 | 19-59 | -58.9907 | 18.5281 | 240.5745 | 168.1624 | 194.9742 | 236.5143 | 273.7242 | 316.7899 | 3.447%
5320 | 19-59.5 | -59.262 | 18.5281 | 233.0033 | 168.651 | 195.4433 | 237.0428 | 274.3004 | 317.4158 | 3.495%
5321 | 19-59.5 | -59.5333 | 18.5281 | 226.6003 | 169.1028 | 195.8743 | 237.5039 | 274.7802 | 317.9091 | 3.541%
5322 | 19-60 | -59.8046 | 18.5281 | 221.4669 | 169.5773 | 196.3342 | 238.0018 | 275.3043 | 318.4556 | 3.59%
5323 | 19-60 | -60.076 | 18.5281 | 217.693 | 170.0536 | 196.799 | 238.4998 | 275.8235 | 318.9906 | 3.641%
5324 | 19-60.5 | -60.3473 | 18.5281 | 215.35 | 170.5115 | 197.2372 | 238.95 | 276.2737 | 319.4303 | 3.691%
5325 | 19-60.5 | -60.6186 | 18.5281 | 214.4848 | 170.9931 | 197.708 | 239.4426 | 276.7756 | 319.9328 | 3.744%
5326 | 19-61 | -60.8899 | 18.5281 | 215.1153 | 171.472 | 198.1805 | 239.9323 | 277.27 | 320.4219 | 3.798%
5327 | 19-61 | -61.1613 | 18.5281 | 217.2285 | 171.9274 | 198.6299 | 240.3839 | 277.7114 | 320.8395 | 3.851%
5328 | 19-61.5 | -61.4326 | 18.5281 | 220.7817 | 172.3967 | 199.1088 | 240.879 | 278.2101 | 321.3314 | 3.906%
5329 | 19-61.5 | -61.7039 | 18.5281 | 225.707 | 172.8486 | 199.5791 | 241.3675 | 278.7043 | 321.8217 | 3.961%
5330 | 19-62 | -61.9752 | 18.5281 | 231.9169 | 173.2733 | 200.0217 | 241.8266 | 279.1681 | 322.2806 | 4.012%
5331 | 19-62 | -62.2465 | 18.5281 | 239.3116 | 173.7077 | 200.4883 | 242.3349 | 279.7061 | 322.8456 | 4.065%
5332 | 19-62.5 | -62.5179 | 18.5281 | 247.7848 | 174.1755 | 201.0105 | 242.9375 | 280.3765 | 323.5902 | 4.12%
5333 | 19-63 | -62.7892 | 18.5281 | 257.23 | 174.718 | 201.642 | 243.7091 | 281.2743 | 324.6346 | 4.182%
5334 | 19-63 | -63.0605 | 18.5281 | 267.5443 | 175.3724 | 202.4319 | 244.7197 | 282.4894 | 326.0935 | 4.254%
5335 | 19-63.5 | -63.3318 | 18.5281 | 278.6312 | 175.978 | 203.1708 | 245.6765 | 283.6494 | 327.4967 | 4.321%
5336 | 19-63.5 | -63.6031 | 18.5281 | 290.4022 | 176.4425 | 203.7409 | 246.4196 | 284.5543 | 328.5953 | 4.372%
5337 | 19-64 | -63.8745 | 18.5281 | 302.7774 | 176.7975 | 204.1886 | 247.0214 | 285.3016 | 329.5187 | 4.41%
5338 | 19-64 | -64.1458 | 18.5281 | 315.6859 | 177.0705 | 204.5456 | 247.52 | 285.9355 | 330.3176 | 4.438%
5339 | 19-64.5 | -64.4171 | 18.5281 | 329.0648 | 177.2959 | 204.8563 | 247.9762 | 286.5325 | 331.088 | 4.459%
5340 | 19-64.5 | -64.6884 | 18.5281 | 342.859 | 177.4993 | 205.1563 | 248.4433 | 287.163 | 331.9214 | 4.476%
5341 | 19-65 | -64.9598 | 18.5281 | 357.0204 | 177.6407 | 205.3859 | 248.8271 | 287.6991 | 332.6478 | 4.485%
5342 | 19-65 | -65.2311 | 18.5281 | 371.507 | 177.7292 | 205.5531 | 249.1333 | 288.1436 | 333.2663 | 4.488%
5343 | 19-65.5 | -65.5024 | 18.5281 | 386.2821 | 177.7932 | 205.694 | 249.4112 | 288.5588 | 333.855 | 4.487%
5344 | 19-66 | -65.7737 | 18.5281 | 401.3139 | 177.7961 | 205.7588 | 249.5883 | 288.85 | 334.2918 | 4.48%
5345 | 19-66 | -66.045 | 18.5281 | 416.5745 | 177.6973 | 205.6961 | 249.5953 | 288.9308 | 334.4695 | 4.462%
5346 | 19-66.5 | -66.3164 | 18.5281 | 432.0397 | 177.471 | 205.4752 | 249.3932 | 288.7549 | 334.333 | 4.431%
5347 | 19-66.5 | -66.5877 | 18.5281 | 447.6883 | 177.006 | 204.945 | 248.7629 | 288.0366 | 333.5148 | 4.375%
5348 | 19-67 | -66.859 | 18.5281 | 463.5016 | 176.4241 | 204.2733 | 247.9383 | 287.0739 | 332.3912 | 4.308%
5349 | 19-67 | -67.1303 | 18.5281 | 479.4633 | 175.7841 | 203.6039 | 247.1236 | 286.1289 | 331.2953 | 4.236%
5350 | 19-67.5 | -67.4016 | 18.5281 | 495.559 | 175.1571 | 202.9714 | 246.3557 | 285.2399 | 330.2665 | 4.167%
5351 | 19-67.5 | -67.673 | 18.5281 | 511.7762 | 174.5297 | 202.3468 | 245.5999 | 284.367 | 329.2586 | 4.099%
5352 | 19-68 | -67.9443 | 18.5281 | 528.1035 | 173.8884 | 201.7125 | 244.8368 | 283.4895 | 328.2496 | 4.03%
5353 | 19-68 | -68.2156 | 18.5281 | 544.531 | 173.0741 | 200.8871 | 243.8026 | 282.2639 | 326.7978 | 3.947%
5354 | 19-68.5 | -68.4869 | 18.5281 | 561.0499 | 172.073 | 199.9111 | 242.5667 | 280.788 | 325.0369 | 3.847%
5355 | 19-69 | -68.7583 | 18.5281 | 577.6523 | 170.8888 | 198.8141 | 241.1793 | 279.1327 | 323.064 | 3.733%
5356 | 19-69 | -69.0296 | 18.5281 | 594.3312 | 169.5935 | 197.6228 | 239.6563 | 277.302 | 320.8665 | 3.613%
5357 | 19-69.5 | -69.3009 | 18.5281 | 611.0803 | 168.2327 | 196.3867 | 238.0706 | 275.3914 | 318.5681 | 3.49%
5358 | 19-69.5 | -69.5722 | 18.5281 | 627.8939 | 166.8244 | 195.1216 | 236.4465 | 273.4337 | 316.2119 | 3.367%
5359 | 19-70 | -69.8435 | 18.5281 | 644.767 | 165.2904 | 193.7541 | 234.6723 | 271.2794 | 313.6024 | 3.238%
5360 | 19-70 | -70.1149 | 18.5281 | 661.695 | 163.7488 | 192.4322 | 232.9647 | 269.2125 | 311.1057 | 3.113%
5361 | 19-70.5 | -70.3862 | 18.5281 | 678.6737 | 162.261 | 191.2069 | 231.3961 | 267.3257 | 308.8397 | 2.996%
5362 | 19-70.5 | -70.6575 | 18.5281 | 695.6994 | 161.2475 | 190.3268 | 230.2789 | 265.9892 | 307.2423 | 2.918%
5363 | 19-71 | -70.9288 | 18.5281 | 712.7688 | 160.6647 | 189.7614 | 229.5859 | 265.1805 | 306.2985 | 2.872%
5364 | 19-71 | -71.2001 | 18.5281 | 729.8786 | 160.4633 | 189.4742 | 229.2689 | 264.8414 | 305.9385 | 2.853%
5365 | 19-71.5 | -71.4715 | 18.5281 | 747.0261 | 160.2294 | 189.1494 | 228.8719 | 264.3798 | 305.4022 | 2.832%
5366 | 19-71.5 | -71.7428 | 18.5281 | 764.2088 | 160.1276 | 188.9715 | 228.6662 | 264.1511 | 305.1492 | 2.823%
5367 | 19-72 | -72.0141 | 18.5281 | 781.4242 | 160.1703 | 188.9197 | 228.6206 | 264.1144 | 305.1259 | 2.823%
5368 | 19-72.5 | -72.2854 | 18.5281 | 798.6702 | 160.0645 | 188.7676 | 228.4037 | 263.8358 | 304.7724 | 2.815%
5369 | 19-72.5 | -72.5568 | 18.5281 | 815.9449 | 159.7636 | 188.4929 | 228.0102 | 263.3286 | 304.1265 | 2.794%
5370 | 19-73 | -72.8281 | 18.5281 | 833.2464 | 159.4035 | 188.185 | 227.5618 | 262.7455 | 303.3788 | 2.77%
5371 | 19-73 | -73.0994 | 18.5281 | 850.5731 | 159.4746 | 188.18 | 227.506 | 262.6387 | 303.2077 | 2.775%
5372 | 19-73.5 | -73.3707 | 18.5281 | 867.9234 | 160.0104 | 188.5537 | 227.9606 | 263.1673 | 303.8234 | 2.814%
5373 | 19-73.5 | -73.642 | 18.5281 | 885.2959 | 160.848 | 189.1736 | 228.7415 | 264.0974 | 304.9318 | 2.875%
5374 | 19-74 | -73.9134 | 18.5281 | 902.6893 | 161.5873 | 189.6389 | 229.2876 | 264.7141 | 305.628 | 2.93%
5375 | 19-74 | -74.1847 | 18.5281 | 920.1024 | 161.7632 | 189.7084 | 229.3006 | 264.6673 | 305.503 | 2.945%
5376 | 19-74.5 | -74.456 | 18.5281 | 937.534 | 161.4399 | 189.4291 | 228.8407 | 264.0296 | 304.6437 | 2.924%
5377 | 19-74.5 | -74.7273 | 18.5281 | 954.9831 | 160.813 | 188.9368 | 228.0834 | 263.0132 | 303.3056 | 2.882%
5378 | 19-75 | -74.9986 | 18.5281 | 972.4487 | 160.3114 | 188.5496 | 227.4892 | 262.2163 | 302.2569 | 2.848%
5379 | 19-75.5 | -75.27 | 18.5281 | 989.9299 | 159.9473 | 188.2621 | 227.0373 | 261.6027 | 301.4414 | 2.824%
5380 | 19-75.5 | -75.5413 | 18.5281 | 1007.4259 | 159.7843 | 188.1069 | 226.7557 | 261.1946 | 300.8733 | 2.814%
5381 | 19-76 | -75.8126 | 18.5281 | 1024.9358 | 160.1532 | 188.312 | 226.9774 | 261.4268 | 301.1131 | 2.842%
5382 | 19-76 | -76.0839 | 18.5281 | 1042.459 | 160.9631 | 188.8206 | 227.6144 | 262.1804 | 302.0032 | 2.901%
5383 | 19-76.5 | -76.3553 | 18.5281 | 1059.9948 | 161.968 | 189.4657 | 228.4278 | 263.1473 | 303.1507 | 2.976%
5384 | 19-76.5 | -76.6266 | 18.5281 | 1077.5424 | 162.6664 | 189.9169 | 228.9778 | 263.7852 | 303.8891 | 3.031%
5385 | 19-77 | -76.8979 | 18.5281 | 1095.1013 | 163.0856 | 190.1492 | 229.2238 | 264.0373 | 304.1421 | 3.065%
5386 | 19-77 | -77.1692 | 18.5281 | 1112.671 | 163.3588 | 190.2699 | 229.3119 | 264.0869 | 304.1375 | 3.088%
5387 | 19-77.5 | -77.4405 | 18.5281 | 1130.2508 | 163.8623 | 190.6719 | 229.7932 | 264.6375 | 304.7668 | 3.13%
5388 | 19-77.5 | -77.7119 | 18.5281 | 1147.8403 | 164.6659 | 191.3095 | 230.5908 | 265.5812 | 305.8823 | 3.198%
5389 | 19-78 | -77.9832 | 18.5281 | 1165.4391 | 165.6529 | 192.0951 | 231.5779 | 266.753 | 307.2719 | 3.282%
5390 | 19-78.5 | -78.2545 | 18.5281 | 1183.0466 | 166.6629 | 192.9293 | 232.6297 | 268.0049 | 308.7603 | 3.371%
5391 | 19-78.5 | -78.5258 | 18.5281 | 1200.6624 | 167.6561 | 193.7745 | 233.6849 | 269.2519 | 310.233 | 3.461%
5392 | 19-79 | -78.7971 | 18.5281 | 1218.2862 | 168.5978 | 194.6084 | 234.7175 | 270.4652 | 311.6581 | 3.549%
5393 | 19-79 | -79.0685 | 18.5281 | 1235.9176 | 169.4683 | 195.4422 | 235.7625 | 271.7036 | 313.1246 | 3.633%
5394 | 19-79.5 | -79.3398 | 18.5281 | 1253.5562 | 170.2132 | 196.2224 | 236.7288 | 272.8392 | 314.4587 | 3.709%
5395 | 19-79.5 | -79.6111 | 18.5281 | 1271.2017 | 170.8788 | 196.9725 | 237.6488 | 273.9126 | 315.7109 | 3.778%
5396 | 19-80 | -79.8824 | 18.5281 | 1288.8538 | 171.5663 | 197.7737 | 238.6469 | 275.0906 | 317.1005 | 3.851%
5397 | 19-80 | -80.1537 | 18.5281 | 1306.5121 | 172.233 | 198.5541 | 239.6168 | 276.2333 | 318.4462 | 3.923%
5398 | 19-80.5 | -80.4251 | 18.5281 | 1324.1764 | 172.8719 | 199.3023 | 240.5421 | 277.3195 | 319.7209 | 3.993%
5399 | 19-80.5 | -80.6964 | 18.5281 | 1341.8464 | 173.504 | 200.0453 | 241.463 | 278.4024 | 320.994 | 4.063%
5400 | 19-81 | -80.9677 | 18.5281 | 1359.5219 | 174.0966 | 200.7404 | 242.3209 | 279.4081 | 322.1727 | 4.13%
5401 | 19-81 | -81.239 | 18.5281 | 1377.2026 | 174.6632 | 201.4104 | 243.1566 | 280.3952 | 323.3382 | 4.194%
5402 | 19-81.5 | -81.5104 | 18.5281 | 1394.8883 | 175.2275 | 202.0904 | 244.0246 | 281.4375 | 324.5878 | 4.257%
5403 | 19-82 | -81.7817 | 18.5281 | 1412.5787 | 175.7314 | 202.6991 | 244.8037 | 282.3746 | 325.7133 | 4.313%
5404 | 19-82 | -82.053 | 18.5281 | 1430.2737 | 176.1829 | 203.252 | 245.5229 | 283.2493 | 326.7745 | 4.364%
5405 | 19-82.5 | -82.3243 | 18.5281 | 1447.973 | 176.601 | 203.7788 | 246.2307 | 284.1282 | 327.8607 | 4.409%
5406 | 19-82.5 | -82.5956 | 18.5281 | 1465.6764 | 176.9154 | 204.1823 | 246.7832 | 284.8229 | 328.7283 | 4.442%
5407 | 19-83 | -82.867 | 18.5281 | 1483.3838 | 177.144 | 204.4957 | 247.2416 | 285.4215 | 329.4997 | 4.464%
5408 | 19-83 | -83.1383 | 18.5281 | 1501.095 | 177.3082 | 204.7532 | 247.662 | 286.0024 | 330.281 | 4.475%
5409 | 19-83.5 | -83.4096 | 18.5281 | 1518.8098 | 177.3428 | 204.8582 | 247.8931 | 286.3604 | 330.7997 | 4.472%
5410 | 19-83.5 | -83.6809 | 18.5281 | 1536.5281 | 177.2901 | 204.8672 | 248.0158 | 286.5999 | 331.1895 | 4.457%
5411 | 19-84 | -83.9522 | 18.5281 | 1554.2497 | 177.175 | 204.8161 | 248.0829 | 286.7903 | 331.5399 | 4.433%
5412 | 19-84 | -84.2236 | 18.5281 | 1571.9744 | 176.9277 | 204.6234 | 247.984 | 286.7934 | 331.6793 | 4.394%
5413 | 19-84.5 | -84.4949 | 18.5281 | 1589.7022 | 176.5668 | 204.3196 | 247.7608 | 286.6623 | 331.6743 | 4.342%
5414 | 19-85 | -84.7662 | 18.5281 | 1607.4328 | 176.1001 | 203.9178 | 247.4332 | 286.4229 | 331.5592 | 4.277%
5415 | 19-85 | -85.0375 | 18.5281 | 1625.1662 | 175.4538 | 203.3385 | 246.8911 | 285.9363 | 331.1591 | 4.195%
5416 | 19-85.5 | -85.3089 | 18.5281 | 1642.9022 | 174.6756 | 202.6545 | 246.2439 | 285.3474 | 330.6635 | 4.098%
5417 | 19-85.5 | -85.5802 | 18.5281 | 1660.6407 | 173.7652 | 201.8714 | 245.5014 | 284.6708 | 330.0927 | 3.99%
5418 | 19-86 | -85.8515 | 18.5281 | 1678.3816 | 172.3076 | 200.585 | 244.0702 | 283.1281 | 328.4391 | 3.835%
5419 | 19-86 | -86.1228 | 18.5281 | 1696.1247 | 170.2158 | 198.8942 | 242.1003 | 280.9196 | 325.9661 | 3.634%
5420 | 19-86.5 | -86.3941 | 18.5281 | 1713.8701 | 167.5477 | 196.8201 | 239.625 | 278.0909 | 322.7346 | 3.396%
5421 | 19-86.5 | -86.6655 | 18.5281 | 1731.6175 | 164.3385 | 194.3474 | 236.5955 | 274.5565 | 318.6114 | 3.134%
5422 | 19-87 | -86.9368 | 18.5281 | 1749.3668 | 160.6878 | 191.4656 | 233.1645 | 270.527 | 313.88 | 2.857%
5423 | 19-87 | -87.2081 | 18.5281 | 1767.1181 | 156.6593 | 188.1395 | 229.3822 | 266.0726 | 308.6361 | 2.576%
5424 | 19-87.5 | -87.4794 | 18.5281 | 1784.8711 | 152.4148 | 184.5379 | 225.3889 | 261.3562 | 303.0684 | 2.306%
5425 | 19-88 | -87.7507 | 18.5281 | 1802.6258 | 148.0349 | 180.7332 | 221.2863 | 256.5065 | 297.3385 | 2.055%
5426 | 19-88 | -88.0221 | 18.5281 | 1820.3821 | 143.5504 | 176.746 | 217.0854 | 251.5395 | 291.4688 | 1.825%
5427 | 19-88.5 | -88.2934 | 18.5281 | 1838.1399 | 139.0044 | 172.6229 | 212.7935 | 246.4499 | 285.4367 | 1.617%
5428 | 19-88.5 | -88.5647 | 18.5281 | 1855.8992 | 134.48 | 168.4576 | 208.5128 | 241.3623 | 279.3944 | 1.433%
5429 | 19-89 | -88.836 | 18.5281 | 1873.6598 | 130.0109 | 164.2924 | 204.2584 | 236.2918 | 273.3557 | 1.271%
5430 | 19-89 | -89.1074 | 18.5281 | 1891.4217 | 125.6741 | 160.2307 | 200.093 | 231.31 | 267.4031 | 1.132%
5431 | 19-89.5 | -89.3787 | 18.5281 | 1909.1848 | 121.8945 | 156.671 | 196.5929 | 227.205 | 262.5705 | 1.024%
5432 | 19-89.5 | -89.65 | 18.5281 | 1926.949 | 118.8007 | 153.5546 | 193.6748 | 223.8608 | 258.685 | 0.9422%
5433 | 19-90 | -89.9213 | 18.5281 | 1944.7143 | 116.2753 | 150.8283 | 191.2309 | 221.1091 | 255.5159 | 0.8796%
5434 | 19-90 | -90.1926 | 18.5281 | 1962.4806 | 114.2935 | 148.5146 | 189.3141 | 219.0428 | 253.2141 | 0.8331%
5435 | 19-90.5 | -90.464 | 18.5281 | 1980.2479 | 112.8126 | 146.7003 | 187.9226 | 217.6225 | 251.7172 | 0.8002%
5436 | 19-90.5 | -90.7353 | 18.5281 | 1998.016 | 111.748 | 145.3837 | 187.0091 | 216.7291 | 250.8524 | 0.7781%
5437 | 19-50 | -50.0371 | 18.7994 | 737.7743 | 148.9292 | 180.7425 | 215.5954 | 246.3607 | 281.5174 | 2.15%
5438 | 19-50.5 | -50.3084 | 18.7994 | 720.808 | 149.8331 | 181.3059 | 216.3772 | 247.349 | 282.7553 | 2.201%
5439 | 19-50.5 | -50.5797 | 18.7994 | 703.888 | 150.6633 | 181.828 | 217.1084 | 248.2785 | 283.9249 | 2.25%
5440 | 19-51 | -50.851 | 18.7994 | 687.0178 | 151.454 | 182.3304 | 217.8208 | 249.1907 | 285.0796 | 2.296%
5441 | 19-51 | -51.1224 | 18.7994 | 670.201 | 152.2489 | 182.8425 | 218.5578 | 250.1423 | 286.2926 | 2.344%
5442 | 19-51.5 | -51.3937 | 18.7994 | 653.442 | 152.9854 | 183.319 | 219.2456 | 251.032 | 287.4285 | 2.388%
5443 | 19-51.5 | -51.665 | 18.7994 | 636.7452 | 153.7038 | 183.7873 | 219.9286 | 251.9208 | 288.5684 | 2.432%
5444 | 19-52 | -51.9363 | 18.7994 | 620.1158 | 154.4415 | 184.2739 | 220.6493 | 252.8664 | 289.7895 | 2.478%
5445 | 19-52 | -52.2077 | 18.7994 | 603.5593 | 155.1178 | 184.7221 | 221.3199 | 253.7513 | 290.9371 | 2.52%
5446 | 19-52.5 | -52.479 | 18.7994 | 587.082 | 155.7749 | 185.1612 | 221.9866 | 254.6378 | 292.0935 | 2.562%
5447 | 19-53 | -52.7503 | 18.7994 | 570.6907 | 156.4403 | 185.6113 | 222.681 | 255.5685 | 293.3153 | 2.604%
5448 | 19-53 | -53.0216 | 18.7994 | 554.3931 | 157.0476 | 186.0272 | 223.3342 | 256.4522 | 294.4831 | 2.642%
5449 | 19-53.5 | -53.2929 | 18.7994 | 538.1978 | 157.6437 | 186.4375 | 223.983 | 257.3327 | 295.6498 | 2.68%
5450 | 19-53.5 | -53.5643 | 18.7994 | 522.1143 | 158.2468 | 186.8542 | 224.6424 | 258.2283 | 296.8374 | 2.718%
5451 | 19-54 | -53.8356 | 18.7994 | 506.1533 | 158.78 | 187.2218 | 225.2256 | 259.0214 | 297.89 | 2.753%
5452 | 19-54 | -54.1069 | 18.7994 | 490.3268 | 159.2953 | 187.5771 | 225.789 | 259.7876 | 298.9071 | 2.786%
5453 | 19-54.5 | -54.3782 | 18.7994 | 474.6483 | 159.8094 | 187.9315 | 226.3485 | 260.547 | 299.9138 | 2.82%
5454 | 19-54.5 | -54.6495 | 18.7994 | 459.133 | 160.2725 | 188.2536 | 226.8593 | 261.242 | 300.837 | 2.85%
5455 | 19-55 | -54.9209 | 18.7994 | 443.7979 | 160.7552 | 188.5944 | 227.4013 | 261.9806 | 301.8194 | 2.882%
5456 | 19-55 | -55.1922 | 18.7994 | 428.6626 | 161.2671 | 188.9636 | 227.9874 | 262.7787 | 302.8807 | 2.916%
5457 | 19-55.5 | -55.4635 | 18.7994 | 413.7489 | 161.739 | 189.3088 | 228.5311 | 263.5165 | 303.8592 | 2.947%
5458 | 19-55.5 | -55.7348 | 18.7994 | 399.0817 | 162.2496 | 189.6924 | 229.1264 | 264.3184 | 304.9174 | 2.982%
5459 | 19-56 | -56.0061 | 18.7994 | 384.6894 | 162.7926 | 190.1177 | 229.7771 | 265.1888 | 306.0597 | 3.02%
5460 | 19-56.5 | -56.2775 | 18.7994 | 370.6038 | 163.3076 | 190.5307 | 230.3985 | 266.0128 | 307.1342 | 3.057%
5461 | 19-56.5 | -56.5488 | 18.7994 | 356.8613 | 163.8559 | 190.9812 | 231.0637 | 266.8863 | 308.2646 | 3.096%
5462 | 19-57 | -56.8201 | 18.7994 | 343.5033 | 164.4229 | 191.4644 | 231.7647 | 267.7977 | 309.4349 | 3.139%
5463 | 19-57 | -57.0914 | 18.7994 | 330.5762 | 164.9546 | 191.9238 | 232.4153 | 268.632 | 310.4945 | 3.179%
5464 | 19-57.5 | -57.3628 | 18.7994 | 318.1328 | 165.5202 | 192.4206 | 233.1101 | 269.5166 | 311.6109 | 3.224%
5465 | 19-57.5 | -57.6341 | 18.7994 | 306.2318 | 166.1025 | 192.9457 | 233.8358 | 270.4339 | 312.7619 | 3.27%
5466 | 19-58 | -57.9054 | 18.7994 | 294.9392 | 166.6514 | 193.4478 | 234.5154 | 271.282 | 313.8144 | 3.315%
5467 | 19-58 | -58.1767 | 18.7994 | 284.3273 | 167.2079 | 193.9648 | 235.1997 | 272.1238 | 314.8463 | 3.362%
5468 | 19-58.5 | -58.448 | 18.7994 | 274.4752 | 167.7437 | 194.4803 | 235.8638 | 272.9261 | 315.8138 | 3.409%
5469 | 19-58.5 | -58.7194 | 18.7994 | 265.4675 | 168.2187 | 194.9485 | 236.44 | 273.6002 | 316.6023 | 3.453%
5470 | 19-59 | -58.9907 | 18.7994 | 257.3929 | 168.6973 | 195.4299 | 237.0225 | 274.2733 | 317.38 | 3.498%
5471 | 19-59.5 | -59.262 | 18.7994 | 250.3417 | 169.1619 | 195.9059 | 237.5848 | 274.9109 | 318.1027 | 3.544%
5472 | 19-59.5 | -59.5333 | 18.7994 | 244.4025 | 169.588 | 196.3411 | 238.0787 | 275.4527 | 318.6954 | 3.587%
5473 | 19-60 | -59.8046 | 18.7994 | 239.6579 | 170.03 | 196.7981 | 238.5994 | 276.0261 | 319.3255 | 3.633%
5474 | 19-60 | -60.076 | 18.7994 | 236.1802 | 170.468 | 197.2531 | 239.1107 | 276.5825 | 319.9287 | 3.679%
5475 | 19-60.5 | -60.3473 | 18.7994 | 234.0256 | 170.8846 | 197.6766 | 239.5669 | 277.0604 | 320.4243 | 3.724%
5476 | 19-60.5 | -60.6186 | 18.7994 | 233.2309 | 171.3262 | 198.1325 | 240.0652 | 277.5896 | 320.9821 | 3.773%
5477 | 19-61 | -60.8899 | 18.7994 | 233.81 | 171.7674 | 198.5887 | 240.558 | 278.1075 | 321.5212 | 3.822%
5478 | 19-61 | -61.1613 | 18.7994 | 235.7527 | 172.1878 | 199.0195 | 241.0075 | 278.5642 | 321.9771 | 3.871%
5479 | 19-61.5 | -61.4326 | 18.7994 | 239.0258 | 172.6271 | 199.4806 | 241.4989 | 279.0742 | 322.4998 | 3.922%
5480 | 19-61.5 | -61.7039 | 18.7994 | 243.5757 | 173.0549 | 199.9332 | 241.9805 | 279.5729 | 323.0099 | 3.972%
5481 | 19-62 | -61.9752 | 18.7994 | 249.3324 | 173.4583 | 200.3578 | 242.4283 | 280.0329 | 323.4751 | 4.021%
5482 | 19-62 | -62.2465 | 18.7994 | 256.2147 | 173.8745 | 200.8078 | 242.9238 | 280.5625 | 324.0377 | 4.071%
5483 | 19-62.5 | -62.5179 | 18.7994 | 264.1344 | 174.3268 | 201.315 | 243.5129 | 281.2215 | 324.774 | 4.124%
5484 | 19-63 | -62.7892 | 18.7994 | 273.0014 | 174.8555 | 201.9322 | 244.2701 | 282.105 | 325.8047 | 4.183%
5485 | 19-63 | -63.0605 | 18.7994 | 282.7266 | 175.4971 | 202.7077 | 245.2635 | 283.3008 | 327.2417 | 4.254%
5486 | 19-63.5 | -63.3318 | 18.7994 | 293.2244 | 176.0919 | 203.4332 | 246.2029 | 284.4396 | 328.6193 | 4.319%
5487 | 19-63.5 | -63.6031 | 18.7994 | 304.415 | 176.5478 | 203.9919 | 246.9299 | 285.3238 | 329.6919 | 4.37%
5488 | 19-64 | -63.8745 | 18.7994 | 316.2249 | 176.8961 | 204.4298 | 247.5167 | 286.0511 | 330.589 | 4.407%
5489 | 19-64 | -64.1458 | 18.7994 | 328.5872 | 177.1653 | 204.7801 | 248.0032 | 286.6678 | 331.3644 | 4.435%
5490 | 19-64.5 | -64.4171 | 18.7994 | 341.4418 | 177.3911 | 205.0893 | 248.4548 | 287.2571 | 332.1232 | 4.456%
5491 | 19-64.5 | -64.6884 | 18.7994 | 354.7354 | 177.6 | 205.3956 | 248.9292 | 287.8959 | 332.966 | 4.473%
5492 | 19-65 | -64.9598 | 18.7994 | 368.4203 | 177.7492 | 205.6352 | 249.3271 | 288.4499 | 333.7151 | 4.483%
5493 | 19-65 | -65.2311 | 18.7994 | 382.4545 | 177.8471 | 205.8158 | 249.6536 | 288.9216 | 334.3694 | 4.487%
5494 | 19-65.5 | -65.5024 | 18.7994 | 396.8009 | 177.9222 | 205.9739 | 249.9595 | 289.3753 | 335.0099 | 4.487%
5495 | 19-66 | -65.7737 | 18.7994 | 411.4268 | 177.938 | 206.0587 | 250.169 | 289.7113 | 335.5069 | 4.481%
5496 | 19-66 | -66.045 | 18.7994 | 426.3035 | 177.8544 | 206.0187 | 250.2116 | 289.8404 | 335.7489 | 4.465%
5497 | 19-66.5 | -66.3164 | 18.7994 | 441.4055 | 177.6461 | 205.8231 | 250.0474 | 289.7147 | 335.678 | 4.435%
5498 | 19-66.5 | -66.5877 | 18.7994 | 456.7105 | 177.2004 | 205.319 | 249.4551 | 289.0461 | 334.9239 | 4.381%
5499 | 19-67 | -66.859 | 18.7994 | 472.1987 | 176.6378 | 204.6725 | 248.6657 | 288.1283 | 333.8571 | 4.316%
5500 | 19-67 | -67.1303 | 18.7994 | 487.8526 | 176.0169 | 204.0264 | 247.8812 | 287.2202 | 332.8065 | 4.247%
5501 | 19-67.5 | -67.4016 | 18.7994 | 503.6568 | 175.4063 | 203.413 | 247.1371 | 286.3593 | 331.811 | 4.18%
5502 | 19-67.5 | -67.673 | 18.7994 | 519.5975 | 174.7914 | 202.802 | 246.3964 | 285.5029 | 330.821 | 4.113%
5503 | 19-68 | -67.9443 | 18.7994 | 535.6625 | 174.1584 | 202.1753 | 245.6391 | 284.6294 | 329.8138 | 4.045%
5504 | 19-68 | -68.2156 | 18.7994 | 551.8409 | 173.3486 | 201.3511 | 244.6005 | 283.3935 | 328.3441 | 3.963%
5505 | 19-68.5 | -68.4869 | 18.7994 | 568.123 | 172.3506 | 200.3733 | 243.3539 | 281.8979 | 326.5519 | 3.864%
5506 | 19-69 | -68.7583 | 18.7994 | 584.5 | 171.1694 | 199.2729 | 241.9515 | 280.2156 | 324.5368 | 3.751%
5507 | 19-69 | -69.0296 | 18.7994 | 600.9643 | 169.8762 | 198.0763 | 240.4097 | 278.3523 | 322.289 | 3.632%
5508 | 19-69.5 | -69.3009 | 18.7994 | 617.5088 | 168.5167 | 196.8341 | 238.8043 | 276.4083 | 319.9397 | 3.51%
5509 | 19-69.5 | -69.5722 | 18.7994 | 634.1271 | 167.1085 | 195.5621 | 237.1608 | 274.4182 | 317.5348 | 3.387%
5510 | 19-70 | -69.8435 | 18.7994 | 650.8137 | 165.5719 | 194.1857 | 235.3661 | 272.232 | 314.8784 | 3.258%
5511 | 19-70 | -70.1149 | 18.7994 | 667.5632 | 164.0264 | 192.8546 | 233.6395 | 270.1363 | 312.3404 | 3.133%
5512 | 19-70.5 | -70.3862 | 18.7994 | 684.3712 | 162.5351 | 191.6204 | 232.0551 | 268.2265 | 310.0424 | 3.015%
5513 | 19-70.5 | -70.6575 | 18.7994 | 701.2333 | 161.5187 | 190.7322 | 230.9279 | 266.8778 | 308.4302 | 2.937%
5514 | 19-71 | -70.9288 | 18.7994 | 718.1457 | 160.9352 | 190.1616 | 230.2317 | 266.0683 | 307.4884 | 2.89%
5515 | 19-71 | -71.2001 | 18.7994 | 735.105 | 160.7344 | 189.8719 | 229.918 | 265.7385 | 307.1452 | 2.871%
5516 | 19-71.5 | -71.4715 | 18.7994 | 752.1078 | 160.503 | 189.5458 | 229.5282 | 265.2924 | 306.6352 | 2.85%
5517 | 19-71.5 | -71.7428 | 18.7994 | 769.1513 | 160.4044 | 189.3685 | 229.3348 | 265.0882 | 306.4218 | 2.84%
5518 | 19-72 | -72.0141 | 18.7994 | 786.2329 | 160.4479 | 189.3153 | 229.3016 | 265.0776 | 306.4426 | 2.841%
5519 | 19-72.5 | -72.2854 | 18.7994 | 803.3499 | 160.3122 | 189.1384 | 229.0645 | 264.7841 | 306.0812 | 2.83%
5520 | 19-72.5 | -72.5568 | 18.7994 | 820.5003 | 159.9491 | 188.8162 | 228.6187 | 264.2208 | 305.3754 | 2.804%
5521 | 19-73 | -72.8281 | 18.7994 | 837.6819 | 159.5154 | 188.4523 | 228.1052 | 263.5648 | 304.546 | 2.774%
5522 | 19-73 | -73.0994 | 18.7994 | 854.8927 | 159.5817 | 188.4374 | 228.0461 | 263.4616 | 304.3874 | 2.779%
5523 | 19-73.5 | -73.3707 | 18.7994 | 872.1311 | 160.1569 | 188.8501 | 228.5629 | 264.0752 | 305.1166 | 2.82%
5524 | 19-73.5 | -73.642 | 18.7994 | 889.3954 | 161.0481 | 189.5269 | 229.4286 | 265.1176 | 306.3713 | 2.885%
5525 | 19-74 | -73.9134 | 18.7994 | 906.6841 | 161.7793 | 189.9775 | 229.9566 | 265.7128 | 307.0423 | 2.939%
5526 | 19-74 | -74.1847 | 18.7994 | 923.9957 | 161.8478 | 189.9628 | 229.85 | 265.5125 | 306.7224 | 2.947%
5527 | 19-74.5 | -74.456 | 18.7994 | 941.3291 | 161.3555 | 189.5535 | 229.2031 | 264.6332 | 305.5544 | 2.914%
5528 | 19-74.5 | -74.7273 | 18.7994 | 958.6829 | 160.5656 | 188.9343 | 228.2596 | 263.3732 | 303.902 | 2.86%
5529 | 19-75 | -74.9986 | 18.7994 | 976.056 | 159.9069 | 188.425 | 227.4824 | 262.3343 | 302.5385 | 2.816%
5530 | 19-75.5 | -75.27 | 18.7994 | 993.4475 | 159.4143 | 188.0352 | 226.8721 | 261.5076 | 301.4422 | 2.784%
5531 | 19-75.5 | -75.5413 | 18.7994 | 1010.8562 | 159.1955 | 187.8292 | 226.5017 | 260.9731 | 300.7007 | 2.771%
5532 | 19-76 | -75.8126 | 18.7994 | 1028.2814 | 159.601 | 188.0575 | 226.7387 | 261.2118 | 300.9354 | 2.801%
5533 | 19-76 | -76.0839 | 18.7994 | 1045.7221 | 160.4969 | 188.6359 | 227.4561 | 262.055 | 301.9253 | 2.866%
5534 | 19-76.5 | -76.3553 | 18.7994 | 1063.1775 | 161.5878 | 189.344 | 228.3399 | 263.0985 | 303.1557 | 2.947%
5535 | 19-76.5 | -76.6266 | 18.7994 | 1080.647 | 162.2912 | 189.7969 | 228.8764 | 263.707 | 303.8446 | 3.002%
5536 | 19-77 | -76.8979 | 18.7994 | 1098.1298 | 162.6663 | 189.976 | 229.0327 | 263.8333 | 303.9263 | 3.033%
5537 | 19-77 | -77.1692 | 18.7994 | 1115.6252 | 162.8833 | 190.028 | 229.009 | 263.7285 | 303.7142 | 3.052%
5538 | 19-77.5 | -77.4405 | 18.7994 | 1133.1326 | 163.3933 | 190.4353 | 229.4822 | 264.2572 | 304.3035 | 3.095%
5539 | 19-77.5 | -77.7119 | 18.7994 | 1150.6514 | 164.3039 | 191.1488 | 230.3696 | 265.3028 | 305.5346 | 3.171%
5540 | 19-78 | -77.9832 | 18.7994 | 1168.1812 | 165.4601 | 192.056 | 231.5089 | 266.6548 | 307.1375 | 3.269%
5541 | 19-78.5 | -78.2545 | 18.7994 | 1185.7213 | 166.6351 | 193.0088 | 232.7087 | 268.0814 | 308.8318 | 3.371%
5542 | 19-78.5 | -78.5258 | 18.7994 | 1203.2712 | 167.7882 | 193.9701 | 233.9093 | 269.5005 | 310.5082 | 3.476%
5543 | 19-79 | -78.7971 | 18.7994 | 1220.8307 | 168.8632 | 194.9032 | 235.0657 | 270.8601 | 312.106 | 3.577%
5544 | 19-79 | -79.0685 | 18.7994 | 1238.399 | 169.7997 | 195.7922 | 236.1752 | 272.1711 | 313.6542 | 3.668%
5545 | 19-79.5 | -79.3398 | 18.7994 | 1255.976 | 170.5504 | 196.5803 | 237.1413 | 273.2979 | 314.968 | 3.745%
5546 | 19-79.5 | -79.6111 | 18.7994 | 1273.5611 | 171.2065 | 197.3174 | 238.0325 | 274.3265 | 316.1554 | 3.815%
5547 | 19-80 | -79.8824 | 18.7994 | 1291.1541 | 171.8981 | 198.1239 | 239.0293 | 275.4962 | 317.5274 | 3.89%
5548 | 19-80 | -80.1537 | 18.7994 | 1308.7545 | 172.5837 | 198.9279 | 240.0244 | 276.6649 | 318.8997 | 3.965%
5549 | 19-80.5 | -80.4251 | 18.7994 | 1326.3621 | 173.2511 | 199.711 | 240.9912 | 277.7987 | 320.2288 | 4.039%
5550 | 19-80.5 | -80.6964 | 18.7994 | 1343.9764 | 173.9154 | 200.4925 | 241.9596 | 278.937 | 321.5666 | 4.113%
5551 | 19-81 | -80.9677 | 18.7994 | 1361.5973 | 174.5393 | 201.2238 | 242.8614 | 279.9937 | 322.8043 | 4.184%
5552 | 19-81 | -81.239 | 18.7994 | 1379.2244 | 175.1352 | 201.9271 | 243.7362 | 281.0251 | 324.0199 | 4.252%
5553 | 19-81.5 | -81.5104 | 18.7994 | 1396.8575 | 175.7284 | 202.639 | 244.6404 | 282.1068 | 325.3126 | 4.32%
5554 | 19-82 | -81.7817 | 18.7994 | 1414.4962 | 176.2614 | 203.2797 | 245.4556 | 283.0834 | 326.481 | 4.381%
5555 | 19-82 | -82.053 | 18.7994 | 1432.1404 | 176.7431 | 203.865 | 246.2102 | 283.9955 | 327.5813 | 4.436%
5556 | 19-82.5 | -82.3243 | 18.7994 | 1449.7899 | 177.1927 | 204.424 | 246.9499 | 284.9053 | 328.6962 | 4.486%
5557 | 19-82.5 | -82.5956 | 18.7994 | 1467.4443 | 177.5393 | 204.8588 | 247.5312 | 285.625 | 329.5832 | 4.524%
5558 | 19-83 | -82.867 | 18.7994 | 1485.1035 | 177.8019 | 205.2051 | 248.0191 | 286.2488 | 330.3734 | 4.551%
5559 | 19-83 | -83.1383 | 18.7994 | 1502.7673 | 178.0025 | 205.4982 | 248.472 | 286.858 | 331.1766 | 4.568%
5560 | 19-83.5 | -83.4096 | 18.7994 | 1520.4354 | 178.0758 | 205.6414 | 248.7388 | 287.2479 | 331.7214 | 4.569%
5561 | 19-83.5 | -83.6809 | 18.7994 | 1538.1078 | 178.0636 | 205.691 | 248.9007 | 287.524 | 332.1431 | 4.56%
5562 | 19-84 | -83.9522 | 18.7994 | 1555.7841 | 177.9918 | 205.6826 | 249.01 | 287.7544 | 332.5298 | 4.541%
5563 | 19-84 | -84.2236 | 18.7994 | 1573.4644 | 177.7896 | 205.5255 | 248.9422 | 287.7831 | 332.6865 | 4.507%
5564 | 19-84.5 | -84.4949 | 18.7994 | 1591.1482 | 177.4787 | 205.2556 | 248.7475 | 287.6736 | 332.6936 | 4.46%
5565 | 19-85 | -84.7662 | 18.7994 | 1608.8356 | 177.0674 | 204.8881 | 248.4493 | 287.4576 | 332.5928 | 4.401%
5566 | 19-85 | -85.0375 | 18.7994 | 1626.5264 | 176.4738 | 204.3329 | 247.9296 | 286.9907 | 332.2081 | 4.321%
5567 | 19-85.5 | -85.3089 | 18.7994 | 1644.2204 | 175.7442 | 203.6607 | 247.2931 | 286.4112 | 331.7195 | 4.226%
5568 | 19-85.5 | -85.5802 | 18.7994 | 1661.9174 | 174.8768 | 202.8762 | 246.5483 | 285.7309 | 331.1434 | 4.118%
5569 | 19-86 | -85.8515 | 18.7994 | 1679.6175 | 173.4372 | 201.5667 | 245.0879 | 284.1534 | 329.4483 | 3.959%
5570 | 19-86 | -86.1228 | 18.7994 | 1697.3203 | 171.3326 | 199.831 | 243.061 | 281.8765 | 326.8934 | 3.749%
5571 | 19-86.5 | -86.3941 | 18.7994 | 1715.0258 | 168.6304 | 197.696 | 240.5087 | 278.956 | 323.5523 | 3.5%
5572 | 19-86.5 | -86.6655 | 18.7994 | 1732.7339 | 165.4512 | 195.2125 | 237.4724 | 275.4213 | 319.4375 | 3.231%
5573 | 19-87 | -86.9368 | 18.7994 | 1750.4445 | 161.8878 | 192.4221 | 234.0997 | 271.4747 | 314.8199 | 2.952%
5574 | 19-87 | -87.2081 | 18.7994 | 1768.1574 | 157.9878 | 189.2618 | 230.4253 | 267.1657 | 309.7679 | 2.671%
5575 | 19-87.5 | -87.4794 | 18.7994 | 1785.8726 | 153.8491 | 185.807 | 226.5154 | 262.5649 | 304.3558 | 2.398%
5576 | 19-88 | -87.7507 | 18.7994 | 1803.5898 | 149.5526 | 182.137 | 222.484 | 257.8166 | 298.7654 | 2.142%
5577 | 19-88 | -88.0221 | 18.7994 | 1821.3092 | 145.1356 | 178.2772 | 218.3474 | 252.9428 | 293.0254 | 1.906%
5578 | 19-88.5 | -88.2934 | 18.7994 | 1839.0304 | 140.6636 | 174.2974 | 214.1351 | 247.9645 | 287.1445 | 1.692%
5579 | 19-88.5 | -88.5647 | 18.7994 | 1856.7536 | 136.2258 | 170.2978 | 209.9561 | 243.0114 | 281.2771 | 1.503%
5580 | 19-89 | -88.836 | 18.7994 | 1874.4784 | 131.8614 | 166.3267 | 205.832 | 238.1062 | 275.447 | 1.338%
5581 | 19-89 | -89.1074 | 18.7994 | 1892.205 | 127.6663 | 162.5117 | 201.8496 | 233.3501 | 269.7715 | 1.196%
5582 | 19-89.5 | -89.3787 | 18.7994 | 1909.9331 | 124.0822 | 159.2555 | 198.6099 | 229.5437 | 265.2985 | 1.089%
5583 | 19-89.5 | -89.65 | 18.7994 | 1927.6627 | 121.235 | 156.4893 | 196.0206 | 226.5646 | 261.8523 | 1.009%
5584 | 19-90 | -89.9213 | 18.7994 | 1945.3938 | 118.9737 | 154.1293 | 193.9254 | 224.1908 | 259.1331 | 0.9497%
5585 | 19-90 | -90.1926 | 18.7994 | 1963.1262 | 117.1865 | 152.1273 | 192.2801 | 222.3965 | 257.1405 | 0.9048%
5586 | 19-90.5 | -90.464 | 18.7994 | 1980.8598 | 115.8275 | 150.5029 | 191.0645 | 221.1329 | 255.8062 | 0.8721%
5587 | 19-90.5 | -90.7353 | 18.7994 | 1998.5947 | 114.8103 | 149.2587 | 190.2116 | 220.2784 | 254.9612 | 0.8488%
5588 | 19-50 | -50.0371 | 19.0707 | 743.409 | 147.6644 | 180.0558 | 214.7459 | 245.3636 | 280.3477 | 2.08%
5589 | 19-50.5 | -50.3084 | 19.0707 | 726.6004 | 148.661 | 180.672 | 215.5924 | 246.4274 | 281.6737 | 2.135%
5590 | 19-50.5 | -50.5797 | 19.0707 | 709.8445 | 149.585 | 181.2472 | 216.388 | 247.4314 | 282.9295 | 2.187%
5591 | 19-51 | -50.851 | 19.0707 | 693.1452 | 150.4707 | 181.8035 | 217.1662 | 248.4198 | 284.1726 | 2.238%
5592 | 19-51 | -51.1224 | 19.0707 | 676.5067 | 151.3622 | 182.3709 | 217.9718 | 249.4523 | 285.4807 | 2.29%
5593 | 19-51.5 | -51.3937 | 19.0707 | 659.9335 | 152.1932 | 182.9017 | 218.727 | 250.4214 | 286.71 | 2.34%
5594 | 19-51.5 | -51.665 | 19.0707 | 643.4309 | 153.0063 | 183.4243 | 219.4774 | 251.3893 | 287.943 | 2.389%
5595 | 19-52 | -51.9363 | 19.0707 | 627.0044 | 153.8407 | 183.9664 | 220.2665 | 252.4151 | 289.2578 | 2.44%
5596 | 19-52 | -52.2077 | 19.0707 | 610.6601 | 154.6135 | 184.4699 | 221.0038 | 253.3768 | 290.4939 | 2.488%
5597 | 19-52.5 | -52.479 | 19.0707 | 594.4049 | 155.3669 | 184.9639 | 221.7359 | 254.3379 | 291.7354 | 2.535%
5598 | 19-53 | -52.7503 | 19.0707 | 578.2464 | 156.1284 | 185.4687 | 222.4951 | 255.3423 | 293.0408 | 2.584%
5599 | 19-53 | -53.0216 | 19.0707 | 562.1929 | 156.8309 | 185.9384 | 223.2107 | 256.2956 | 294.2863 | 2.628%
5600 | 19-53.5 | -53.2929 | 19.0707 | 546.2537 | 157.5224 | 186.4017 | 223.9184 | 257.2397 | 295.5212 | 2.673%
5601 | 19-53.5 | -53.5643 | 19.0707 | 530.4391 | 158.2214 | 186.8705 | 224.633 | 258.1922 | 296.7667 | 2.718%
5602 | 19-54 | -53.8356 | 19.0707 | 514.7607 | 158.8453 | 187.2858 | 225.2633 | 259.0306 | 297.8612 | 2.759%
5603 | 19-54 | -54.1069 | 19.0707 | 499.2313 | 159.4447 | 187.6839 | 225.8667 | 259.8327 | 298.9079 | 2.799%
5604 | 19-54.5 | -54.3782 | 19.0707 | 483.8654 | 160.0352 | 188.0757 | 226.4586 | 260.6183 | 299.9321 | 2.838%
5605 | 19-54.5 | -54.6495 | 19.0707 | 468.6789 | 160.5627 | 188.4272 | 226.991 | 261.3261 | 300.856 | 2.874%
5606 | 19-55 | -54.9209 | 19.0707 | 453.69 | 161.1008 | 188.7918 | 227.5477 | 262.0695 | 301.83 | 2.911%
5607 | 19-55 | -55.1922 | 19.0707 | 438.9189 | 161.6601 | 189.1796 | 228.1426 | 262.8659 | 302.8755 | 2.949%
5608 | 19-55.5 | -55.4635 | 19.0707 | 424.3884 | 162.1711 | 189.5394 | 228.6905 | 263.5968 | 303.8326 | 2.984%
5609 | 19-55.5 | -55.7348 | 19.0707 | 410.1242 | 162.7134 | 189.9349 | 229.2878 | 264.3902 | 304.8681 | 3.022%
5610 | 19-56 | -56.0061 | 19.0707 | 396.155 | 163.2809 | 190.3703 | 229.9395 | 265.2516 | 305.9887 | 3.063%
5611 | 19-56.5 | -56.2775 | 19.0707 | 382.5131 | 163.818 | 190.7952 | 230.5668 | 266.0751 | 307.0539 | 3.102%
5612 | 19-56.5 | -56.5488 | 19.0707 | 369.2349 | 164.3858 | 191.2602 | 231.2449 | 266.9591 | 308.1914 | 3.144%
5613 | 19-57 | -56.8201 | 19.0707 | 356.361 | 164.9681 | 191.76 | 231.9647 | 267.8912 | 309.3842 | 3.189%
5614 | 19-57 | -57.0914 | 19.0707 | 343.9369 | 165.5081 | 192.235 | 232.6364 | 268.7519 | 310.4764 | 3.231%
5615 | 19-57.5 | -57.3628 | 19.0707 | 332.0132 | 166.0791 | 192.7494 | 233.358 | 269.6721 | 311.6396 | 3.276%
5616 | 19-57.5 | -57.6341 | 19.0707 | 320.6456 | 166.6621 | 193.293 | 234.1146 | 270.6325 | 312.8486 | 3.324%
5617 | 19-58 | -57.9054 | 19.0707 | 309.8954 | 167.2048 | 193.8117 | 234.8253 | 271.526 | 313.9647 | 3.369%
5618 | 19-58 | -58.1767 | 19.0707 | 299.829 | 167.7507 | 194.345 | 235.5432 | 272.4185 | 315.0686 | 3.415%
5619 | 19-58.5 | -58.448 | 19.0707 | 290.5176 | 168.2744 | 194.8763 | 236.2422 | 273.275 | 316.1148 | 3.462%
5620 | 19-58.5 | -58.7194 | 19.0707 | 282.0359 | 168.7341 | 195.358 | 236.8522 | 274.0035 | 316.9838 | 3.504%
5621 | 19-59 | -58.9907 | 19.0707 | 274.4609 | 169.1941 | 195.8494 | 237.4664 | 274.7301 | 317.843 | 3.548%
5622 | 19-59.5 | -59.262 | 19.0707 | 267.8696 | 169.6385 | 196.3329 | 238.0594 | 275.4221 | 318.6504 | 3.591%
5623 | 19-59.5 | -59.5333 | 19.0707 | 262.3361 | 170.0438 | 196.7741 | 238.5843 | 276.0205 | 319.3324 | 3.632%
5624 | 19-60 | -59.8046 | 19.0707 | 257.9284 | 170.4594 | 197.2318 | 239.1301 | 276.644 | 320.0446 | 3.675%
5625 | 19-60 | -60.076 | 19.0707 | 254.7052 | 170.8665 | 197.682 | 239.6598 | 277.2428 | 320.7213 | 3.717%
5626 | 19-60.5 | -60.3473 | 19.0707 | 252.7117 | 171.2488 | 198.0956 | 240.1279 | 277.7553 | 321.2807 | 3.759%
5627 | 19-60.5 | -60.6186 | 19.0707 | 251.9771 | 171.6556 | 198.5396 | 240.6359 | 278.3166 | 321.8997 | 3.803%
5628 | 19-61 | -60.8899 | 19.0707 | 252.5124 | 172.0622 | 198.9813 | 241.1346 | 278.8616 | 322.4937 | 3.848%
5629 | 19-61 | -61.1613 | 19.0707 | 254.3095 | 172.4496 | 199.3947 | 241.5843 | 279.3372 | 322.9926 | 3.892%
5630 | 19-61.5 | -61.4326 | 19.0707 | 257.3421 | 172.8599 | 199.8391 | 242.0751 | 279.8635 | 323.5539 | 3.939%
5631 | 19-61.5 | -61.7039 | 19.0707 | 261.5672 | 173.2638 | 200.2747 | 242.553 | 280.3728 | 324.0931 | 3.986%
5632 | 19-62 | -61.9752 | 19.0707 | 266.9281 | 173.6448 | 200.6819 | 242.9933 | 280.8357 | 324.5753 | 4.031%
5633 | 19-62 | -62.2465 | 19.0707 | 273.3579 | 174.0418 | 201.1165 | 243.481 | 281.3658 | 325.1494 | 4.078%
5634 | 19-62.5 | -62.5179 | 19.0707 | 280.7834 | 174.4708 | 201.6011 | 244.0499 | 282.0077 | 325.8732 | 4.128%
5635 | 19-63 | -62.7892 | 19.0707 | 289.1277 | 174.9657 | 202.1805 | 244.7633 | 282.8426 | 326.8499 | 4.183%
5636 | 19-63 | -63.0605 | 19.0707 | 298.3138 | 175.5622 | 202.902 | 245.6884 | 283.9568 | 328.1898 | 4.249%
5637 | 19-63.5 | -63.3318 | 19.0707 | 308.2663 | 176.1156 | 203.5765 | 246.5611 | 285.0143 | 329.4687 | 4.309%
5638 | 19-63.5 | -63.6031 | 19.0707 | 318.9136 | 176.5443 | 204.1009 | 247.2424 | 285.842 | 330.4717 | 4.356%
5639 | 19-64 | -63.8745 | 19.0707 | 330.1883 | 176.8796 | 204.5218 | 247.8051 | 286.5388 | 331.3304 | 4.392%
5640 | 19-64 | -64.1458 | 19.0707 | 342.0285 | 177.144 | 204.8642 | 248.2787 | 287.1375 | 332.0817 | 4.419%
5641 | 19-64.5 | -64.4171 | 19.0707 | 354.3774 | 177.3701 | 205.172 | 248.7256 | 287.719 | 332.8287 | 4.441%
5642 | 19-64.5 | -64.6884 | 19.0707 | 367.1837 | 177.5849 | 205.4846 | 249.2073 | 288.3658 | 333.6808 | 4.459%
5643 | 19-65 | -64.9598 | 19.0707 | 380.4012 | 177.7428 | 205.7346 | 249.6182 | 288.9355 | 334.4486 | 4.47%
5644 | 19-65 | -65.2311 | 19.0707 | 393.9884 | 177.8517 | 205.929 | 249.9634 | 289.4305 | 335.132 | 4.475%
5645 | 19-65.5 | -65.5024 | 19.0707 | 407.9085 | 177.9403 | 206.1054 | 250.2956 | 289.9185 | 335.8166 | 4.476%
5646 | 19-66 | -65.7737 | 19.0707 | 422.1283 | 177.9713 | 206.2111 | 250.536 | 290.2949 | 336.3659 | 4.472%
5647 | 19-66 | -66.045 | 19.0707 | 436.6187 | 177.912 | 206.2036 | 250.625 | 290.4842 | 336.6848 | 4.458%
5648 | 19-66.5 | -66.3164 | 19.0707 | 451.3536 | 177.7431 | 206.0596 | 250.5333 | 290.4508 | 336.7308 | 4.432%
5649 | 19-66.5 | -66.5877 | 19.0707 | 466.3097 | 177.3502 | 205.624 | 250.0357 | 289.9022 | 336.1276 | 4.384%
5650 | 19-67 | -66.859 | 19.0707 | 481.4663 | 176.8386 | 205.0429 | 249.3363 | 289.0978 | 335.2028 | 4.324%
5651 | 19-67 | -67.1303 | 19.0707 | 496.8052 | 176.2567 | 204.4463 | 248.6188 | 288.2735 | 334.2564 | 4.259%
5652 | 19-67.5 | -67.4016 | 19.0707 | 512.3099 | 175.6717 | 203.8645 | 247.9162 | 287.4637 | 333.3237 | 4.195%
5653 | 19-67.5 | -67.673 | 19.0707 | 527.9658 | 175.0749 | 203.2747 | 247.2019 | 286.6384 | 332.3705 | 4.13%
5654 | 19-68 | -67.9443 | 19.0707 | 543.7598 | 174.4564 | 202.6634 | 246.4615 | 285.7829 | 331.3825 | 4.064%
5655 | 19-68 | -68.2156 | 19.0707 | 559.6801 | 173.6567 | 201.8476 | 245.4277 | 284.548 | 329.9089 | 3.983%
5656 | 19-68.5 | -68.4869 | 19.0707 | 575.7163 | 172.6671 | 200.8746 | 244.1792 | 283.0434 | 328.0985 | 3.886%
5657 | 19-69 | -68.7583 | 19.0707 | 591.8589 | 171.4935 | 199.7769 | 242.7703 | 281.3453 | 326.0555 | 3.774%
5658 | 19-69 | -69.0296 | 19.0707 | 608.0994 | 170.2062 | 198.5806 | 241.2183 | 279.4611 | 323.773 | 3.656%
5659 | 19-69.5 | -69.3009 | 19.0707 | 624.4301 | 168.851 | 197.3371 | 239.6017 | 277.4956 | 321.389 | 3.534%
5660 | 19-69.5 | -69.5722 | 19.0707 | 640.8441 | 167.4454 | 196.063 | 237.9471 | 275.4855 | 318.9525 | 3.412%
5661 | 19-70 | -69.8435 | 19.0707 | 657.3352 | 165.9081 | 194.6802 | 236.1356 | 273.2717 | 316.255 | 3.283%
5662 | 19-70 | -70.1149 | 19.0707 | 673.8976 | 164.3602 | 193.3407 | 234.3901 | 271.1462 | 313.6735 | 3.157%
5663 | 19-70.5 | -70.3862 | 19.0707 | 690.5262 | 162.8656 | 192.0974 | 232.7868 | 269.2079 | 311.3344 | 3.04%
5664 | 19-70.5 | -70.6575 | 19.0707 | 707.2162 | 161.8478 | 191.2013 | 231.6465 | 267.841 | 309.6973 | 2.96%
5665 | 19-71 | -70.9288 | 19.0707 | 723.9635 | 161.2656 | 190.6263 | 230.9461 | 267.0273 | 308.7516 | 2.914%
5666 | 19-71 | -71.2001 | 19.0707 | 740.764 | 161.0683 | 190.3358 | 230.6369 | 266.7072 | 308.4247 | 2.894%
5667 | 19-71.5 | -71.4715 | 19.0707 | 757.6143 | 160.8417 | 190.0093 | 230.2541 | 266.2756 | 307.9385 | 2.874%
5668 | 19-71.5 | -71.7428 | 19.0707 | 774.5109 | 160.7489 | 189.8333 | 230.0732 | 266.095 | 307.7629 | 2.864%
5669 | 19-72 | -72.0141 | 19.0707 | 791.451 | 160.7976 | 189.7819 | 230.0558 | 266.1147 | 307.832 | 2.864%
5670 | 19-72.5 | -72.2854 | 19.0707 | 808.4318 | 160.6626 | 189.598 | 229.8232 | 265.8373 | 307.5019 | 2.853%
5671 | 19-72.5 | -72.5568 | 19.0707 | 825.4507 | 160.2887 | 189.2608 | 229.3705 | 265.2758 | 306.809 | 2.826%
5672 | 19-73 | -72.8281 | 19.0707 | 842.5053 | 159.8411 | 188.8795 | 228.8463 | 264.6161 | 305.9853 | 2.794%
5673 | 19-73 | -73.0994 | 19.0707 | 859.5936 | 159.9197 | 188.8665 | 228.8006 | 264.5381 | 305.8666 | 2.799%
5674 | 19-73.5 | -73.3707 | 19.0707 | 876.7134 | 160.5248 | 189.3041 | 229.3627 | 265.217 | 306.6865 | 2.842%
5675 | 19-73.5 | -73.642 | 19.0707 | 893.863 | 161.4479 | 190.0089 | 230.2774 | 266.3291 | 308.0367 | 2.909%
5676 | 19-74 | -73.9134 | 19.0707 | 911.0407 | 162.1521 | 190.4328 | 230.7764 | 266.8937 | 308.6756 | 2.961%
5677 | 19-74 | -74.1847 | 19.0707 | 928.2449 | 162.1141 | 190.3362 | 230.5599 | 266.5572 | 308.1874 | 2.961%
5678 | 19-74.5 | -74.456 | 19.0707 | 945.474 | 161.4642 | 189.8068 | 229.7462 | 265.4663 | 306.7534 | 2.917%
5679 | 19-74.5 | -74.7273 | 19.0707 | 962.7267 | 160.5164 | 189.0656 | 228.6287 | 263.9825 | 304.8163 | 2.852%
5680 | 19-75 | -74.9986 | 19.0707 | 980.0017 | 159.7008 | 188.4357 | 227.6768 | 262.7169 | 303.1621 | 2.798%
5681 | 19-75.5 | -75.27 | 19.0707 | 997.2979 | 159.0836 | 187.9481 | 226.9209 | 261.6981 | 301.8167 | 2.758%
5682 | 19-75.5 | -75.5413 | 19.0707 | 1014.6141 | 158.8349 | 187.7088 | 226.4925 | 261.0812 | 300.9623 | 2.743%
5683 | 19-76 | -75.8126 | 19.0707 | 1031.9492 | 159.2712 | 187.9794 | 226.7776 | 261.373 | 301.2557 | 2.775%
5684 | 19-76 | -76.0839 | 19.0707 | 1049.3024 | 160.2287 | 188.6352 | 227.5916 | 262.3307 | 302.3818 | 2.845%
5685 | 19-76.5 | -76.3553 | 19.0707 | 1066.6726 | 161.3599 | 189.3909 | 228.5289 | 263.4328 | 303.6762 | 2.929%
5686 | 19-76.5 | -76.6266 | 19.0707 | 1084.0591 | 162.0525 | 189.8408 | 229.0487 | 264.0107 | 304.3168 | 2.983%
5687 | 19-77 | -76.8979 | 19.0707 | 1101.461 | 162.388 | 189.9804 | 229.1367 | 264.0403 | 304.2664 | 3.011%
5688 | 19-77 | -77.1692 | 19.0707 | 1118.8776 | 162.5661 | 189.9923 | 229.0427 | 263.8352 | 303.9164 | 3.027%
5689 | 19-77.5 | -77.4405 | 19.0707 | 1136.3081 | 163.0988 | 190.4163 | 229.5242 | 264.3632 | 304.4929 | 3.072%
5690 | 19-77.5 | -77.7119 | 19.0707 | 1153.7519 | 164.1104 | 191.2015 | 230.4956 | 265.5035 | 305.8307 | 3.156%
5691 | 19-78 | -77.9832 | 19.0707 | 1171.2084 | 165.4185 | 192.2173 | 231.7696 | 267.0138 | 307.6195 | 3.266%
5692 | 19-78.5 | -78.2545 | 19.0707 | 1188.6769 | 166.7459 | 193.2797 | 233.1055 | 268.6006 | 309.5025 | 3.381%
5693 | 19-78.5 | -78.5258 | 19.0707 | 1206.157 | 168.0508 | 194.351 | 234.4433 | 270.1818 | 311.3701 | 3.499%
5694 | 19-79 | -78.7971 | 19.0707 | 1223.648 | 169.2459 | 195.3726 | 235.7083 | 271.6681 | 313.1158 | 3.612%
5695 | 19-79 | -79.0685 | 19.0707 | 1241.1496 | 170.2105 | 196.2896 | 236.8434 | 273.0014 | 314.6813 | 3.708%
5696 | 19-79.5 | -79.3398 | 19.0707 | 1258.6611 | 170.9339 | 197.0407 | 237.7444 | 274.0351 | 315.8669 | 3.784%
5697 | 19-79.5 | -79.6111 | 19.0707 | 1276.1822 | 171.5444 | 197.7149 | 238.5348 | 274.9254 | 316.8689 | 3.851%
5698 | 19-80 | -79.8824 | 19.0707 | 1293.7125 | 172.2163 | 198.4924 | 239.4796 | 276.0202 | 318.1371 | 3.925%
5699 | 19-80 | -80.1537 | 19.0707 | 1311.2515 | 172.9097 | 199.3009 | 240.47 | 277.1748 | 319.4829 | 4.002%
5700 | 19-80.5 | -80.4251 | 19.0707 | 1328.7988 | 173.6012 | 200.1083 | 241.4607 | 278.3311 | 320.8325 | 4.079%
5701 | 19-80.5 | -80.6964 | 19.0707 | 1346.3541 | 174.2925 | 200.9188 | 242.4605 | 279.5027 | 322.205 | 4.158%
5702 | 19-81 | -80.9677 | 19.0707 | 1363.9171 | 174.9429 | 201.6784 | 243.3931 | 280.5917 | 323.4765 | 4.233%
5703 | 19-81 | -81.239 | 19.0707 | 1381.4874 | 175.5642 | 202.4084 | 244.2958 | 281.6515 | 324.7206 | 4.305%
5704 | 19-81.5 | -81.5104 | 19.0707 | 1399.0647 | 176.1833 | 203.1468 | 245.2266 | 282.7594 | 326.038 | 4.376%
5705 | 19-82 | -81.7817 | 19.0707 | 1416.6487 | 176.742 | 203.8138 | 246.0683 | 283.7618 | 327.2307 | 4.442%
5706 | 19-82 | -82.053 | 19.0707 | 1434.2392 | 177.2501 | 204.4261 | 246.8497 | 284.6998 | 328.355 | 4.501%
5707 | 19-82.5 | -82.3243 | 19.0707 | 1451.8358 | 177.7276 | 205.0128 | 247.6159 | 285.6339 | 329.4907 | 4.555%
5708 | 19-82.5 | -82.5956 | 19.0707 | 1469.4383 | 178.1028 | 205.4752 | 248.2216 | 286.3741 | 330.3924 | 4.598%
5709 | 19-83 | -82.867 | 19.0707 | 1487.0465 | 178.3963 | 205.8513 | 248.7361 | 287.0202 | 331.1988 | 4.63%
5710 | 19-83 | -83.1383 | 19.0707 | 1504.66 | 178.631 | 206.1778 | 249.2199 | 287.6566 | 332.0235 | 4.652%
5711 | 19-83.5 | -83.4096 | 19.0707 | 1522.2788 | 178.7413 | 206.3583 | 249.5231 | 288.0809 | 332.5992 | 4.659%
5712 | 19-83.5 | -83.6809 | 19.0707 | 1539.9026 | 178.7684 | 206.449 | 249.7278 | 288.4003 | 333.0638 | 4.654%
5713 | 19-84 | -83.9522 | 19.0707 | 1557.5311 | 178.7375 | 206.4848 | 249.8854 | 288.6822 | 333.5046 | 4.641%
5714 | 19-84 | -84.2236 | 19.0707 | 1575.1642 | 178.5714 | 206.3649 | 249.8555 | 288.7481 | 333.6969 | 4.611%
5715 | 19-84.5 | -84.4949 | 19.0707 | 1592.8017 | 178.3009 | 206.13 | 249.6953 | 288.6715 | 333.7338 | 4.568%
5716 | 19-85 | -84.7662 | 19.0707 | 1610.4434 | 177.9357 | 205.7975 | 249.4319 | 288.489 | 333.6637 | 4.513%
5717 | 19-85 | -85.0375 | 19.0707 | 1628.0891 | 177.3738 | 205.2507 | 248.9144 | 288.0176 | 333.2657 | 4.435%
5718 | 19-85.5 | -85.3089 | 19.0707 | 1645.7387 | 176.6611 | 204.5596 | 248.2457 | 287.3925 | 332.7147 | 4.339%
5719 | 19-85.5 | -85.5802 | 19.0707 | 1663.392 | 175.778 | 203.73 | 247.4352 | 286.6267 | 332.0285 | 4.226%
5720 | 19-86 | -85.8515 | 19.0707 | 1681.0489 | 174.3117 | 202.3677 | 245.9011 | 284.9553 | 330.2149 | 4.061%
5721 | 19-86 | -86.1228 | 19.0707 | 1698.7091 | 172.1702 | 200.5716 | 243.7923 | 282.576 | 327.5325 | 3.841%
5722 | 19-86.5 | -86.3941 | 19.0707 | 1716.3726 | 169.4272 | 198.3725 | 241.1554 | 279.5517 | 324.0643 | 3.582%
5723 | 19-86.5 | -86.6655 | 19.0707 | 1734.0393 | 166.265 | 195.8679 | 238.0973 | 275.995 | 319.9279 | 3.306%
5724 | 19-87 | -86.9368 | 19.0707 | 1751.7089 | 162.7712 | 193.1349 | 234.7599 | 272.0995 | 315.3812 | 3.026%
5725 | 19-87 | -87.2081 | 19.0707 | 1769.3814 | 158.9804 | 190.1032 | 231.1647 | 267.8969 | 310.4692 | 2.746%
5726 | 19-87.5 | -87.4794 | 19.0707 | 1787.0567 | 154.9389 | 186.7714 | 227.3189 | 263.3835 | 305.1737 | 2.472%
5727 | 19-88 | -87.7507 | 19.0707 | 1804.7345 | 150.7338 | 183.2265 | 223.351 | 258.7235 | 299.7025 | 2.214%
5728 | 19-88 | -88.0221 | 19.0707 | 1822.4149 | 146.4024 | 179.4975 | 219.2825 | 253.9446 | 294.0908 | 1.974%
5729 | 19-88.5 | -88.2934 | 19.0707 | 1840.0976 | 142.0351 | 175.6741 | 215.1672 | 249.0961 | 288.3805 | 1.758%
5730 | 19-88.5 | -88.5647 | 19.0707 | 1857.7827 | 137.7394 | 171.8796 | 211.1456 | 244.3463 | 282.7731 | 1.568%
5731 | 19-89 | -88.836 | 19.0707 | 1875.4699 | 133.5535 | 168.1618 | 207.2372 | 239.7151 | 277.2879 | 1.402%
5732 | 19-89 | -89.1074 | 19.0707 | 1893.1593 | 129.5841 | 164.6502 | 203.5224 | 235.2922 | 272.0255 | 1.262%
5733 | 19-89.5 | -89.3787 | 19.0707 | 1910.8506 | 126.2499 | 161.7251 | 200.5771 | 231.8432 | 267.9876 | 1.157%
5734 | 19-89.5 | -89.65 | 19.0707 | 1928.5438 | 123.6719 | 159.3134 | 198.3173 | 229.2467 | 265.0047 | 1.081%
5735 | 19-90 | -89.9213 | 19.0707 | 1946.2388 | 121.6815 | 157.3136 | 196.5589 | 227.2512 | 262.7386 | 1.025%
5736 | 19-90 | -90.1926 | 19.0707 | 1963.9356 | 120.1037 | 155.6278 | 195.1876 | 225.7453 | 261.0801 | 0.9826%
5737 | 19-90.5 | -90.464 | 19.0707 | 1981.6339 | 118.8903 | 154.2271 | 194.1672 | 224.6727 | 259.955 | 0.951%
5738 | 19-90.5 | -90.7353 | 19.0707 | 1999.3339 | 117.9537 | 153.1018 | 193.4128 | 223.9072 | 259.1937 | 0.9275%
5739 | 19-50 | -50.0371 | 19.342 | 749.4653 | 146.2258 | 179.2703 | 213.7982 | 244.2688 | 279.0832 | 2.003%
5740 | 19-50.5 | -50.3084 | 19.342 | 732.8219 | 147.3165 | 179.9461 | 214.7201 | 245.4252 | 280.5223 | 2.061%
5741 | 19-50.5 | -50.5797 | 19.342 | 716.2376 | 148.3369 | 180.5791 | 215.592 | 246.5226 | 281.8921 | 2.117%
5742 | 19-51 | -50.851 | 19.342 | 699.7169 | 149.3215 | 181.1945 | 216.4476 | 247.6057 | 283.2506 | 2.172%
5743 | 19-51 | -51.1224 | 19.342 | 683.2642 | 150.3145 | 181.8224 | 217.3327 | 248.7354 | 284.6772 | 2.229%
5744 | 19-51.5 | -51.3937 | 19.342 | 666.8848 | 151.2442 | 182.4111 | 218.1628 | 249.7952 | 286.016 | 2.283%
5745 | 19-51.5 | -51.665 | 19.342 | 650.5841 | 152.1546 | 182.9905 | 218.9853 | 250.8494 | 287.352 | 2.337%
5746 | 19-52 | -51.9363 | 19.342 | 634.3684 | 153.0873 | 183.5894 | 219.8452 | 251.9587 | 288.7654 | 2.393%
5747 | 19-52 | -52.2077 | 19.342 | 618.2442 | 153.9581 | 184.149 | 220.6505 | 252.9991 | 290.0923 | 2.446%
5748 | 19-52.5 | -52.479 | 19.342 | 602.219 | 154.8095 | 184.6988 | 221.449 | 254.0357 | 291.4199 | 2.499%
5749 | 19-53 | -52.7503 | 19.342 | 586.3009 | 155.6696 | 185.2594 | 222.2736 | 255.114 | 292.8087 | 2.553%
5750 | 19-53 | -53.0216 | 19.342 | 570.4989 | 156.4702 | 185.7837 | 223.0509 | 256.1348 | 294.1278 | 2.604%
5751 | 19-53.5 | -53.2929 | 19.342 | 554.823 | 157.2611 | 186.3011 | 223.8168 | 257.1397 | 295.4257 | 2.655%
5752 | 19-53.5 | -53.5643 | 19.342 | 539.2843 | 158.0609 | 186.8233 | 224.5859 | 258.1464 | 296.7236 | 2.707%
5753 | 19-54 | -53.8356 | 19.342 | 523.8948 | 158.7816 | 187.2883 | 225.2626 | 259.0266 | 297.853 | 2.755%
5754 | 19-54 | -54.1069 | 19.342 | 508.6684 | 159.4725 | 187.7316 | 225.9057 | 259.8616 | 298.9228 | 2.802%
5755 | 19-54.5 | -54.3782 | 19.342 | 493.6199 | 160.1472 | 188.1635 | 226.5303 | 260.6714 | 299.9592 | 2.848%
5756 | 19-54.5 | -54.6495 | 19.342 | 478.7663 | 160.7456 | 188.5464 | 227.0842 | 261.3894 | 300.8784 | 2.89%
5757 | 19-55 | -54.9209 | 19.342 | 464.1264 | 161.3459 | 188.9374 | 227.6569 | 262.1374 | 301.8417 | 2.932%
5758 | 19-55 | -55.1922 | 19.342 | 449.7209 | 161.9593 | 189.3471 | 228.2635 | 262.9344 | 302.8731 | 2.974%
5759 | 19-55.5 | -55.4635 | 19.342 | 435.5732 | 162.5156 | 189.7248 | 228.8192 | 263.6622 | 303.8124 | 3.014%
5760 | 19-55.5 | -55.7348 | 19.342 | 421.7093 | 163.0944 | 190.1348 | 229.4209 | 264.4493 | 304.8276 | 3.056%
5761 | 19-56 | -56.0061 | 19.342 | 408.1581 | 163.6892 | 190.5814 | 230.0739 | 265.3016 | 305.9251 | 3.099%
5762 | 19-56.5 | -56.2775 | 19.342 | 394.9518 | 164.2481 | 191.0164 | 230.7023 | 266.1165 | 306.9691 | 3.141%
5763 | 19-56.5 | -56.5488 | 19.342 | 382.1263 | 164.8323 | 191.4918 | 231.3842 | 266.9973 | 308.0939 | 3.186%
5764 | 19-57 | -56.8201 | 19.342 | 369.7212 | 165.4248 | 192.0022 | 232.1108 | 267.9319 | 309.2835 | 3.232%
5765 | 19-57 | -57.0914 | 19.342 | 357.7801 | 165.9686 | 192.4874 | 232.7923 | 268.8015 | 310.3832 | 3.275%
5766 | 19-57.5 | -57.3628 | 19.342 | 346.3513 | 166.5403 | 193.0142 | 233.5301 | 269.7413 | 311.5699 | 3.322%
5767 | 19-57.5 | -57.6341 | 19.342 | 335.487 | 167.1194 | 193.5716 | 234.3077 | 270.7296 | 312.8155 | 3.369%
5768 | 19-58 | -57.9054 | 19.342 | 325.2438 | 167.6513 | 194.1022 | 235.0398 | 271.654 | 313.9741 | 3.414%
5769 | 19-58 | -58.1767 | 19.342 | 315.6823 | 168.1867 | 194.6484 | 235.7827 | 272.5837 | 315.1307 | 3.46%
5770 | 19-58.5 | -58.448 | 19.342 | 306.8662 | 168.6996 | 195.1928 | 236.5093 | 273.4822 | 316.237 | 3.506%
5771 | 19-58.5 | -58.7194 | 19.342 | 298.8614 | 169.147 | 195.686 | 237.1461 | 274.2528 | 317.1676 | 3.548%
5772 | 19-59 | -58.9907 | 19.342 | 291.7348 | 169.5929 | 196.1866 | 237.7863 | 275.0224 | 318.0912 | 3.59%
5773 | 19-59.5 | -59.262 | 19.342 | 285.5521 | 170.0226 | 196.6776 | 238.4054 | 275.7595 | 318.9679 | 3.632%
5774 | 19-59.5 | -59.5333 | 19.342 | 280.3759 | 170.4132 | 197.1252 | 238.9577 | 276.4066 | 319.726 | 3.672%
5775 | 19-60 | -59.8046 | 19.342 | 276.2627 | 170.8103 | 197.586 | 239.529 | 277.0786 | 320.5162 | 3.712%
5776 | 19-60 | -60.076 | 19.342 | 273.2604 | 171.196 | 198.0357 | 240.0814 | 277.7239 | 321.2701 | 3.751%
5777 | 19-60.5 | -60.3473 | 19.342 | 271.4061 | 171.5547 | 198.4448 | 240.568 | 278.2787 | 321.9025 | 3.79%
5778 | 19-60.5 | -60.6186 | 19.342 | 270.7233 | 171.9356 | 198.8815 | 241.0913 | 278.8787 | 322.5904 | 3.83%
5779 | 19-61 | -60.8899 | 19.342 | 271.2208 | 172.3154 | 199.3126 | 241.6009 | 279.457 | 323.2466 | 3.871%
5780 | 19-61 | -61.1613 | 19.342 | 272.8922 | 172.6763 | 199.712 | 242.0562 | 279.9587 | 323.7983 | 3.912%
5781 | 19-61.5 | -61.4326 | 19.342 | 275.7162 | 173.0634 | 200.1431 | 242.5527 | 280.5104 | 324.4107 | 3.955%
5782 | 19-61.5 | -61.7039 | 19.342 | 279.6577 | 173.4448 | 200.565 | 243.0334 | 281.0399 | 324.9926 | 3.999%
5783 | 19-62 | -61.9752 | 19.342 | 284.6704 | 173.8044 | 200.9575 | 243.472 | 281.515 | 325.5053 | 4.04%
5784 | 19-62 | -62.2465 | 19.342 | 290.6989 | 174.1826 | 201.3792 | 243.9581 | 282.0556 | 326.1055 | 4.084%
5785 | 19-62.5 | -62.5179 | 19.342 | 297.6815 | 174.5815 | 201.8344 | 244.5001 | 282.6738 | 326.8106 | 4.13%
5786 | 19-63 | -62.7892 | 19.342 | 305.5527 | 175.0226 | 202.3517 | 245.1385 | 283.4221 | 327.6877 | 4.179%
5787 | 19-63 | -63.0605 | 19.342 | 314.2457 | 175.5412 | 202.978 | 245.9398 | 284.3861 | 328.8455 | 4.236%
5788 | 19-63.5 | -63.3318 | 19.342 | 323.6944 | 176.0228 | 203.5628 | 246.6934 | 285.2968 | 329.944 | 4.288%
5789 | 19-63.5 | -63.6031 | 19.342 | 333.8345 | 176.4066 | 204.0304 | 247.2981 | 286.0292 | 330.8292 | 4.33%
5790 | 19-64 | -63.8745 | 19.342 | 344.6051 | 176.7239 | 204.4275 | 247.8276 | 286.6836 | 331.6346 | 4.364%
5791 | 19-64 | -64.1458 | 19.342 | 355.9488 | 176.9827 | 204.761 | 248.2865 | 287.2621 | 332.3588 | 4.391%
5792 | 19-64.5 | -64.4171 | 19.342 | 367.8126 | 177.2084 | 205.066 | 248.7265 | 287.8325 | 333.0897 | 4.412%
5793 | 19-64.5 | -64.6884 | 19.342 | 380.1478 | 177.4286 | 205.3836 | 249.2121 | 288.4823 | 333.9434 | 4.431%
5794 | 19-65 | -64.9598 | 19.342 | 392.91 | 177.5954 | 205.6425 | 249.6316 | 289.0602 | 334.7189 | 4.443%
5795 | 19-65 | -65.2311 | 19.342 | 406.0589 | 177.7161 | 205.8495 | 249.9907 | 289.5702 | 335.4185 | 4.449%
5796 | 19-65.5 | -65.5024 | 19.342 | 419.5581 | 177.8196 | 206.0435 | 250.3451 | 290.0848 | 336.1348 | 4.453%
5797 | 19-66 | -65.7737 | 19.342 | 433.3749 | 177.8674 | 206.1698 | 250.6125 | 290.4941 | 336.7244 | 4.45%
5798 | 19-66 | -66.045 | 19.342 | 447.4797 | 177.8407 | 206.2036 | 250.7574 | 290.753 | 337.1296 | 4.44%
5799 | 19-66.5 | -66.3164 | 19.342 | 461.8463 | 177.7329 | 206.1376 | 250.7719 | 290.853 | 337.3421 | 4.42%
5800 | 19-66.5 | -66.5877 | 19.342 | 476.4509 | 177.4276 | 205.8142 | 250.428 | 290.4977 | 336.9804 | 4.381%
5801 | 19-67 | -66.859 | 19.342 | 491.2722 | 177 | 205.3408 | 249.876 | 289.8786 | 336.2872 | 4.331%
5802 | 19-67 | -67.1303 | 19.342 | 506.2911 | 176.4779 | 204.8207 | 249.2631 | 289.1856 | 335.5049 | 4.272%
5803 | 19-67.5 | -67.4016 | 19.342 | 521.4907 | 175.9276 | 204.2828 | 248.6197 | 288.4497 | 334.6639 | 4.211%
5804 | 19-67.5 | -67.673 | 19.342 | 536.8554 | 175.3546 | 203.7219 | 247.9427 | 287.6697 | 333.7659 | 4.149%
5805 | 19-68 | -67.9443 | 19.342 | 552.3716 | 174.7566 | 203.1342 | 247.231 | 286.8475 | 332.8165 | 4.085%
5806 | 19-68 | -68.2156 | 19.342 | 568.0267 | 173.9733 | 202.3349 | 246.2134 | 285.6281 | 331.3571 | 4.006%
5807 | 19-68.5 | -68.4869 | 19.342 | 583.8095 | 172.9977 | 201.3742 | 244.9735 | 284.1281 | 329.546 | 3.911%
5808 | 19-69 | -68.7583 | 19.342 | 599.71 | 171.837 | 200.2864 | 243.5686 | 282.4277 | 327.4923 | 3.8%
5809 | 19-69 | -69.0296 | 19.342 | 615.7189 | 170.5599 | 199.0969 | 242.0169 | 280.5369 | 325.1944 | 3.683%
5810 | 19-69.5 | -69.3009 | 19.342 | 631.828 | 169.2131 | 197.859 | 240.4003 | 278.5657 | 322.797 | 3.563%
5811 | 19-69.5 | -69.5722 | 19.342 | 648.0299 | 167.8143 | 196.5898 | 238.747 | 276.5529 | 320.3528 | 3.441%
5812 | 19-70 | -69.8435 | 19.342 | 664.3176 | 166.2799 | 195.2058 | 236.927 | 274.3231 | 317.6294 | 3.312%
5813 | 19-70 | -70.1149 | 19.342 | 680.6851 | 164.7327 | 193.8618 | 235.1672 | 272.1734 | 315.0108 | 3.186%
5814 | 19-70.5 | -70.3862 | 19.342 | 697.1265 | 163.2371 | 192.6113 | 233.5458 | 270.2057 | 312.6283 | 3.068%
5815 | 19-70.5 | -70.6575 | 19.342 | 713.6369 | 162.2181 | 191.7093 | 232.3923 | 268.8182 | 310.9611 | 2.988%
5816 | 19-71 | -70.9288 | 19.342 | 730.2115 | 161.6379 | 191.132 | 231.6878 | 267.9985 | 310.0068 | 2.941%
5817 | 19-71 | -71.2001 | 19.342 | 746.8459 | 161.4452 | 190.8431 | 231.3842 | 267.6879 | 309.6942 | 2.922%
5818 | 19-71.5 | -71.4715 | 19.342 | 763.5363 | 161.2243 | 190.518 | 231.0089 | 267.2701 | 309.2297 | 2.902%
5819 | 19-71.5 | -71.7428 | 19.342 | 780.279 | 161.1384 | 190.3454 | 230.8418 | 267.1136 | 309.0914 | 2.892%
5820 | 19-72 | -72.0141 | 19.342 | 797.0706 | 161.1947 | 190.2995 | 230.8446 | 267.1683 | 309.2141 | 2.892%
5821 | 19-72.5 | -72.2854 | 19.342 | 813.9082 | 161.071 | 190.1234 | 230.6371 | 266.9333 | 308.9482 | 2.881%
5822 | 19-72.5 | -72.5568 | 19.342 | 830.7889 | 160.7124 | 189.7971 | 230.2139 | 266.4199 | 308.3269 | 2.855%
5823 | 19-73 | -72.8281 | 19.342 | 847.7101 | 160.2829 | 189.4289 | 229.7219 | 265.8116 | 307.5784 | 2.824%
5824 | 19-73 | -73.0994 | 19.342 | 864.6694 | 160.3815 | 189.428 | 229.7044 | 265.7775 | 307.5237 | 2.83%
5825 | 19-73.5 | -73.3707 | 19.342 | 881.6644 | 161.0098 | 189.8824 | 230.3027 | 266.5121 | 308.4235 | 2.874%
5826 | 19-73.5 | -73.642 | 19.342 | 898.6933 | 161.9499 | 190.5974 | 231.2458 | 267.6709 | 309.8435 | 2.942%
5827 | 19-74 | -73.9134 | 19.342 | 915.7541 | 162.6216 | 190.9926 | 231.7191 | 268.2134 | 310.4656 | 2.992%
5828 | 19-74 | -74.1847 | 19.342 | 932.8449 | 162.493 | 190.8253 | 231.4152 | 267.7741 | 309.8564 | 2.984%
5829 | 19-74.5 | -74.456 | 19.342 | 949.9641 | 161.7108 | 190.1947 | 230.4675 | 266.5184 | 308.2205 | 2.93%
5830 | 19-74.5 | -74.7273 | 19.342 | 967.1102 | 160.6252 | 189.3463 | 229.203 | 264.8497 | 306.0522 | 2.856%
5831 | 19-75 | -74.9986 | 19.342 | 984.2817 | 159.6681 | 188.6072 | 228.0989 | 263.3906 | 304.1544 | 2.792%
5832 | 19-75.5 | -75.27 | 19.342 | 1001.4774 | 158.9402 | 188.0318 | 227.2177 | 262.2107 | 302.6036 | 2.745%
5833 | 19-75.5 | -75.5413 | 19.342 | 1018.6959 | 158.6732 | 187.7693 | 226.7514 | 261.5414 | 301.6791 | 2.729%
5834 | 19-76 | -75.8126 | 19.342 | 1035.936 | 159.1373 | 188.0836 | 227.0916 | 261.8994 | 302.0522 | 2.763%
5835 | 19-76 | -76.0839 | 19.342 | 1053.1967 | 160.1353 | 188.8043 | 227.9896 | 262.9594 | 303.3029 | 2.836%
5836 | 19-76.5 | -76.3553 | 19.342 | 1070.477 | 161.2723 | 189.5811 | 228.9476 | 264.0813 | 304.6159 | 2.92%
5837 | 19-76.5 | -76.6266 | 19.342 | 1087.7758 | 161.9387 | 190.0126 | 229.4328 | 264.6087 | 305.1863 | 2.972%
5838 | 19-77 | -76.8979 | 19.342 | 1105.0923 | 162.2318 | 190.1122 | 229.4548 | 264.5469 | 305.0128 | 2.997%
5839 | 19-77 | -77.1692 | 19.342 | 1122.4256 | 162.3761 | 190.0933 | 229.3054 | 264.2621 | 304.5527 | 3.011%
5840 | 19-77.5 | -77.4405 | 19.342 | 1139.7749 | 162.9272 | 190.5279 | 229.7878 | 264.7807 | 305.1065 | 3.058%
5841 | 19-77.5 | -77.7119 | 19.342 | 1157.1394 | 164.017 | 191.3656 | 230.8173 | 265.9835 | 306.5113 | 3.147%
5842 | 19-78 | -77.9832 | 19.342 | 1174.5185 | 165.4452 | 192.4653 | 232.1926 | 267.6107 | 308.435 | 3.267%
5843 | 19-78.5 | -78.2545 | 19.342 | 1191.9115 | 166.8994 | 193.6185 | 233.6399 | 269.3275 | 310.4696 | 3.393%
5844 | 19-78.5 | -78.5258 | 19.342 | 1209.3177 | 168.3348 | 194.7842 | 235.0942 | 271.0452 | 312.4972 | 3.523%
5845 | 19-79 | -78.7971 | 19.342 | 1226.7365 | 169.6293 | 195.8785 | 236.446 | 272.6306 | 314.356 | 3.646%
5846 | 19-79 | -79.0685 | 19.342 | 1244.1674 | 170.6015 | 196.8041 | 237.579 | 273.9508 | 315.8938 | 3.743%
5847 | 19-79.5 | -79.3398 | 19.342 | 1261.6099 | 171.282 | 197.4946 | 238.381 | 274.8474 | 316.8945 | 3.816%
5848 | 19-79.5 | -79.6111 | 19.342 | 1279.0634 | 171.8328 | 198.0828 | 239.0365 | 275.5546 | 317.6531 | 3.879%
5849 | 19-80 | -79.8824 | 19.342 | 1296.5274 | 172.4774 | 198.8154 | 239.9046 | 276.5411 | 318.7735 | 3.952%
5850 | 19-80 | -80.1537 | 19.342 | 1314.0015 | 173.1755 | 199.6202 | 240.8759 | 277.6607 | 320.064 | 4.03%
5851 | 19-80.5 | -80.4251 | 19.342 | 1331.4852 | 173.8904 | 200.4485 | 241.8822 | 278.8266 | 321.4148 | 4.112%
5852 | 19-80.5 | -80.6964 | 19.342 | 1348.9782 | 174.6084 | 201.2854 | 242.9068 | 280.0207 | 322.8061 | 4.194%
5853 | 19-81 | -80.9677 | 19.342 | 1366.4801 | 175.2856 | 202.0721 | 243.8657 | 281.1345 | 324.0998 | 4.273%
5854 | 19-81 | -81.239 | 19.342 | 1383.9904 | 175.9327 | 202.8272 | 244.7917 | 282.2149 | 325.3603 | 4.35%
5855 | 19-81.5 | -81.5104 | 19.342 | 1401.5089 | 176.5764 | 203.5888 | 245.7419 | 283.3374 | 326.6858 | 4.425%
5856 | 19-82 | -81.7817 | 19.342 | 1419.0351 | 177.1575 | 204.2759 | 246.599 | 284.3498 | 327.881 | 4.495%
5857 | 19-82 | -82.053 | 19.342 | 1436.5689 | 177.6874 | 204.9082 | 247.3961 | 285.2986 | 329.0092 | 4.558%
5858 | 19-82.5 | -82.3243 | 19.342 | 1454.1097 | 178.1883 | 205.5169 | 248.1808 | 286.247 | 330.1532 | 4.616%
5859 | 19-82.5 | -82.5956 | 19.342 | 1471.6575 | 178.5881 | 206.0021 | 248.8054 | 287.0011 | 331.0619 | 4.664%
5860 | 19-83 | -82.867 | 19.342 | 1489.2118 | 178.9093 | 206.4046 | 249.3427 | 287.6657 | 331.8803 | 4.7%
5861 | 19-83 | -83.1383 | 19.342 | 1506.7724 | 179.1759 | 206.7626 | 249.8555 | 288.3278 | 332.7256 | 4.727%
5862 | 19-83.5 | -83.4096 | 19.342 | 1524.3392 | 179.3219 | 206.98 | 250.1967 | 288.79 | 333.3382 | 4.739%
5863 | 19-83.5 | -83.6809 | 19.342 | 1541.9117 | 179.3872 | 207.1127 | 250.4487 | 289.1609 | 333.8586 | 4.74%
5864 | 19-84 | -83.9522 | 19.342 | 1559.4898 | 179.396 | 207.1943 | 250.6616 | 289.5065 | 334.373 | 4.731%
5865 | 19-84 | -84.2236 | 19.342 | 1577.0733 | 179.2652 | 207.114 | 250.6778 | 289.6241 | 334.623 | 4.705%
5866 | 19-84.5 | -84.4949 | 19.342 | 1594.6619 | 179.0287 | 206.917 | 250.5612 | 289.5959 | 334.7134 | 4.665%
5867 | 19-85 | -84.7662 | 19.342 | 1612.2555 | 178.6995 | 206.6224 | 250.3421 | 289.4629 | 334.6987 | 4.613%
5868 | 19-85 | -85.0375 | 19.342 | 1629.8538 | 178.1525 | 206.0769 | 249.8202 | 288.9814 | 334.2831 | 4.535%
5869 | 19-85.5 | -85.3089 | 19.342 | 1647.4566 | 177.4341 | 205.3512 | 249.0985 | 288.2852 | 333.6385 | 4.437%
5870 | 19-85.5 | -85.5802 | 19.342 | 1665.0639 | 176.4965 | 204.4532 | 248.1889 | 287.3907 | 332.787 | 4.316%
5871 | 19-86 | -85.8515 | 19.342 | 1682.6753 | 174.9809 | 203.0251 | 246.5606 | 285.5974 | 330.8175 | 4.142%
5872 | 19-86 | -86.1228 | 19.342 | 1700.2908 | 172.7947 | 201.1659 | 244.3631 | 283.1051 | 327.992 | 3.914%
5873 | 19-86.5 | -86.3941 | 19.342 | 1717.9101 | 170.0154 | 198.909 | 241.6477 | 279.9821 | 324.4007 | 3.646%
5874 | 19-86.5 | -86.6655 | 19.342 | 1735.5331 | 166.8675 | 196.3836 | 238.5649 | 276.3976 | 320.2331 | 3.366%
5875 | 19-87 | -86.9368 | 19.342 | 1753.1597 | 163.4343 | 193.6769 | 235.2511 | 272.5358 | 315.7328 | 3.085%
5876 | 19-87 | -87.2081 | 19.342 | 1770.7897 | 159.7409 | 190.7379 | 231.7173 | 268.4141 | 310.9258 | 2.806%
5877 | 19-87.5 | -87.4794 | 19.342 | 1788.423 | 155.7961 | 187.5094 | 227.9286 | 263.9757 | 305.7273 | 2.533%
5878 | 19-88 | -87.7507 | 19.342 | 1806.0594 | 151.6925 | 184.0859 | 224.0287 | 259.4064 | 300.3747 | 2.274%
5879 | 19-88 | -88.0221 | 19.342 | 1823.6989 | 147.4718 | 180.4971 | 220.0433 | 254.7381 | 294.9077 | 2.034%
5880 | 19-88.5 | -88.2934 | 19.342 | 1841.3412 | 143.244 | 176.8431 | 216.0451 | 250.042 | 289.3931 | 1.817%
5881 | 19-88.5 | -88.5647 | 19.342 | 1858.9863 | 139.1392 | 173.2811 | 212.2232 | 245.5482 | 284.1107 | 1.629%
5882 | 19-89 | -88.836 | 19.342 | 1876.634 | 135.1888 | 169.8533 | 208.5892 | 241.266 | 279.0661 | 1.467%
5883 | 19-89 | -89.1074 | 19.342 | 1894.2843 | 131.5029 | 166.6739 | 205.1934 | 237.245 | 274.3067 | 1.331%
5884 | 19-89.5 | -89.3787 | 19.342 | 1911.937 | 128.4458 | 164.0843 | 202.5608 | 234.1845 | 270.7491 | 1.229%
5885 | 19-89.5 | -89.65 | 19.342 | 1929.592 | 126.1391 | 162.0109 | 200.6089 | 231.9676 | 268.2329 | 1.157%
5886 | 19-90 | -89.9213 | 19.342 | 1947.2492 | 124.4097 | 160.3472 | 199.1488 | 230.3339 | 266.4073 | 1.106%
5887 | 19-90 | -90.1926 | 19.342 | 1964.9086 | 123.0398 | 158.9612 | 198.0249 | 229.1142 | 265.0897 | 1.066%
5888 | 19-90.5 | -90.464 | 19.342 | 1982.57 | 121.9804 | 157.8043 | 197.1906 | 228.2478 | 264.2021 | 1.037%
5889 | 19-90.5 | -90.7353 | 19.342 | 2000.2333 | 121.1444 | 156.8342 | 196.5496 | 227.6057 | 263.5748 | 1.014%
5890 | 20-50 | -50.0371 | 19.6134 | 755.9332 | 144.503 | 178.2852 | 212.6005 | 242.8603 | 277.4282 | 1.914%
5891 | 20-50.5 | -50.3084 | 19.6134 | 739.4615 | 145.6801 | 179.0288 | 213.591 | 244.0997 | 278.9676 | 1.975%
5892 | 20-50.5 | -50.5797 | 19.6134 | 723.0557 | 146.7896 | 179.7209 | 214.5341 | 245.2844 | 280.4436 | 2.033%
5893 | 20-51 | -50.851 | 19.6134 | 706.7203 | 147.8663 | 180.3918 | 215.4631 | 246.4575 | 281.9121 | 2.091%
5894 | 20-51 | -51.1224 | 19.6134 | 690.4604 | 148.9544 | 181.0765 | 216.4232 | 247.6791 | 283.4509 | 2.151%
5895 | 20-51.5 | -51.3937 | 19.6134 | 674.2815 | 149.9778 | 181.72 | 217.3245 | 248.8252 | 284.894 | 2.209%
5896 | 20-51.5 | -51.665 | 19.6134 | 658.1897 | 150.9809 | 182.353 | 218.2152 | 249.9612 | 286.3278 | 2.266%
5897 | 20-52 | -51.9363 | 19.6134 | 642.1914 | 152.0064 | 183.005 | 219.1414 | 251.1487 | 287.8333 | 2.327%
5898 | 20-52 | -52.2077 | 19.6134 | 626.2939 | 152.971 | 183.6184 | 220.0127 | 252.266 | 289.2499 | 2.384%
5899 | 20-52.5 | -52.479 | 19.6134 | 610.5051 | 153.9178 | 184.223 | 220.8781 | 253.3804 | 290.6678 | 2.442%
5900 | 20-53 | -52.7503 | 19.6134 | 594.8338 | 154.8753 | 184.8396 | 221.7711 | 254.5382 | 292.149 | 2.501%
5901 | 20-53 | -53.0216 | 19.6134 | 579.2893 | 155.774 | 185.4193 | 222.6137 | 255.6329 | 293.5516 | 2.558%
5902 | 20-53.5 | -53.2929 | 19.6134 | 563.8824 | 156.6653 | 185.9923 | 223.4424 | 256.7065 | 294.9245 | 2.615%
5903 | 20-53.5 | -53.5643 | 19.6134 | 548.6245 | 157.5682 | 186.5703 | 224.272 | 257.777 | 296.2891 | 2.674%
5904 | 20-54 | -53.8356 | 19.6134 | 533.5286 | 158.3913 | 187.0896 | 225.0053 | 258.7146 | 297.4755 | 2.729%
5905 | 20-54 | -54.1069 | 19.6134 | 518.6088 | 159.1817 | 187.5848 | 225.7005 | 259.6006 | 298.5938 | 2.783%
5906 | 20-54.5 | -54.3782 | 19.6134 | 503.8807 | 159.9515 | 188.0648 | 226.3718 | 260.4543 | 299.6694 | 2.836%
5907 | 20-54.5 | -54.6495 | 19.6134 | 489.3618 | 160.6314 | 188.4871 | 226.9605 | 261.2016 | 300.6098 | 2.883%
5908 | 20-55 | -54.9209 | 19.6134 | 475.0712 | 161.3039 | 188.9114 | 227.5608 | 261.9704 | 301.5843 | 2.931%
5909 | 20-55 | -55.1922 | 19.6134 | 461.0302 | 161.9806 | 189.3489 | 228.1885 | 262.7809 | 302.6187 | 2.979%
5910 | 20-55.5 | -55.4635 | 19.6134 | 447.2623 | 162.5938 | 189.7508 | 228.7616 | 263.5184 | 303.5574 | 3.023%
5911 | 20-55.5 | -55.7348 | 19.6134 | 433.7936 | 163.2197 | 190.1797 | 229.3743 | 264.3075 | 304.5627 | 3.069%
5912 | 20-56 | -56.0061 | 19.6134 | 420.6528 | 163.8499 | 190.6398 | 230.0306 | 265.1523 | 305.6384 | 3.116%
5913 | 20-56.5 | -56.2775 | 19.6134 | 407.8716 | 164.435 | 191.0834 | 230.6551 | 265.9502 | 306.6482 | 3.161%
5914 | 20-56.5 | -56.5488 | 19.6134 | 395.485 | 165.0366 | 191.5642 | 231.3302 | 266.8115 | 307.737 | 3.208%
5915 | 20-57 | -56.8201 | 19.6134 | 383.5312 | 165.6398 | 192.0777 | 232.0488 | 267.7264 | 308.8918 | 3.256%
5916 | 20-57 | -57.0914 | 19.6134 | 372.052 | 166.1888 | 192.5665 | 232.7263 | 268.584 | 309.9689 | 3.3%
5917 | 20-57.5 | -57.3628 | 19.6134 | 361.0925 | 166.763 | 193.0981 | 233.4642 | 269.519 | 311.1442 | 3.348%
5918 | 20-57.5 | -57.6341 | 19.6134 | 350.7017 | 167.3407 | 193.6605 | 234.245 | 270.5083 | 312.3878 | 3.396%
5919 | 20-58 | -57.9054 | 19.6134 | 340.9315 | 167.8652 | 194.1944 | 234.9812 | 271.4376 | 313.5522 | 3.441%
5920 | 20-58 | -58.1767 | 19.6134 | 331.8368 | 168.3951 | 194.7464 | 235.7346 | 272.3823 | 314.7295 | 3.487%
5921 | 20-58.5 | -58.448 | 19.6134 | 323.4745 | 168.9038 | 195.2989 | 236.4772 | 273.3048 | 315.8698 | 3.533%
5922 | 20-58.5 | -58.7194 | 19.6134 | 315.9028 | 169.3474 | 195.8009 | 237.1332 | 274.105 | 316.843 | 3.575%
5923 | 20-59 | -58.9907 | 19.6134 | 309.1799 | 169.7865 | 196.3089 | 237.7927 | 274.9059 | 317.8133 | 3.616%
5924 | 20-59.5 | -59.262 | 19.6134 | 303.3622 | 170.2088 | 196.8064 | 238.4325 | 275.6779 | 318.7433 | 3.658%
5925 | 20-59.5 | -59.5333 | 19.6134 | 298.5027 | 170.5932 | 197.2606 | 239.0087 | 276.3668 | 319.5659 | 3.696%
5926 | 20-60 | -59.8046 | 19.6134 | 294.6487 | 170.9828 | 197.7273 | 239.6069 | 277.0872 | 320.432 | 3.734%
5927 | 20-60 | -60.076 | 19.6134 | 291.8401 | 171.3605 | 198.1819 | 240.1882 | 277.7859 | 321.2705 | 3.772%
5928 | 20-60.5 | -60.3473 | 19.6134 | 290.1073 | 171.709 | 198.5945 | 240.7034 | 278.3951 | 321.9904 | 3.808%
5929 | 20-60.5 | -60.6186 | 19.6134 | 289.4696 | 172.0767 | 199.0309 | 241.2501 | 279.043 | 322.7578 | 3.846%
5930 | 20-61 | -60.8899 | 19.6134 | 289.9342 | 172.4401 | 199.458 | 241.7789 | 279.6643 | 323.4877 | 3.884%
5931 | 20-61 | -61.1613 | 19.6134 | 291.4959 | 172.7827 | 199.8512 | 242.2506 | 280.2057 | 324.1093 | 3.922%
5932 | 20-61.5 | -61.4326 | 19.6134 | 294.1371 | 173.1522 | 200.2767 | 242.7636 | 280.7968 | 324.7904 | 3.962%
5933 | 20-61.5 | -61.7039 | 19.6134 | 297.8293 | 173.5162 | 200.6916 | 243.2569 | 281.3592 | 325.4317 | 4.002%
5934 | 20-62 | -61.9752 | 19.6134 | 302.5338 | 173.8579 | 201.0745 | 243.7015 | 281.8564 | 325.9873 | 4.041%
5935 | 20-62 | -62.2465 | 19.6134 | 308.2043 | 174.2191 | 201.4859 | 244.1899 | 282.4125 | 326.6204 | 4.082%
5936 | 20-62.5 | -62.5179 | 19.6134 | 314.7886 | 174.5823 | 201.9045 | 244.6951 | 282.9948 | 327.2917 | 4.123%
5937 | 20-63 | -62.7892 | 19.6134 | 322.2307 | 174.951 | 202.3357 | 245.2252 | 283.6144 | 328.0158 | 4.164%
5938 | 20-63 | -63.0605 | 19.6134 | 330.4726 | 175.3599 | 202.8249 | 245.8441 | 284.3531 | 328.8963 | 4.209%
5939 | 20-63.5 | -63.3318 | 19.6134 | 339.456 | 175.7398 | 203.2805 | 246.4224 | 285.0446 | 329.7223 | 4.251%
5940 | 20-63.5 | -63.6031 | 19.6134 | 349.1238 | 176.0614 | 203.6678 | 246.9162 | 285.637 | 330.4319 | 4.286%
5941 | 20-64 | -63.8745 | 19.6134 | 359.4206 | 176.3551 | 204.0328 | 247.3991 | 286.2308 | 331.1595 | 4.318%
5942 | 20-64 | -64.1458 | 19.6134 | 370.2939 | 176.6068 | 204.3545 | 247.8381 | 286.7814 | 331.846 | 4.343%
5943 | 20-64.5 | -64.4171 | 19.6134 | 381.6946 | 176.8301 | 204.6532 | 248.2648 | 287.3317 | 332.5481 | 4.365%
5944 | 20-64.5 | -64.6884 | 19.6134 | 393.5767 | 177.0527 | 204.9699 | 248.7437 | 287.969 | 333.3818 | 4.384%
5945 | 20-65 | -64.9598 | 19.6134 | 405.8979 | 177.2252 | 205.2313 | 249.1601 | 288.5377 | 334.1406 | 4.397%
5946 | 20-65 | -65.2311 | 19.6134 | 418.6194 | 177.3554 | 205.4457 | 249.5225 | 289.0469 | 334.8337 | 4.405%
5947 | 20-65.5 | -65.5024 | 19.6134 | 431.7059 | 177.4731 | 205.6541 | 249.8911 | 289.5751 | 335.5628 | 4.411%
5948 | 20-66 | -65.7737 | 19.6134 | 445.125 | 177.5379 | 205.799 | 250.1792 | 290.0069 | 336.1767 | 4.41%
5949 | 20-66 | -66.045 | 19.6134 | 458.8477 | 177.5506 | 205.8804 | 250.3853 | 290.3397 | 336.6711 | 4.404%
5950 | 20-66.5 | -66.3164 | 19.6134 | 472.8474 | 177.5223 | 205.9141 | 250.5331 | 290.6047 | 337.0871 | 4.394%
5951 | 20-66.5 | -66.5877 | 19.6134 | 487.1003 | 177.3369 | 205.7434 | 250.3967 | 290.5092 | 337.049 | 4.367%
5952 | 20-67 | -66.859 | 19.6134 | 501.5846 | 177.0248 | 205.4176 | 250.0463 | 290.1433 | 336.672 | 4.328%
5953 | 20-67 | -67.1303 | 19.6134 | 516.281 | 176.5823 | 204.9994 | 249.5729 | 289.6259 | 336.1092 | 4.277%
5954 | 20-67.5 | -67.4016 | 19.6134 | 531.1718 | 176.0752 | 204.5168 | 249.0052 | 288.9852 | 335.3871 | 4.221%
5955 | 20-67.5 | -67.673 | 19.6134 | 546.241 | 175.5311 | 203.9923 | 248.3769 | 288.2655 | 334.5636 | 4.162%
5956 | 20-68 | -67.9443 | 19.6134 | 561.4743 | 174.9601 | 203.4372 | 247.707 | 287.4939 | 333.6753 | 4.101%
5957 | 20-68 | -68.2156 | 19.6134 | 576.8586 | 174.2003 | 202.6646 | 246.7211 | 286.3105 | 332.2569 | 4.024%
5958 | 20-68.5 | -68.4869 | 19.6134 | 592.3821 | 173.2461 | 201.7263 | 245.5049 | 284.8348 | 330.4706 | 3.931%
5959 | 20-69 | -68.7583 | 19.6134 | 608.0342 | 172.1049 | 200.6573 | 244.1167 | 283.1485 | 328.4271 | 3.823%
5960 | 20-69 | -69.0296 | 19.6134 | 623.8052 | 170.8446 | 199.4841 | 242.5798 | 281.2706 | 326.139 | 3.707%
5961 | 20-69.5 | -69.3009 | 19.6134 | 639.6861 | 169.5134 | 198.2626 | 240.9804 | 279.3168 | 323.7592 | 3.588%
5962 | 20-69.5 | -69.5722 | 19.6134 | 655.669 | 168.1293 | 197.0105 | 239.3481 | 277.3286 | 321.3436 | 3.467%
5963 | 20-70 | -69.8435 | 19.6134 | 671.7466 | 166.6065 | 195.6385 | 237.5402 | 275.1108 | 318.6318 | 3.339%
5964 | 20-70 | -70.1149 | 19.6134 | 687.9122 | 165.068 | 194.301 | 235.7828 | 272.959 | 316.0052 | 3.213%
5965 | 20-70.5 | -70.3862 | 19.6134 | 704.1598 | 163.5783 | 193.0521 | 234.1548 | 270.9761 | 313.5962 | 3.095%
5966 | 20-70.5 | -70.6575 | 19.6134 | 720.4836 | 162.5638 | 192.1514 | 232.9964 | 269.5773 | 311.9095 | 3.016%
5967 | 20-71 | -70.9288 | 19.6134 | 736.8787 | 161.9876 | 191.5771 | 232.293 | 268.7565 | 310.9511 | 2.969%
5968 | 20-71 | -71.2001 | 19.6134 | 753.3404 | 161.7992 | 191.2935 | 231.9974 | 268.4565 | 310.6525 | 2.95%
5969 | 20-71.5 | -71.4715 | 19.6134 | 769.8643 | 161.5836 | 190.9739 | 231.6338 | 268.0566 | 310.2136 | 2.93%
5970 | 20-71.5 | -71.7428 | 19.6134 | 786.4464 | 161.5042 | 190.8089 | 231.4854 | 267.9301 | 310.1193 | 2.92%
5971 | 20-72 | -72.0141 | 19.6134 | 803.0833 | 161.5678 | 190.7732 | 231.5146 | 268.0273 | 310.3052 | 2.921%
5972 | 20-72.5 | -72.2854 | 19.6134 | 819.7714 | 161.4554 | 190.6105 | 231.3409 | 267.8468 | 310.1198 | 2.91%
5973 | 20-72.5 | -72.5568 | 19.6134 | 836.5077 | 161.1118 | 190.2997 | 230.9543 | 267.3911 | 309.5828 | 2.884%
5974 | 20-73 | -72.8281 | 19.6134 | 853.2893 | 160.7002 | 189.9484 | 230.5 | 266.8409 | 308.9183 | 2.853%
5975 | 20-73 | -73.0994 | 19.6134 | 870.1136 | 160.8195 | 189.9639 | 230.517 | 266.8592 | 308.9383 | 2.861%
5976 | 20-73.5 | -73.3707 | 19.6134 | 886.9781 | 161.4723 | 190.4405 | 231.1606 | 267.662 | 309.9347 | 2.906%
5977 | 20-73.5 | -73.642 | 19.6134 | 903.8804 | 162.4343 | 191.1759 | 232.1491 | 268.8911 | 311.4565 | 2.976%
5978 | 20-74 | -73.9134 | 19.6134 | 920.8186 | 163.1059 | 191.5672 | 232.6354 | 269.4642 | 312.1317 | 3.025%
5979 | 20-74 | -74.1847 | 19.6134 | 937.7906 | 162.9375 | 191.3672 | 232.3015 | 268.9984 | 311.5012 | 3.014%
5980 | 20-74.5 | -74.456 | 19.6134 | 954.7946 | 162.087 | 190.6818 | 231.2892 | 267.6694 | 309.782 | 2.954%
5981 | 20-74.5 | -74.7273 | 19.6134 | 971.8288 | 160.9273 | 189.7715 | 229.9459 | 265.9061 | 307.5003 | 2.875%
5982 | 20-75 | -74.9986 | 19.6134 | 988.8917 | 159.8897 | 188.9659 | 228.753 | 264.3371 | 305.467 | 2.805%
5983 | 20-75.5 | -75.27 | 19.6134 | 1005.9818 | 159.0908 | 188.3294 | 227.7871 | 263.0498 | 303.7812 | 2.753%
5984 | 20-75.5 | -75.5413 | 19.6134 | 1023.0977 | 158.7893 | 188.0284 | 227.2648 | 262.3078 | 302.7633 | 2.735%
5985 | 20-76 | -75.8126 | 19.6134 | 1040.238 | 159.2341 | 188.3269 | 227.579 | 262.6299 | 303.0883 | 2.768%
5986 | 20-76 | -76.0839 | 19.6134 | 1057.4016 | 160.2128 | 189.0333 | 228.4517 | 263.654 | 304.2899 | 2.839%
5987 | 20-76.5 | -76.3553 | 19.6134 | 1074.5873 | 161.3078 | 189.7672 | 229.344 | 264.688 | 305.4878 | 2.92%
5988 | 20-76.5 | -76.6266 | 19.6134 | 1091.7939 | 161.9037 | 190.13 | 229.7279 | 265.0826 | 305.8868 | 2.966%
5989 | 20-77 | -76.8979 | 19.6134 | 1109.0206 | 162.108 | 190.1459 | 229.6264 | 264.859 | 305.5043 | 2.984%
5990 | 20-77 | -77.1692 | 19.6134 | 1126.2664 | 162.1723 | 190.0485 | 229.358 | 264.4158 | 304.8373 | 2.992%
5991 | 20-77.5 | -77.4405 | 19.6134 | 1143.5303 | 162.6727 | 190.4321 | 229.7575 | 264.8203 | 305.2384 | 3.035%
5992 | 20-77.5 | -77.7119 | 19.6134 | 1160.8115 | 163.7634 | 191.2535 | 230.7514 | 265.9684 | 306.5643 | 3.124%
5993 | 20-78 | -77.9832 | 19.6134 | 1178.1092 | 165.2326 | 192.3716 | 232.1393 | 267.6017 | 308.4854 | 3.247%
5994 | 20-78.5 | -78.2545 | 19.6134 | 1195.4226 | 166.7452 | 193.5626 | 233.626 | 269.3584 | 310.5598 | 3.378%
5995 | 20-78.5 | -78.5258 | 19.6134 | 1212.7512 | 168.248 | 194.7752 | 235.1322 | 271.132 | 312.647 | 3.513%
5996 | 20-79 | -78.7971 | 19.6134 | 1230.094 | 169.5987 | 195.9087 | 236.5248 | 272.7589 | 314.5474 | 3.641%
5997 | 20-79 | -79.0685 | 19.6134 | 1247.4507 | 170.5894 | 196.8485 | 237.6636 | 274.0755 | 316.0694 | 3.741%
5998 | 20-79.5 | -79.3398 | 19.6134 | 1264.8204 | 171.267 | 197.5251 | 238.4317 | 274.9181 | 316.9904 | 3.815%
5999 | 20-79.5 | -79.6111 | 19.6134 | 1282.2028 | 171.809 | 198.0912 | 239.0414 | 275.5557 | 317.6491 | 3.878%
6000 | 20-80 | -79.8824 | 19.6134 | 1299.5971 | 172.4631 | 198.8246 | 239.8942 | 276.5102 | 318.716 | 3.952%
6001 | 20-80 | -80.1537 | 19.6134 | 1317.003 | 173.1975 | 199.656 | 240.8847 | 277.6406 | 320.0058 | 4.036%
6002 | 20-80.5 | -80.4251 | 19.6134 | 1334.4199 | 173.9681 | 200.5277 | 241.9337 | 278.8475 | 321.3942 | 4.124%
6003 | 20-80.5 | -80.6964 | 19.6134 | 1351.8473 | 174.7416 | 201.413 | 243.01 | 280.095 | 322.8403 | 4.213%
6004 | 20-81 | -80.9677 | 19.6134 | 1369.2849 | 175.4698 | 202.2491 | 244.0228 | 281.266 | 324.1941 | 4.299%
6005 | 20-81 | -81.239 | 19.6134 | 1386.7322 | 176.1572 | 203.0461 | 244.9919 | 282.3894 | 325.4965 | 4.382%
6006 | 20-81.5 | -81.5104 | 19.6134 | 1404.1888 | 176.8314 | 203.8358 | 245.9649 | 283.5286 | 326.8297 | 4.463%
6007 | 20-82 | -81.7817 | 19.6134 | 1421.6543 | 177.4312 | 204.5374 | 246.8275 | 284.5368 | 328.008 | 4.536%
6008 | 20-82 | -82.053 | 19.6134 | 1439.1283 | 177.976 | 205.1801 | 247.6266 | 285.4785 | 329.1172 | 4.602%
6009 | 20-82.5 | -82.3243 | 19.6134 | 1456.6106 | 178.4935 | 205.8026 | 248.4191 | 286.4281 | 330.2534 | 4.664%
6010 | 20-82.5 | -82.5956 | 19.6134 | 1474.1008 | 178.9125 | 206.3049 | 249.0562 | 287.1896 | 331.1625 | 4.715%
6011 | 20-83 | -82.867 | 19.6134 | 1491.5986 | 179.2576 | 206.7302 | 249.6133 | 287.8702 | 331.9915 | 4.755%
6012 | 20-83 | -83.1383 | 19.6134 | 1509.1036 | 179.5537 | 207.1174 | 250.1538 | 288.5574 | 332.8577 | 4.787%
6013 | 20-83.5 | -83.4096 | 19.6134 | 1526.6156 | 179.7341 | 207.3723 | 250.5369 | 289.065 | 333.519 | 4.804%
6014 | 20-83.5 | -83.6809 | 19.6134 | 1544.1343 | 179.8362 | 207.5482 | 250.8422 | 289.4982 | 334.1124 | 4.809%
6015 | 20-84 | -83.9522 | 19.6134 | 1561.6595 | 179.8829 | 207.6767 | 251.1166 | 289.9191 | 334.7186 | 4.804%
6016 | 20-84 | -84.2236 | 19.6134 | 1579.1909 | 179.7871 | 207.6399 | 251.1901 | 290.1071 | 335.0547 | 4.782%
6017 | 20-84.5 | -84.4949 | 19.6134 | 1596.7282 | 179.5854 | 207.4866 | 251.1322 | 290.1515 | 335.2347 | 4.745%
6018 | 20-85 | -84.7662 | 19.6134 | 1614.2712 | 179.2917 | 207.2375 | 250.9753 | 290.0968 | 335.3178 | 4.696%
6019 | 20-85 | -85.0375 | 19.6134 | 1631.8197 | 178.7602 | 206.7125 | 250.4828 | 289.653 | 334.95 | 4.618%
6020 | 20-85.5 | -85.3089 | 19.6134 | 1649.3735 | 178.0451 | 205.9828 | 249.7548 | 288.9482 | 334.294 | 4.518%
6021 | 20-85.5 | -85.5802 | 19.6134 | 1666.9324 | 177.0999 | 205.0574 | 248.8045 | 288.0001 | 333.3728 | 4.394%
6022 | 20-86 | -85.8515 | 19.6134 | 1684.4962 | 175.5816 | 203.6041 | 247.1384 | 286.1567 | 331.3378 | 4.217%
6023 | 20-86 | -86.1228 | 19.6134 | 1702.0647 | 173.3969 | 201.7218 | 244.907 | 283.6197 | 328.4542 | 3.985%
6024 | 20-86.5 | -86.3941 | 19.6134 | 1719.6376 | 170.6263 | 199.4466 | 242.1662 | 280.4644 | 324.8219 | 3.712%
6025 | 20-86.5 | -86.6655 | 19.6134 | 1737.2149 | 167.5296 | 196.9343 | 239.1055 | 276.9108 | 320.6961 | 3.43%
6026 | 20-87 | -86.9368 | 19.6134 | 1754.7964 | 164.1878 | 194.2694 | 235.853 | 273.1294 | 316.3 | 3.15%
6027 | 20-87 | -87.2081 | 19.6134 | 1772.3819 | 160.6196 | 191.4176 | 232.4127 | 269.1275 | 311.645 | 2.873%
6028 | 20-87.5 | -87.4794 | 19.6134 | 1789.9712 | 156.8102 | 188.3047 | 228.7246 | 264.817 | 306.6079 | 2.603%
6029 | 20-88 | -87.7507 | 19.6134 | 1807.5642 | 152.8549 | 185.0284 | 224.9429 | 260.3991 | 301.4472 | 2.346%
6030 | 20-88 | -88.0221 | 19.6134 | 1825.1608 | 148.7955 | 181.6136 | 221.0927 | 255.9037 | 296.1992 | 2.107%
6031 | 20-88.5 | -88.2934 | 19.6134 | 1842.7607 | 144.744 | 178.1489 | 217.2447 | 251.3986 | 290.9254 | 1.892%
6032 | 20-88.5 | -88.5647 | 19.6134 | 1860.364 | 140.8501 | 174.8156 | 213.6245 | 247.1611 | 285.966 | 1.706%
6033 | 20-89 | -88.836 | 19.6134 | 1877.9703 | 137.1341 | 171.6517 | 210.2384 | 243.194 | 281.3187 | 1.546%
6034 | 20-89 | -89.1074 | 19.6134 | 1895.5797 | 133.6881 | 168.7599 | 207.1156 | 239.5184 | 276.9933 | 1.412%
6035 | 20-89.5 | -89.3787 | 19.6134 | 1913.192 | 130.8608 | 166.4542 | 204.7442 | 236.7854 | 273.8438 | 1.312%
6036 | 20-89.5 | -89.65 | 19.6134 | 1930.8071 | 128.7749 | 164.6624 | 203.044 | 234.8819 | 271.7163 | 1.243%
6037 | 20-90 | -89.9213 | 19.6134 | 1948.4248 | 127.2563 | 163.2774 | 201.8235 | 233.5442 | 270.2551 | 1.195%
6038 | 20-90 | -90.1926 | 19.6134 | 1966.045 | 126.0513 | 162.1387 | 200.8887 | 232.5527 | 269.2126 | 1.158%
6039 | 20-90.5 | -90.464 | 19.6134 | 1983.6677 | 125.1123 | 161.1955 | 200.1927 | 231.8476 | 268.513 | 1.13%
6040 | 20-90.5 | -90.7353 | 19.6134 | 2001.2928 | 124.355 | 160.3838 | 199.6416 | 231.3049 | 267.9953 | 1.108%
6041 | 20-50 | -50.0371 | 19.8847 | 762.8022 | 142.7307 | 177.2526 | 211.3989 | 241.4691 | 275.8177 | 1.827%
6042 | 20-50.5 | -50.3084 | 19.8847 | 746.5083 | 143.9876 | 178.0694 | 212.4494 | 242.7777 | 277.4368 | 1.889%
6043 | 20-50.5 | -50.5797 | 19.8847 | 730.2868 | 145.178 | 178.8252 | 213.4547 | 244.0359 | 279 | 1.949%
6044 | 20-51 | -50.851 | 19.8847 | 714.1428 | 146.3372 | 179.5515 | 214.4484 | 245.2875 | 280.5632 | 2.009%
6045 | 20-51 | -51.1224 | 19.8847 | 698.0816 | 147.51 | 180.2874 | 215.4764 | 246.5926 | 282.2042 | 2.071%
6046 | 20-51.5 | -51.3937 | 19.8847 | 682.1092 | 148.6171 | 180.9809 | 216.444 | 247.8202 | 283.7471 | 2.132%
6047 | 20-51.5 | -51.665 | 19.8847 | 666.232 | 149.704 | 181.6633 | 217.4 | 249.0362 | 285.2785 | 2.192%
6048 | 20-52 | -51.9363 | 19.8847 | 650.4569 | 150.8146 | 182.3655 | 218.3913 | 250.3029 | 286.8799 | 2.256%
6049 | 20-52 | -52.2077 | 19.8847 | 634.7916 | 151.8667 | 183.0304 | 219.3283 | 251.4988 | 288.3905 | 2.317%
6050 | 20-52.5 | -52.479 | 19.8847 | 619.2446 | 152.9039 | 183.6881 | 220.2607 | 252.6931 | 289.9034 | 2.379%
6051 | 20-53 | -52.7503 | 19.8847 | 603.8248 | 153.955 | 184.3596 | 221.2229 | 253.9332 | 291.4824 | 2.442%
6052 | 20-53 | -53.0216 | 19.8847 | 588.5425 | 154.9488 | 184.9935 | 222.1307 | 255.1029 | 292.9713 | 2.504%
6053 | 20-53.5 | -53.2929 | 19.8847 | 573.4085 | 155.938 | 185.621 | 223.0226 | 256.2472 | 294.423 | 2.566%
6054 | 20-53.5 | -53.5643 | 19.8847 | 558.4351 | 156.9422 | 186.2544 | 223.9142 | 257.3848 | 295.8602 | 2.631%
6055 | 20-54 | -53.8356 | 19.8847 | 543.6355 | 157.8674 | 186.8289 | 224.7075 | 258.386 | 297.1134 | 2.693%
6056 | 20-54 | -54.1069 | 19.8847 | 529.0243 | 158.7604 | 187.3788 | 225.461 | 259.3324 | 298.2935 | 2.753%
6057 | 20-54.5 | -54.3782 | 19.8847 | 514.6176 | 159.6322 | 187.9123 | 226.188 | 260.2425 | 299.4253 | 2.813%
6058 | 20-54.5 | -54.6495 | 19.8847 | 500.433 | 160.4026 | 188.38 | 226.8199 | 261.0297 | 300.4002 | 2.867%
6059 | 20-55 | -54.9209 | 19.8847 | 486.4902 | 161.1568 | 188.8437 | 227.4553 | 261.828 | 301.3963 | 2.921%
6060 | 20-55 | -55.1922 | 19.8847 | 472.8104 | 161.9068 | 189.315 | 228.1107 | 262.6591 | 302.4414 | 2.975%
6061 | 20-55.5 | -55.4635 | 19.8847 | 459.4172 | 162.5883 | 189.7475 | 228.708 | 263.4132 | 303.3864 | 3.025%
6062 | 20-55.5 | -55.7348 | 19.8847 | 446.3365 | 163.2741 | 190.2028 | 229.3398 | 264.2133 | 304.3914 | 3.076%
6063 | 20-56 | -56.0061 | 19.8847 | 433.5965 | 163.9529 | 190.6846 | 230.0092 | 265.0619 | 305.4582 | 3.128%
6064 | 20-56.5 | -56.2775 | 19.8847 | 421.2281 | 164.5766 | 191.144 | 230.6376 | 265.8509 | 306.4424 | 3.176%
6065 | 20-56.5 | -56.5488 | 19.8847 | 409.2652 | 165.2073 | 191.6369 | 231.313 | 266.6999 | 307.5023 | 3.226%
6066 | 20-57 | -56.8201 | 19.8847 | 397.7443 | 165.8312 | 192.1595 | 232.0296 | 267.601 | 308.6278 | 3.277%
6067 | 20-57 | -57.0914 | 19.8847 | 386.7049 | 166.3938 | 192.6562 | 232.7063 | 268.4488 | 309.6832 | 3.324%
6068 | 20-57.5 | -57.3628 | 19.8847 | 376.1896 | 166.9765 | 193.1946 | 233.444 | 269.3759 | 310.8408 | 3.372%
6069 | 20-57.5 | -57.6341 | 19.8847 | 366.2433 | 167.5568 | 193.7621 | 234.224 | 270.3584 | 312.0696 | 3.422%
6070 | 20-58 | -57.9054 | 19.8847 | 356.9138 | 168.0767 | 194.298 | 234.9581 | 271.2811 | 313.2215 | 3.467%
6071 | 20-58 | -58.1767 | 19.8847 | 348.2505 | 168.6041 | 194.8555 | 235.717 | 272.2313 | 314.404 | 3.514%
6072 | 20-58.5 | -58.448 | 19.8847 | 340.3046 | 169.1122 | 195.4161 | 236.4719 | 273.17 | 315.5654 | 3.56%
6073 | 20-58.5 | -58.7194 | 19.8847 | 333.1272 | 169.5555 | 195.9274 | 237.1438 | 273.9926 | 316.5691 | 3.602%
6074 | 20-59 | -58.9907 | 19.8847 | 326.769 | 169.9906 | 196.443 | 237.8187 | 274.8169 | 317.5728 | 3.643%
6075 | 20-59.5 | -59.262 | 19.8847 | 321.2787 | 170.4068 | 196.9463 | 238.4738 | 275.6138 | 318.5399 | 3.684%
6076 | 20-59.5 | -59.5333 | 19.8847 | 316.7015 | 170.7856 | 197.4052 | 239.0663 | 276.3309 | 319.4059 | 3.721%
6077 | 20-60 | -59.8046 | 19.8847 | 313.0774 | 171.1684 | 197.8765 | 239.6851 | 277.088 | 320.3295 | 3.759%
6078 | 20-60 | -60.076 | 19.8847 | 310.4397 | 171.5389 | 198.3355 | 240.29 | 277.83 | 321.2367 | 3.795%
6079 | 20-60.5 | -60.3473 | 19.8847 | 308.8139 | 171.8789 | 198.7508 | 240.8287 | 278.4839 | 322.0286 | 3.83%
6080 | 20-60.5 | -60.6186 | 19.8847 | 308.2158 | 172.2355 | 199.187 | 241.3954 | 279.1725 | 322.8633 | 3.866%
6081 | 20-61 | -60.8899 | 19.8847 | 308.6516 | 172.5856 | 199.6117 | 241.9417 | 279.832 | 323.658 | 3.901%
6082 | 20-61 | -61.1613 | 19.8847 | 310.1167 | 172.9135 | 200.0012 | 242.4303 | 280.4116 | 324.345 | 3.936%
6083 | 20-61.5 | -61.4326 | 19.8847 | 312.5968 | 173.2689 | 200.4243 | 242.9623 | 281.0438 | 325.0959 | 3.973%
6084 | 20-61.5 | -61.7039 | 19.8847 | 316.0679 | 173.6185 | 200.8355 | 243.4718 | 281.6429 | 325.8001 | 4.011%
6085 | 20-62 | -61.9752 | 19.8847 | 320.4978 | 173.9445 | 201.2113 | 243.9254 | 282.1657 | 326.403 | 4.047%
6086 | 20-62 | -62.2465 | 19.8847 | 325.8475 | 174.2903 | 201.6146 | 244.4196 | 282.7422 | 327.0753 | 4.085%
6087 | 20-62.5 | -62.5179 | 19.8847 | 332.0724 | 174.6261 | 202.008 | 244.9045 | 283.31 | 327.7401 | 4.122%
6088 | 20-63 | -62.7892 | 19.8847 | 339.1244 | 174.9442 | 202.3819 | 245.367 | 283.853 | 328.3774 | 4.158%
6089 | 20-63 | -63.0605 | 19.8847 | 346.9529 | 175.2793 | 202.7814 | 245.8705 | 284.452 | 329.0894 | 4.194%
6090 | 20-63.5 | -63.3318 | 19.8847 | 355.5068 | 175.5908 | 203.1516 | 246.3348 | 285.0027 | 329.742 | 4.229%
6091 | 20-63.5 | -63.6031 | 19.8847 | 364.735 | 175.8694 | 203.4836 | 246.7526 | 285.4995 | 330.332 | 4.26%
6092 | 20-64 | -63.8745 | 19.8847 | 374.5875 | 176.1457 | 203.8245 | 247.2003 | 286.0471 | 331.0002 | 4.29%
6093 | 20-64 | -64.1458 | 19.8847 | 385.0165 | 176.3915 | 204.136 | 247.6215 | 286.5727 | 331.6523 | 4.315%
6094 | 20-64.5 | -64.4171 | 19.8847 | 395.9764 | 176.6127 | 204.4287 | 248.0354 | 287.1031 | 332.3259 | 4.337%
6095 | 20-64.5 | -64.6884 | 19.8847 | 407.4243 | 176.8372 | 204.7437 | 248.5059 | 287.7253 | 333.136 | 4.357%
6096 | 20-65 | -64.9598 | 19.8847 | 419.3203 | 177.0151 | 205.0066 | 248.9165 | 288.281 | 333.8722 | 4.371%
6097 | 20-65 | -65.2311 | 19.8847 | 431.6272 | 177.1552 | 205.2282 | 249.2809 | 288.7865 | 334.5545 | 4.38%
6098 | 20-65.5 | -65.5024 | 19.8847 | 444.3109 | 177.289 | 205.4526 | 249.665 | 289.3293 | 335.2966 | 4.388%
6099 | 20-66 | -65.7737 | 19.8847 | 457.3401 | 177.3729 | 205.6174 | 249.9739 | 289.7824 | 335.932 | 4.39%
6100 | 20-66 | -66.045 | 19.8847 | 470.6859 | 177.4192 | 205.7377 | 250.2271 | 290.1696 | 336.4893 | 4.388%
6101 | 20-66.5 | -66.3164 | 19.8847 | 484.3223 | 177.4504 | 205.8438 | 250.4686 | 290.5483 | 337.0429 | 4.384%
6102 | 20-66.5 | -66.5877 | 19.8847 | 498.2253 | 177.36 | 205.7923 | 250.4918 | 290.6506 | 337.249 | 4.367%
6103 | 20-67 | -66.859 | 19.8847 | 512.3731 | 177.1523 | 205.5995 | 250.3221 | 290.5108 | 337.1534 | 4.339%
6104 | 20-67 | -67.1303 | 19.8847 | 526.7461 | 176.8039 | 205.3025 | 250.0155 | 290.2038 | 336.8541 | 4.297%
6105 | 20-67.5 | -67.4016 | 19.8847 | 541.3263 | 176.3699 | 204.9148 | 249.5794 | 289.7297 | 336.3417 | 4.248%
6106 | 20-67.5 | -67.673 | 19.8847 | 556.0973 | 175.8903 | 204.4739 | 249.067 | 289.1571 | 335.7032 | 4.195%
6107 | 20-68 | -67.9443 | 19.8847 | 571.0444 | 175.383 | 204.0011 | 248.5106 | 288.5289 | 334.9948 | 4.14%
6108 | 20-68 | -68.2156 | 19.8847 | 586.1539 | 174.6839 | 203.3056 | 247.6294 | 287.4765 | 333.7395 | 4.069%
6109 | 20-68.5 | -68.4869 | 19.8847 | 601.4137 | 173.7877 | 202.4396 | 246.5096 | 286.12 | 332.1 | 3.981%
6110 | 20-69 | -68.7583 | 19.8847 | 616.8125 | 172.7034 | 201.4383 | 245.2098 | 284.5416 | 330.1877 | 3.878%
6111 | 20-69 | -69.0296 | 19.8847 | 632.3402 | 171.5068 | 200.3327 | 243.7616 | 282.772 | 328.032 | 3.767%
6112 | 20-69.5 | -69.3009 | 19.8847 | 647.9875 | 170.2478 | 199.1833 | 242.2589 | 280.9386 | 325.8011 | 3.653%
6113 | 20-69.5 | -69.5722 | 19.8847 | 663.7458 | 168.9443 | 198.0094 | 240.7345 | 279.0869 | 323.5571 | 3.537%
6114 | 20-70 | -69.8435 | 19.8847 | 679.6075 | 167.4976 | 196.7074 | 239.0222 | 276.989 | 320.9949 | 3.413%
6115 | 20-70 | -70.1149 | 19.8847 | 695.5654 | 166.021 | 195.4196 | 237.3301 | 274.9172 | 318.4662 | 3.291%
6116 | 20-70.5 | -70.3862 | 19.8847 | 711.613 | 164.5751 | 194.1965 | 235.7326 | 272.9688 | 316.0962 | 3.175%
6117 | 20-70.5 | -70.6575 | 19.8847 | 727.7444 | 163.5749 | 193.2907 | 234.5627 | 271.5519 | 314.3831 | 3.095%
6118 | 20-71 | -70.9288 | 19.8847 | 743.954 | 162.9932 | 192.6955 | 233.8279 | 270.6898 | 313.371 | 3.047%
6119 | 20-71 | -71.2001 | 19.8847 | 760.2368 | 162.7822 | 192.3794 | 233.4876 | 270.3335 | 313.002 | 3.026%
6120 | 20-71.5 | -71.4715 | 19.8847 | 776.5883 | 162.545 | 192.0258 | 233.0795 | 269.879 | 312.4963 | 3.003%
6121 | 20-71.5 | -71.7428 | 19.8847 | 793.004 | 162.4459 | 191.8292 | 232.893 | 269.7086 | 312.3515 | 2.991%
6122 | 20-72 | -72.0141 | 19.8847 | 809.4801 | 162.4944 | 191.7664 | 232.8939 | 269.7769 | 312.5084 | 2.99%
6123 | 20-72.5 | -72.2854 | 19.8847 | 826.013 | 162.3892 | 191.5918 | 232.7142 | 269.5968 | 312.3315 | 2.979%
6124 | 20-72.5 | -72.5568 | 19.8847 | 842.5992 | 162.0654 | 191.2793 | 232.3354 | 269.1582 | 311.8235 | 2.953%
6125 | 20-73 | -72.8281 | 19.8847 | 859.2356 | 161.6778 | 190.9305 | 231.8933 | 268.63 | 311.193 | 2.924%
6126 | 20-73 | -73.0994 | 19.8847 | 875.9194 | 161.795 | 190.9303 | 231.896 | 268.6355 | 311.202 | 2.93%
6127 | 20-73.5 | -73.3707 | 19.8847 | 892.6477 | 162.431 | 191.3879 | 232.5236 | 269.4256 | 312.1904 | 2.975%
6128 | 20-73.5 | -73.642 | 19.8847 | 909.4183 | 163.3634 | 192.1001 | 233.4933 | 270.641 | 313.7051 | 3.043%
6129 | 20-74 | -73.9134 | 19.8847 | 926.2286 | 163.9999 | 192.4613 | 233.9531 | 271.1917 | 314.3637 | 3.09%
6130 | 20-74 | -74.1847 | 19.8847 | 943.0766 | 163.8016 | 192.232 | 233.592 | 270.7015 | 313.7131 | 3.076%
6131 | 20-74.5 | -74.456 | 19.8847 | 959.9603 | 162.9293 | 191.5198 | 232.5539 | 269.3484 | 311.9723 | 3.014%
6132 | 20-74.5 | -74.7273 | 19.8847 | 976.8777 | 161.7592 | 190.589 | 231.1908 | 267.5663 | 309.6737 | 2.932%
6133 | 20-75 | -74.9986 | 19.8847 | 993.8271 | 160.704 | 189.7592 | 229.9709 | 265.9682 | 307.6087 | 2.86%
6134 | 20-75.5 | -75.27 | 19.8847 | 1010.8069 | 159.8773 | 189.0894 | 228.9633 | 264.6314 | 305.8641 | 2.805%
6135 | 20-75.5 | -75.5413 | 19.8847 | 1027.8154 | 159.5213 | 188.7348 | 228.3686 | 263.7989 | 304.7338 | 2.783%
6136 | 20-76 | -75.8126 | 19.8847 | 1044.8514 | 159.8636 | 188.949 | 228.5673 | 263.9758 | 304.8773 | 2.809%
6137 | 20-76 | -76.0839 | 19.8847 | 1061.9133 | 160.6964 | 189.5421 | 229.2841 | 264.8035 | 305.8335 | 2.87%
6138 | 20-76.5 | -76.3553 | 19.8847 | 1079 | 161.6161 | 190.1413 | 229.9914 | 265.6049 | 306.741 | 2.939%
6139 | 20-76.5 | -76.6266 | 19.8847 | 1096.1103 | 162.0407 | 190.3705 | 230.1922 | 265.7695 | 306.8531 | 2.973%
6140 | 20-77 | -76.8979 | 19.8847 | 1113.243 | 162.0864 | 190.2575 | 229.9127 | 265.3209 | 306.1888 | 2.979%
6141 | 20-77 | -77.1692 | 19.8847 | 1130.397 | 162.0121 | 190.0414 | 229.4767 | 264.6637 | 305.2509 | 2.977%
6142 | 20-77.5 | -77.4405 | 19.8847 | 1147.5715 | 162.3896 | 190.319 | 229.7243 | 264.8722 | 305.4021 | 3.01%
6143 | 20-77.5 | -77.7119 | 19.8847 | 1164.7654 | 163.3942 | 191.0603 | 230.6005 | 265.8661 | 306.529 | 3.092%
6144 | 20-78 | -77.9832 | 19.8847 | 1181.9778 | 164.82 | 192.1346 | 231.9192 | 267.4055 | 308.3255 | 3.21%
6145 | 20-78.5 | -78.2545 | 19.8847 | 1199.208 | 166.3148 | 193.3125 | 233.3781 | 269.1197 | 310.3388 | 3.338%
6146 | 20-78.5 | -78.5258 | 19.8847 | 1216.4551 | 167.8129 | 194.5252 | 234.8735 | 270.8713 | 312.3899 | 3.473%
6147 | 20-79 | -78.7971 | 19.8847 | 1233.7184 | 169.1658 | 195.6639 | 236.2617 | 272.4838 | 314.2627 | 3.6%
6148 | 20-79 | -79.0685 | 19.8847 | 1250.9972 | 170.1799 | 196.6239 | 237.4164 | 273.8115 | 315.7892 | 3.701%
6149 | 20-79.5 | -79.3398 | 19.8847 | 1268.2908 | 170.9022 | 197.3329 | 238.2173 | 274.6861 | 316.7404 | 3.779%
6150 | 20-79.5 | -79.6111 | 19.8847 | 1285.5985 | 171.5063 | 197.9411 | 238.8719 | 275.3705 | 317.4473 | 3.848%
6151 | 20-80 | -79.8824 | 19.8847 | 1302.9199 | 172.236 | 198.7249 | 239.7795 | 276.3829 | 318.575 | 3.93%
6152 | 20-80 | -80.1537 | 19.8847 | 1320.2542 | 173.0601 | 199.6181 | 240.839 | 277.588 | 319.9454 | 4.023%
6153 | 20-80.5 | -80.4251 | 19.8847 | 1337.6011 | 173.9283 | 200.5608 | 241.9702 | 278.8866 | 321.4359 | 4.121%
6154 | 20-80.5 | -80.6964 | 19.8847 | 1354.9598 | 174.7997 | 201.5225 | 243.1382 | 280.2394 | 323.0028 | 4.221%
6155 | 20-81 | -80.9677 | 19.8847 | 1372.33 | 175.6221 | 202.4367 | 244.2458 | 281.5201 | 324.4836 | 4.318%
6156 | 20-81 | -81.239 | 19.8847 | 1389.7112 | 176.3791 | 203.2989 | 245.2922 | 282.7315 | 325.886 | 4.409%
6157 | 20-81.5 | -81.5104 | 19.8847 | 1407.103 | 177.0913 | 204.1292 | 246.3088 | 283.9162 | 327.2664 | 4.495%
6158 | 20-82 | -81.7817 | 19.8847 | 1424.5048 | 177.7086 | 204.8454 | 247.1806 | 284.9276 | 328.4397 | 4.572%
6159 | 20-82 | -82.053 | 19.8847 | 1441.9164 | 178.2632 | 205.4941 | 247.9781 | 285.8597 | 329.5288 | 4.641%
6160 | 20-82.5 | -82.3243 | 19.8847 | 1459.3373 | 178.7937 | 206.1269 | 248.7758 | 286.8089 | 330.6573 | 4.705%
6161 | 20-82.5 | -82.5956 | 19.8847 | 1476.7672 | 179.229 | 206.6441 | 249.4244 | 287.5781 | 331.5686 | 4.759%
6162 | 20-83 | -82.867 | 19.8847 | 1494.2057 | 179.5961 | 207.0912 | 250.002 | 288.2773 | 332.4131 | 4.804%
6163 | 20-83 | -83.1383 | 19.8847 | 1511.6525 | 179.9209 | 207.5081 | 250.5733 | 288.9953 | 333.3097 | 4.84%
6164 | 20-83.5 | -83.4096 | 19.8847 | 1529.1072 | 180.134 | 207.7992 | 250.9973 | 289.5476 | 334.0197 | 4.861%
6165 | 20-83.5 | -83.6809 | 19.8847 | 1546.5696 | 180.2704 | 208.0145 | 251.3499 | 290.0352 | 334.6756 | 4.87%
6166 | 20-84 | -83.9522 | 19.8847 | 1564.0393 | 180.3515 | 208.1838 | 251.6756 | 290.517 | 335.3539 | 4.87%
6167 | 20-84 | -84.2236 | 19.8847 | 1581.5161 | 180.2873 | 208.1844 | 251.7959 | 290.7603 | 335.7553 | 4.851%
6168 | 20-84.5 | -84.4949 | 19.8847 | 1598.9997 | 180.1171 | 208.0691 | 251.7863 | 290.8628 | 336.0049 | 4.817%
6169 | 20-85 | -84.7662 | 19.8847 | 1616.4898 | 179.8555 | 207.8598 | 251.6818 | 290.8723 | 336.1664 | 4.771%
6170 | 20-85 | -85.0375 | 19.8847 | 1633.9862 | 179.3468 | 207.3629 | 251.226 | 290.4733 | 335.8532 | 4.694%
6171 | 20-85.5 | -85.3089 | 19.8847 | 1651.4887 | 178.6467 | 206.6508 | 250.5197 | 289.7938 | 335.2267 | 4.595%
6172 | 20-85.5 | -85.5802 | 19.8847 | 1668.997 | 177.7165 | 205.7339 | 249.5778 | 288.8534 | 334.3121 | 4.471%
6173 | 20-86 | -85.8515 | 19.8847 | 1686.5109 | 176.2428 | 204.3033 | 247.9403 | 287.0441 | 332.3176 | 4.295%
6174 | 20-86 | -86.1228 | 19.8847 | 1704.0302 | 174.1296 | 202.4574 | 245.7585 | 284.5692 | 329.5114 | 4.065%
6175 | 20-86.5 | -86.3941 | 19.8847 | 1721.5547 | 171.4561 | 200.233 | 243.0897 | 281.5065 | 325.9969 | 3.795%
6176 | 20-86.5 | -86.6655 | 19.8847 | 1739.0842 | 168.4927 | 197.7914 | 240.1309 | 278.085 | 322.0404 | 3.518%
6177 | 20-87 | -86.9368 | 19.8847 | 1756.6185 | 165.3128 | 195.2182 | 237.0093 | 274.4724 | 317.8598 | 3.243%
6178 | 20-87 | -87.2081 | 19.8847 | 1774.1574 | 161.9305 | 192.4943 | 233.7245 | 270.6696 | 313.4575 | 2.972%
6179 | 20-87.5 | -87.4794 | 19.8847 | 1791.7007 | 158.3137 | 189.5337 | 230.1961 | 266.562 | 308.6761 | 2.706%
6180 | 20-88 | -87.7507 | 19.8847 | 1809.2484 | 154.56 | 186.4363 | 226.5856 | 262.3614 | 303.7891 | 2.453%
6181 | 20-88 | -88.0221 | 19.8847 | 1826.8001 | 150.7095 | 183.2216 | 222.916 | 258.0945 | 298.828 | 2.216%
6182 | 20-88.5 | -88.2934 | 19.8847 | 1844.3559 | 146.8676 | 179.9629 | 219.249 | 253.8173 | 293.8395 | 2.001%
6183 | 20-88.5 | -88.5647 | 19.8847 | 1861.9154 | 143.1936 | 176.8527 | 215.8291 | 249.8328 | 289.1974 | 1.815%
6184 | 20-89 | -88.836 | 19.8847 | 1879.4786 | 139.7062 | 173.9273 | 212.6606 | 246.1411 | 284.896 | 1.656%
6185 | 20-89 | -89.1074 | 19.8847 | 1897.0453 | 136.4847 | 171.2852 | 209.7627 | 242.7492 | 280.9262 | 1.522%
6186 | 20-89.5 | -89.3787 | 19.8847 | 1914.6153 | 133.8482 | 169.216 | 207.5896 | 240.2635 | 278.0837 | 1.422%
6187 | 20-89.5 | -89.65 | 19.8847 | 1932.1887 | 131.9201 | 167.6436 | 206.0584 | 238.5681 | 276.2114 | 1.353%
6188 | 20-90 | -89.9213 | 19.8847 | 1949.7651 | 130.5214 | 166.4517 | 204.968 | 237.3866 | 274.9375 | 1.305%
6189 | 20-90 | -90.1926 | 19.8847 | 1967.3446 | 129.3888 | 165.4734 | 204.1174 | 236.4905 | 274.0028 | 1.268%
6190 | 20-90.5 | -90.464 | 19.8847 | 1984.9269 | 128.4855 | 164.6602 | 203.463 | 235.825 | 273.339 | 1.239%
6191 | 20-90.5 | -90.7353 | 19.8847 | 2002.512 | 127.7353 | 163.9379 | 202.9196 | 235.2791 | 272.8037 | 1.215%
6192 | 20-50 | -50.0371 | 20.156 | 770.0615 | 140.8809 | 176.1407 | 210.1609 | 240.0542 | 274.2007 | 1.74%
6193 | 20-50.5 | -50.3084 | 20.156 | 753.9506 | 142.2102 | 177.0356 | 211.2634 | 241.419 | 275.8805 | 1.803%
6194 | 20-50.5 | -50.5797 | 20.156 | 737.9189 | 143.4727 | 177.8591 | 212.3213 | 242.7365 | 277.5103 | 1.864%
6195 | 20-51 | -50.851 | 20.156 | 721.9714 | 144.7042 | 178.644 | 213.3699 | 244.0524 | 279.1488 | 1.925%
6196 | 20-51 | -51.1224 | 20.156 | 706.1142 | 145.9499 | 179.4306 | 214.4562 | 245.4285 | 280.8759 | 1.989%
6197 | 20-51.5 | -51.3937 | 20.156 | 690.3532 | 147.1293 | 180.168 | 215.4821 | 246.7279 | 282.5069 | 2.051%
6198 | 20-51.5 | -51.665 | 20.156 | 674.6955 | 148.2895 | 180.8945 | 216.497 | 248.0167 | 284.1278 | 2.113%
6199 | 20-52 | -51.9363 | 20.156 | 659.1482 | 149.4756 | 181.6419 | 217.5483 | 249.3572 | 285.8195 | 2.179%
6200 | 20-52 | -52.2077 | 20.156 | 643.7196 | 150.6068 | 182.354 | 218.5461 | 250.6266 | 287.4187 | 2.242%
6201 | 20-52.5 | -52.479 | 20.156 | 628.4183 | 151.7268 | 183.0607 | 219.5408 | 251.8955 | 289.0209 | 2.307%
6202 | 20-53 | -52.7503 | 20.156 | 613.2539 | 152.8646 | 183.7829 | 220.5672 | 253.2121 | 290.6911 | 2.374%
6203 | 20-53 | -53.0216 | 20.156 | 598.2369 | 153.9474 | 184.4672 | 221.5356 | 254.4516 | 292.2603 | 2.44%
6204 | 20-53.5 | -53.2929 | 20.156 | 583.3787 | 155.0294 | 185.1463 | 222.4878 | 255.6636 | 293.788 | 2.507%
6205 | 20-53.5 | -53.5643 | 20.156 | 568.6917 | 156.1307 | 185.8329 | 223.4401 | 256.8683 | 295.2991 | 2.577%
6206 | 20-54 | -53.8356 | 20.156 | 554.1896 | 157.1552 | 186.4616 | 224.2945 | 257.936 | 296.6247 | 2.644%
6207 | 20-54 | -54.1069 | 20.156 | 539.8873 | 158.1509 | 187.0672 | 225.1097 | 258.9488 | 297.8759 | 2.71%
6208 | 20-54.5 | -54.3782 | 20.156 | 525.8012 | 159.1281 | 187.6572 | 225.8983 | 259.9243 | 299.0765 | 2.777%
6209 | 20-54.5 | -54.6495 | 20.156 | 511.9492 | 159.9955 | 188.1747 | 226.5802 | 260.7602 | 300.0975 | 2.838%
6210 | 20-55 | -54.9209 | 20.156 | 498.3507 | 160.8388 | 188.6825 | 227.2569 | 261.5959 | 301.1248 | 2.898%
6211 | 20-55 | -55.1922 | 20.156 | 485.0272 | 161.6703 | 189.1923 | 227.9458 | 262.4543 | 302.1882 | 2.958%
6212 | 20-55.5 | -55.4635 | 20.156 | 472.002 | 162.4282 | 189.6601 | 228.5725 | 263.2308 | 303.1457 | 3.014%
6213 | 20-55.5 | -55.7348 | 20.156 | 459.3005 | 163.1839 | 190.147 | 229.2293 | 264.0484 | 304.1579 | 3.071%
6214 | 20-56 | -56.0061 | 20.156 | 446.9502 | 163.9213 | 190.6558 | 229.9184 | 264.9081 | 305.2243 | 3.127%
6215 | 20-56.5 | -56.2775 | 20.156 | 434.9812 | 164.5936 | 191.1365 | 230.5572 | 265.6958 | 306.1914 | 3.181%
6216 | 20-56.5 | -56.5488 | 20.156 | 423.4258 | 165.2641 | 191.6467 | 231.2389 | 266.5392 | 307.2299 | 3.235%
6217 | 20-57 | -56.8201 | 20.156 | 412.3188 | 165.9196 | 192.1831 | 231.9584 | 267.4316 | 308.3315 | 3.289%
6218 | 20-57 | -57.0914 | 20.156 | 401.6974 | 166.5052 | 192.6906 | 232.6367 | 268.2711 | 309.3657 | 3.338%
6219 | 20-57.5 | -57.3628 | 20.156 | 391.6012 | 167.1041 | 193.2372 | 233.3736 | 269.1882 | 310.5009 | 3.389%
6220 | 20-57.5 | -57.6341 | 20.156 | 382.0718 | 167.6932 | 193.8096 | 234.1501 | 270.1581 | 311.7053 | 3.44%
6221 | 20-58 | -57.9054 | 20.156 | 373.1527 | 168.2138 | 194.3468 | 234.8772 | 271.0654 | 312.8311 | 3.486%
6222 | 20-58 | -58.1767 | 20.156 | 364.8886 | 168.744 | 194.9089 | 235.6374 | 272.0132 | 314.0063 | 3.534%
6223 | 20-58.5 | -58.448 | 20.156 | 357.325 | 169.2566 | 195.4773 | 236.4009 | 272.9612 | 315.1775 | 3.581%
6224 | 20-58.5 | -58.7194 | 20.156 | 350.5074 | 169.7047 | 195.9978 | 237.0856 | 273.8 | 316.2016 | 3.623%
6225 | 20-59 | -58.9907 | 20.156 | 344.4799 | 170.1414 | 196.5213 | 237.7734 | 274.642 | 317.2292 | 3.666%
6226 | 20-59.5 | -59.262 | 20.156 | 339.2847 | 170.5559 | 197.0311 | 238.4413 | 275.458 | 318.2232 | 3.706%
6227 | 20-59.5 | -59.5333 | 20.156 | 334.9606 | 170.9338 | 197.4951 | 239.0467 | 276.1959 | 319.1201 | 3.743%
6228 | 20-60 | -59.8046 | 20.156 | 331.5416 | 171.3143 | 197.9716 | 239.6824 | 276.982 | 320.0881 | 3.781%
6229 | 20-60 | -60.076 | 20.156 | 329.056 | 171.6811 | 198.4352 | 240.3073 | 277.7597 | 321.0511 | 3.816%
6230 | 20-60.5 | -60.3473 | 20.156 | 327.5251 | 172.015 | 198.8537 | 240.8663 | 278.4514 | 321.9032 | 3.849%
6231 | 20-60.5 | -60.6186 | 20.156 | 326.9621 | 172.3635 | 199.2911 | 241.4513 | 279.176 | 322.7966 | 3.883%
6232 | 20-61 | -60.8899 | 20.156 | 327.3723 | 172.7038 | 199.7155 | 242.0149 | 279.8709 | 323.6501 | 3.917%
6233 | 20-61 | -61.1613 | 20.156 | 328.7518 | 173.0211 | 200.1046 | 242.5219 | 280.4881 | 324.3995 | 3.95%
6234 | 20-61.5 | -61.4326 | 20.156 | 331.0885 | 173.3664 | 200.5287 | 243.0755 | 281.163 | 325.2201 | 3.985%
6235 | 20-61.5 | -61.7039 | 20.156 | 334.3625 | 173.7054 | 200.94 | 243.6048 | 281.8021 | 325.9905 | 4.02%
6236 | 20-62 | -61.9752 | 20.156 | 338.5465 | 174.0192 | 201.3125 | 244.0717 | 282.3554 | 326.6459 | 4.054%
6237 | 20-62 | -62.2465 | 20.156 | 343.6073 | 174.3526 | 201.7115 | 244.5768 | 282.9584 | 327.3649 | 4.09%
6238 | 20-62.5 | -62.5179 | 20.156 | 349.5067 | 174.6706 | 202.0922 | 245.0587 | 283.5338 | 328.051 | 4.124%
6239 | 20-63 | -62.7892 | 20.156 | 356.203 | 174.9607 | 202.4382 | 245.4946 | 284.0522 | 328.6672 | 4.156%
6240 | 20-63 | -63.0605 | 20.156 | 363.6524 | 175.2578 | 202.795 | 245.9483 | 284.5954 | 329.3166 | 4.188%
6241 | 20-63.5 | -63.3318 | 20.156 | 371.8094 | 175.5339 | 203.1231 | 246.3597 | 285.0831 | 329.8944 | 4.219%
6242 | 20-63.5 | -63.6031 | 20.156 | 380.6285 | 175.7894 | 203.4256 | 246.7377 | 285.5301 | 330.4226 | 4.247%
6243 | 20-64 | -63.8745 | 20.156 | 390.0649 | 176.0551 | 203.7514 | 247.162 | 286.0468 | 331.05 | 4.276%
6244 | 20-64 | -64.1458 | 20.156 | 400.0749 | 176.2967 | 204.0546 | 247.5675 | 286.549 | 331.6695 | 4.301%
6245 | 20-64.5 | -64.4171 | 20.156 | 410.6164 | 176.5167 | 204.3416 | 247.9679 | 287.0581 | 332.3116 | 4.323%
6246 | 20-64.5 | -64.6884 | 20.156 | 421.6496 | 176.743 | 204.6536 | 248.4268 | 287.6599 | 333.0902 | 4.344%
6247 | 20-65 | -64.9598 | 20.156 | 433.1369 | 176.9257 | 204.9162 | 248.8276 | 288.1961 | 333.7946 | 4.359%
6248 | 20-65 | -65.2311 | 20.156 | 445.0431 | 177.0756 | 205.1437 | 249.1904 | 288.6921 | 334.457 | 4.37%
6249 | 20-65.5 | -65.5024 | 20.156 | 457.3355 | 177.2261 | 205.3835 | 249.5873 | 289.2445 | 335.2044 | 4.38%
6250 | 20-66 | -65.7737 | 20.156 | 469.9837 | 177.3295 | 205.5674 | 249.9135 | 289.7127 | 335.8515 | 4.385%
6251 | 20-66 | -66.045 | 20.156 | 482.9598 | 177.4027 | 205.7162 | 250.1969 | 290.1312 | 336.4409 | 4.386%
6252 | 20-66.5 | -66.3164 | 20.156 | 496.238 | 177.4734 | 205.8674 | 250.4922 | 290.5713 | 337.0644 | 4.387%
6253 | 20-66.5 | -66.5877 | 20.156 | 509.7947 | 177.4536 | 205.9024 | 250.6281 | 290.8107 | 337.4371 | 4.378%
6254 | 20-67 | -66.859 | 20.156 | 523.6083 | 177.3399 | 205.8284 | 250.6186 | 290.8706 | 337.5891 | 4.359%
6255 | 20-67 | -67.1303 | 20.156 | 537.6588 | 177.1158 | 205.671 | 250.5045 | 290.8065 | 337.5942 | 4.33%
6256 | 20-67.5 | -67.4016 | 20.156 | 551.9282 | 176.8056 | 205.4161 | 250.253 | 290.5668 | 337.3768 | 4.292%
6257 | 20-67.5 | -67.673 | 20.156 | 566.3999 | 176.4485 | 205.1042 | 249.9206 | 290.2229 | 337.0268 | 4.25%
6258 | 20-68 | -67.9443 | 20.156 | 581.0588 | 176.0653 | 204.7612 | 249.5453 | 289.8249 | 336.6088 | 4.206%
6259 | 20-68 | -68.2156 | 20.156 | 595.891 | 175.4896 | 204.1913 | 248.8383 | 288.9933 | 335.6311 | 4.146%
6260 | 20-68.5 | -68.4869 | 20.156 | 610.8838 | 174.7148 | 203.446 | 247.8844 | 287.8459 | 334.2535 | 4.068%
6261 | 20-69 | -68.7583 | 20.156 | 626.0257 | 173.749 | 202.56 | 246.7415 | 286.464 | 332.5861 | 3.974%
6262 | 20-69 | -69.0296 | 20.156 | 641.3062 | 172.682 | 201.5726 | 245.4537 | 284.8952 | 330.6801 | 3.873%
6263 | 20-69.5 | -69.3009 | 20.156 | 656.7154 | 171.5667 | 200.5503 | 244.1253 | 283.2809 | 328.7232 | 3.77%
6264 | 20-69.5 | -69.5722 | 20.156 | 672.2446 | 170.4208 | 199.5143 | 242.7923 | 281.672 | 326.7848 | 3.665%
6265 | 20-70 | -69.8435 | 20.156 | 687.8855 | 169.1221 | 198.3393 | 241.256 | 279.797 | 324.503 | 3.55%
6266 | 20-70 | -70.1149 | 20.156 | 703.6306 | 167.765 | 197.1432 | 239.6895 | 277.8832 | 322.1717 | 3.434%
6267 | 20-70.5 | -70.3862 | 20.156 | 719.4732 | 166.4034 | 195.9697 | 238.1575 | 276.0155 | 319.9009 | 3.321%
6268 | 20-70.5 | -70.6575 | 20.156 | 735.4068 | 165.4121 | 195.0528 | 236.9687 | 274.5722 | 318.152 | 3.239%
6269 | 20-71 | -70.9288 | 20.156 | 751.4257 | 164.7924 | 194.4134 | 236.1705 | 273.6281 | 317.0352 | 3.186%
6270 | 20-71 | -71.2001 | 20.156 | 767.5245 | 164.5059 | 194.0278 | 235.733 | 273.1483 | 316.5104 | 3.158%
6271 | 20-71.5 | -71.4715 | 20.156 | 783.6981 | 164.193 | 193.6022 | 235.2257 | 272.5686 | 315.8479 | 3.129%
6272 | 20-71.5 | -71.7428 | 20.156 | 799.9421 | 164.0193 | 193.3361 | 234.9462 | 272.2828 | 315.5607 | 3.111%
6273 | 20-72 | -72.0141 | 20.156 | 816.2523 | 164.0006 | 193.2109 | 234.8662 | 272.2531 | 315.599 | 3.104%
6274 | 20-72.5 | -72.2854 | 20.156 | 832.6246 | 163.8709 | 193.0013 | 234.6445 | 272.0246 | 315.3662 | 3.091%
6275 | 20-72.5 | -72.5568 | 20.156 | 849.0554 | 163.5483 | 192.6727 | 234.2489 | 271.5687 | 314.8406 | 3.064%
6276 | 20-73 | -72.8281 | 20.156 | 865.5414 | 163.1704 | 192.3146 | 233.7984 | 271.033 | 314.2035 | 3.034%
6277 | 20-73 | -73.0994 | 20.156 | 882.0795 | 163.2479 | 192.2694 | 233.7432 | 270.9682 | 314.1271 | 3.038%
6278 | 20-73.5 | -73.3707 | 20.156 | 898.6668 | 163.8158 | 192.6685 | 234.2972 | 271.6706 | 315.0107 | 3.078%
6279 | 20-73.5 | -73.642 | 20.156 | 915.3005 | 164.6595 | 193.3139 | 235.1846 | 272.7892 | 316.4116 | 3.141%
6280 | 20-74 | -73.9134 | 20.156 | 931.9781 | 165.2152 | 193.615 | 235.5728 | 273.2579 | 316.976 | 3.182%
6281 | 20-74 | -74.1847 | 20.156 | 948.6973 | 164.9673 | 193.3512 | 235.176 | 272.7316 | 316.2893 | 3.164%
6282 | 20-74.5 | -74.456 | 20.156 | 965.4558 | 164.0783 | 192.6292 | 234.1362 | 271.3852 | 314.5661 | 3.099%
6283 | 20-74.5 | -74.7273 | 20.156 | 982.2517 | 162.9222 | 191.7086 | 232.7982 | 269.6432 | 312.3264 | 3.016%
6284 | 20-75 | -74.9986 | 20.156 | 999.083 | 161.8741 | 190.8862 | 231.5989 | 268.0789 | 310.3121 | 2.943%
6285 | 20-75.5 | -75.27 | 20.156 | 1015.9479 | 161.0371 | 190.2065 | 230.5865 | 266.7427 | 308.5751 | 2.886%
6286 | 20-75.5 | -75.5413 | 20.156 | 1032.8447 | 160.6253 | 189.795 | 229.9195 | 265.8237 | 307.3412 | 2.859%
6287 | 20-76 | -75.8126 | 20.156 | 1049.7719 | 160.808 | 189.8848 | 229.9526 | 265.796 | 307.2332 | 2.875%
6288 | 20-76 | -76.0839 | 20.156 | 1066.728 | 161.402 | 190.2998 | 230.4304 | 266.3272 | 307.8233 | 2.92%
6289 | 20-76.5 | -76.3553 | 20.156 | 1083.7115 | 162.0513 | 190.6975 | 230.8673 | 266.7932 | 308.317 | 2.969%
6290 | 20-76.5 | -76.6266 | 20.156 | 1100.7212 | 162.2353 | 190.744 | 230.8236 | 266.6551 | 308.056 | 2.986%
6291 | 20-77 | -76.8979 | 20.156 | 1117.7559 | 162.0782 | 190.4701 | 230.3276 | 265.9374 | 307.0591 | 2.977%
6292 | 20-77 | -77.1692 | 20.156 | 1134.8143 | 161.8384 | 190.1131 | 229.6991 | 265.0386 | 305.82 | 2.962%
6293 | 20-77.5 | -77.4405 | 20.156 | 1151.8954 | 162.0628 | 190.2554 | 229.7592 | 265.0101 | 305.6737 | 2.984%
6294 | 20-77.5 | -77.7119 | 20.156 | 1168.9982 | 162.9453 | 190.8782 | 230.4685 | 265.7907 | 306.5308 | 3.055%
6295 | 20-78 | -77.9832 | 20.156 | 1186.1217 | 164.2905 | 191.8622 | 231.657 | 267.1613 | 308.1113 | 3.165%
6296 | 20-78.5 | -78.2545 | 20.156 | 1203.2649 | 165.7293 | 192.9799 | 233.0252 | 268.7553 | 309.9678 | 3.287%
6297 | 20-78.5 | -78.5258 | 20.156 | 1220.427 | 167.1832 | 194.1444 | 234.445 | 270.4045 | 311.8833 | 3.416%
6298 | 20-79 | -78.7971 | 20.156 | 1237.6072 | 168.5049 | 195.2481 | 235.7752 | 271.9364 | 313.6472 | 3.539%
6299 | 20-79 | -79.0685 | 20.156 | 1254.8047 | 169.5237 | 196.2121 | 236.9263 | 273.2525 | 315.1517 | 3.64%
6300 | 20-79.5 | -79.3398 | 20.156 | 1272.0188 | 170.3081 | 196.9614 | 237.7735 | 274.1785 | 316.16 | 3.722%
6301 | 20-79.5 | -79.6111 | 20.156 | 1289.2487 | 171.0092 | 197.631 | 238.5029 | 274.9497 | 316.9677 | 3.799%
6302 | 20-80 | -79.8824 | 20.156 | 1306.4938 | 171.8411 | 198.4792 | 239.4879 | 276.0511 | 318.1975 | 3.89%
6303 | 20-80 | -80.1537 | 20.156 | 1323.7534 | 172.7753 | 199.4457 | 240.6359 | 277.3583 | 319.6856 | 3.993%
6304 | 20-80.5 | -80.4251 | 20.156 | 1341.027 | 173.7581 | 200.4709 | 241.8689 | 278.776 | 321.3157 | 4.103%
6305 | 20-80.5 | -80.6964 | 20.156 | 1358.314 | 174.7426 | 201.5213 | 243.1493 | 280.2632 | 323.043 | 4.215%
6306 | 20-81 | -80.9677 | 20.156 | 1375.6139 | 175.6681 | 202.5206 | 244.3652 | 281.6736 | 324.6788 | 4.323%
6307 | 20-81 | -81.239 | 20.156 | 1392.9261 | 176.498 | 203.4493 | 245.495 | 282.9839 | 326.1985 | 4.422%
6308 | 20-81.5 | -81.5104 | 20.156 | 1410.2501 | 177.2437 | 204.3177 | 246.5568 | 284.2199 | 327.6371 | 4.513%
6309 | 20-82 | -81.7817 | 20.156 | 1427.5855 | 177.8726 | 205.0444 | 247.4364 | 285.2362 | 328.8113 | 4.591%
6310 | 20-82 | -82.053 | 20.156 | 1444.9318 | 178.4313 | 205.6939 | 248.2288 | 286.157 | 329.8812 | 4.661%
6311 | 20-82.5 | -82.3243 | 20.156 | 1462.2886 | 178.969 | 206.3314 | 249.0265 | 287.1014 | 330.9983 | 4.728%
6312 | 20-82.5 | -82.5956 | 20.156 | 1479.6555 | 179.4188 | 206.8626 | 249.6877 | 287.8812 | 331.9176 | 4.784%
6313 | 20-83 | -82.867 | 20.156 | 1497.032 | 179.8105 | 207.3365 | 250.2951 | 288.6125 | 332.7964 | 4.832%
6314 | 20-83 | -83.1383 | 20.156 | 1514.418 | 180.1712 | 207.7943 | 250.9149 | 289.3858 | 333.756 | 4.873%
6315 | 20-83.5 | -83.4096 | 20.156 | 1531.8129 | 180.4239 | 208.1313 | 251.3946 | 290.0026 | 334.5407 | 4.899%
6316 | 20-83.5 | -83.6809 | 20.156 | 1549.2164 | 180.5986 | 208.3909 | 251.801 | 290.5525 | 335.2686 | 4.914%
6317 | 20-84 | -83.9522 | 20.156 | 1566.6282 | 180.7141 | 208.5998 | 252.1743 | 291.0891 | 336.01 | 4.918%
6318 | 20-84 | -84.2236 | 20.156 | 1584.048 | 180.6786 | 208.6324 | 252.3315 | 291.3733 | 336.457 | 4.902%
6319 | 20-84.5 | -84.4949 | 20.156 | 1601.4755 | 180.5385 | 208.5515 | 252.3631 | 291.5231 | 336.7609 | 4.872%
6320 | 20-85 | -84.7662 | 20.156 | 1618.9104 | 180.311 | 208.3829 | 252.3098 | 291.5934 | 336.9945 | 4.83%
6321 | 20-85 | -85.0375 | 20.156 | 1636.3525 | 179.8384 | 207.929 | 251.9082 | 291.2589 | 336.7579 | 4.757%
6322 | 20-85.5 | -85.3089 | 20.156 | 1653.8014 | 179.1757 | 207.2614 | 251.2579 | 290.646 | 336.2105 | 4.66%
6323 | 20-85.5 | -85.5802 | 20.156 | 1671.2569 | 178.2844 | 206.3911 | 250.3748 | 289.7758 | 335.3795 | 4.539%
6324 | 20-86 | -85.8515 | 20.156 | 1688.7187 | 176.8958 | 205.0343 | 248.8362 | 288.0891 | 333.5365 | 4.37%
6325 | 20-86 | -86.1228 | 20.156 | 1706.1868 | 174.9076 | 203.2837 | 246.7854 | 285.7795 | 330.9375 | 4.148%
6326 | 20-86.5 | -86.3941 | 20.156 | 1723.6607 | 172.3935 | 201.1736 | 244.2764 | 282.9204 | 327.6806 | 3.887%
6327 | 20-86.5 | -86.6655 | 20.156 | 1741.1403 | 169.607 | 198.8501 | 241.4835 | 279.7109 | 323.9928 | 3.619%
6328 | 20-87 | -86.9368 | 20.156 | 1758.6253 | 166.6269 | 196.4078 | 238.5456 | 276.3329 | 320.1093 | 3.352%
6329 | 20-87 | -87.2081 | 20.156 | 1776.1157 | 163.4655 | 193.8392 | 235.4613 | 272.7852 | 316.0294 | 3.089%
6330 | 20-87.5 | -87.4794 | 20.156 | 1793.6111 | 160.0838 | 191.0552 | 232.1354 | 268.9337 | 311.5693 | 2.83%
6331 | 20-88 | -87.7507 | 20.156 | 1811.1115 | 156.5708 | 188.156 | 228.7341 | 264.9961 | 307.0112 | 2.582%
6332 | 20-88 | -88.0221 | 20.156 | 1828.6165 | 152.9636 | 185.1558 | 225.2773 | 260.9958 | 302.3822 | 2.349%
6333 | 20-88.5 | -88.2934 | 20.156 | 1846.1261 | 149.3559 | 182.1119 | 221.8145 | 256.9739 | 297.7112 | 2.136%
6334 | 20-88.5 | -88.5647 | 20.156 | 1863.6401 | 145.9092 | 179.2188 | 218.5964 | 253.2426 | 293.385 | 1.95%
6335 | 20-89 | -88.836 | 20.156 | 1881.1582 | 142.6432 | 176.5122 | 215.6271 | 249.8019 | 289.398 | 1.79%
6336 | 20-89 | -89.1074 | 20.156 | 1898.6805 | 139.639 | 174.0917 | 212.9233 | 246.6548 | 285.7345 | 1.655%
6337 | 20-89.5 | -89.3787 | 20.156 | 1916.2066 | 137.1713 | 172.2201 | 210.9021 | 244.3579 | 283.1257 | 1.554%
6338 | 20-89.5 | -89.65 | 20.156 | 1933.7365 | 135.3604 | 170.8132 | 209.4739 | 242.7876 | 281.4047 | 1.484%
6339 | 20-90 | -89.9213 | 20.156 | 1951.2699 | 134.0191 | 169.7366 | 208.4215 | 241.6462 | 280.1724 | 1.434%
6340 | 20-90 | -90.1926 | 20.156 | 1968.8069 | 132.9012 | 168.837 | 207.5665 | 240.7346 | 279.2076 | 1.394%
6341 | 20-90.5 | -90.464 | 20.156 | 1986.3472 | 131.9771 | 168.0732 | 206.8718 | 240.007 | 278.4541 | 1.361%
6342 | 20-90.5 | -90.7353 | 20.156 | 2003.8907 | 131.1825 | 167.3764 | 206.2682 | 239.3748 | 277.7992 | 1.334%
6343 | 20-50 | -50.0371 | 20.4273 | 777.7002 | 138.8929 | 174.8828 | 208.8058 | 238.5034 | 272.4259 | 1.65%
6344 | 20-50.5 | -50.3084 | 20.4273 | 761.7771 | 140.2856 | 175.8625 | 209.9531 | 239.914 | 274.1518 | 1.714%
6345 | 20-50.5 | -50.5797 | 20.4273 | 745.9395 | 141.6103 | 176.7597 | 211.0542 | 241.2767 | 275.8286 | 1.775%
6346 | 20-51 | -50.851 | 20.4273 | 730.1932 | 142.9024 | 177.6081 | 212.1463 | 242.6405 | 277.5198 | 1.837%
6347 | 20-51 | -51.1224 | 20.4273 | 714.5441 | 144.2074 | 178.4488 | 213.2778 | 244.0689 | 279.3075 | 1.901%
6348 | 20-51.5 | -51.3937 | 20.4273 | 698.9988 | 145.4461 | 179.2289 | 214.3496 | 245.4232 | 281.0038 | 1.963%
6349 | 20-51.5 | -51.665 | 20.4273 | 683.5645 | 146.6673 | 179.9922 | 215.4118 | 246.769 | 282.6933 | 2.026%
6350 | 20-52 | -51.9363 | 20.4273 | 668.2488 | 147.9174 | 180.7777 | 216.512 | 248.1682 | 284.4556 | 2.092%
6351 | 20-52 | -52.2077 | 20.4273 | 653.0601 | 149.1165 | 181.5298 | 217.5598 | 249.4969 | 286.1249 | 2.158%
6352 | 20-52.5 | -52.479 | 20.4273 | 638.0076 | 150.3082 | 182.2776 | 218.6049 | 250.8244 | 287.7953 | 2.224%
6353 | 20-53 | -52.7503 | 20.4273 | 623.1011 | 151.5212 | 183.042 | 219.6816 | 252.1988 | 289.5316 | 2.294%
6354 | 20-53 | -53.0216 | 20.4273 | 608.3515 | 152.6828 | 183.7693 | 220.6998 | 253.4935 | 291.1621 | 2.362%
6355 | 20-53.5 | -53.2929 | 20.4273 | 593.7703 | 153.8486 | 184.4941 | 221.7045 | 254.7639 | 292.7547 | 2.432%
6356 | 20-53.5 | -53.5643 | 20.4273 | 579.3705 | 155.0396 | 185.2296 | 222.7136 | 256.0321 | 294.3368 | 2.506%
6357 | 20-54 | -53.8356 | 20.4273 | 565.1658 | 156.1571 | 185.9094 | 223.6279 | 257.1672 | 295.7379 | 2.577%
6358 | 20-54 | -54.1069 | 20.4273 | 551.1714 | 157.2512 | 186.5688 | 224.505 | 258.2488 | 297.0654 | 2.649%
6359 | 20-54.5 | -54.3782 | 20.4273 | 537.4038 | 158.3319 | 187.215 | 225.357 | 259.2935 | 298.3416 | 2.722%
6360 | 20-54.5 | -54.6495 | 20.4273 | 523.8809 | 159.2982 | 187.7843 | 226.0939 | 260.1864 | 299.4207 | 2.788%
6361 | 20-55 | -54.9209 | 20.4273 | 510.6221 | 160.2345 | 188.3391 | 226.8179 | 261.0683 | 300.4916 | 2.855%
6362 | 20-55 | -55.1922 | 20.4273 | 497.6485 | 161.1522 | 188.8909 | 227.5464 | 261.9626 | 301.5853 | 2.92%
6363 | 20-55.5 | -55.4635 | 20.4273 | 484.9832 | 161.9895 | 189.3963 | 228.2063 | 262.7669 | 302.5626 | 2.982%
6364 | 20-55.5 | -55.7348 | 20.4273 | 472.6509 | 162.8165 | 189.9153 | 228.8897 | 263.6043 | 303.5852 | 3.044%
6365 | 20-56 | -56.0061 | 20.4273 | 460.6783 | 163.6202 | 190.4511 | 229.5986 | 264.4758 | 304.6523 | 3.106%
6366 | 20-56.5 | -56.2775 | 20.4273 | 449.0943 | 164.3531 | 190.955 | 230.2518 | 265.2681 | 305.611 | 3.164%
6367 | 20-56.5 | -56.5488 | 20.4273 | 437.9298 | 165.0762 | 191.4845 | 230.943 | 266.1104 | 306.6343 | 3.223%
6368 | 20-57 | -56.8201 | 20.4273 | 427.2176 | 165.7756 | 192.0362 | 231.667 | 266.9958 | 307.7137 | 3.281%
6369 | 20-57 | -57.0914 | 20.4273 | 416.9927 | 166.3959 | 192.555 | 232.3463 | 267.8253 | 308.7233 | 3.334%
6370 | 20-57.5 | -57.3628 | 20.4273 | 407.2917 | 167.022 | 193.1096 | 233.0809 | 268.7292 | 309.8311 | 3.388%
6371 | 20-57.5 | -57.6341 | 20.4273 | 398.153 | 167.6309 | 193.6868 | 233.8518 | 269.6828 | 311.0053 | 3.441%
6372 | 20-58 | -57.9054 | 20.4273 | 389.6162 | 168.1637 | 194.2254 | 234.5706 | 270.5715 | 312.0992 | 3.489%
6373 | 20-58 | -58.1767 | 20.4273 | 381.7216 | 168.7072 | 194.7919 | 235.3295 | 271.512 | 313.2592 | 3.538%
6374 | 20-58.5 | -58.448 | 20.4273 | 374.51 | 169.2337 | 195.3674 | 236.0983 | 272.4632 | 314.4307 | 3.587%
6375 | 20-58.5 | -58.7194 | 20.4273 | 368.0214 | 169.6955 | 195.8965 | 236.7928 | 273.3129 | 315.4669 | 3.631%
6376 | 20-59 | -58.9907 | 20.4273 | 362.2948 | 170.1454 | 196.4292 | 237.4934 | 274.1711 | 316.5146 | 3.675%
6377 | 20-59.5 | -59.262 | 20.4273 | 357.3667 | 170.5722 | 196.949 | 238.1768 | 275.0081 | 317.5366 | 3.716%
6378 | 20-59.5 | -59.5333 | 20.4273 | 353.2706 | 170.9576 | 197.423 | 238.8 | 275.7713 | 318.4684 | 3.754%
6379 | 20-60 | -59.8046 | 20.4273 | 350.0358 | 171.3408 | 197.9078 | 239.4542 | 276.5862 | 319.478 | 3.791%
6380 | 20-60 | -60.076 | 20.4273 | 347.6863 | 171.7075 | 198.3785 | 240.0989 | 277.3968 | 320.4904 | 3.826%
6381 | 20-60.5 | -60.3473 | 20.4273 | 346.2401 | 172.039 | 198.803 | 240.6791 | 278.1252 | 321.3992 | 3.858%
6382 | 20-60.5 | -60.6186 | 20.4273 | 345.7085 | 172.3835 | 199.245 | 241.2847 | 278.8865 | 322.3502 | 3.892%
6383 | 20-61 | -60.8899 | 20.4273 | 346.0957 | 172.7183 | 199.6729 | 241.8682 | 279.6181 | 323.2619 | 3.924%
6384 | 20-61 | -61.1613 | 20.4273 | 347.3988 | 173.0293 | 200.065 | 242.3955 | 280.2734 | 324.0722 | 3.955%
6385 | 20-61.5 | -61.4326 | 20.4273 | 349.6074 | 173.3682 | 200.4928 | 242.9713 | 280.9895 | 324.9582 | 3.989%
6386 | 20-61.5 | -61.7039 | 20.4273 | 352.7045 | 173.7 | 200.9068 | 243.5216 | 281.6682 | 325.7922 | 4.022%
6387 | 20-62 | -61.9752 | 20.4273 | 356.6671 | 174.0059 | 201.2803 | 244.0057 | 282.2556 | 326.5033 | 4.054%
6388 | 20-62 | -62.2465 | 20.4273 | 361.4665 | 174.3315 | 201.6799 | 244.5269 | 282.8906 | 327.2749 | 4.088%
6389 | 20-62.5 | -62.5179 | 20.4273 | 367.07 | 174.6423 | 202.0608 | 245.0228 | 283.4939 | 328.007 | 4.121%
6390 | 20-63 | -62.7892 | 20.4273 | 373.4413 | 174.9261 | 202.4064 | 245.4693 | 284.0344 | 328.6597 | 4.151%
6391 | 20-63 | -63.0605 | 20.4273 | 380.542 | 175.2183 | 202.763 | 245.9314 | 284.5948 | 329.3379 | 4.182%
6392 | 20-63.5 | -63.3318 | 20.4273 | 388.3319 | 175.4902 | 203.0894 | 246.3457 | 285.0905 | 329.9299 | 4.212%
6393 | 20-63.5 | -63.6031 | 20.4273 | 396.7705 | 175.7417 | 203.3879 | 246.7195 | 285.5332 | 330.4539 | 4.24%
6394 | 20-64 | -63.8745 | 20.4273 | 405.8172 | 176.0043 | 203.7079 | 247.1336 | 286.0351 | 331.0609 | 4.268%
6395 | 20-64 | -64.1458 | 20.4273 | 415.4324 | 176.2439 | 204.005 | 247.5256 | 286.5163 | 331.6499 | 4.294%
6396 | 20-64.5 | -64.4171 | 20.4273 | 425.5775 | 176.4636 | 204.2866 | 247.9112 | 287.0012 | 332.2557 | 4.316%
6397 | 20-64.5 | -64.6884 | 20.4273 | 436.2155 | 176.6913 | 204.5937 | 248.3539 | 287.5752 | 332.9916 | 4.338%
6398 | 20-65 | -64.9598 | 20.4273 | 447.3111 | 176.8784 | 204.8542 | 248.7405 | 288.0846 | 333.6531 | 4.354%
6399 | 20-65 | -65.2311 | 20.4273 | 458.8313 | 177.0374 | 205.0851 | 249.0961 | 288.5626 | 334.2835 | 4.368%
6400 | 20-65.5 | -65.5024 | 20.4273 | 470.7447 | 177.2025 | 205.336 | 249.4971 | 289.1115 | 335.0173 | 4.38%
6401 | 20-66 | -65.7737 | 20.4273 | 483.0223 | 177.3231 | 205.5339 | 249.8308 | 289.5801 | 335.6553 | 4.387%
6402 | 20-66 | -66.045 | 20.4273 | 495.637 | 177.4153 | 205.6986 | 250.1243 | 290.0021 | 336.2393 | 4.391%
6403 | 20-66.5 | -66.3164 | 20.4273 | 508.5637 | 177.5066 | 205.8686 | 250.434 | 290.4515 | 336.8653 | 4.395%
6404 | 20-66.5 | -66.5877 | 20.4273 | 521.7791 | 177.5351 | 205.9599 | 250.6387 | 290.7712 | 337.3314 | 4.391%
6405 | 20-67 | -66.859 | 20.4273 | 535.2619 | 177.5116 | 205.9899 | 250.7675 | 291.0017 | 337.693 | 4.382%
6406 | 20-67 | -67.1303 | 20.4273 | 548.9923 | 177.4423 | 205.9846 | 250.8613 | 291.1986 | 338.0237 | 4.368%
6407 | 20-67.5 | -67.4016 | 20.4273 | 562.9521 | 177.3002 | 205.8922 | 250.8341 | 291.2422 | 338.1615 | 4.346%
6408 | 20-67.5 | -67.673 | 20.4273 | 577.1248 | 177.1149 | 205.7459 | 250.7314 | 291.1892 | 338.177 | 4.32%
6409 | 20-68 | -67.9443 | 20.4273 | 591.4949 | 176.906 | 205.5714 | 250.5902 | 291.0882 | 338.1329 | 4.292%
6410 | 20-68 | -68.2156 | 20.4273 | 606.0484 | 176.5053 | 205.1686 | 250.1155 | 290.5513 | 337.5263 | 4.248%
6411 | 20-68.5 | -68.4869 | 20.4273 | 620.7724 | 175.9042 | 204.5865 | 249.3875 | 289.6898 | 336.5076 | 4.185%
6412 | 20-69 | -68.7583 | 20.4273 | 635.655 | 175.1094 | 203.8592 | 248.4622 | 288.5818 | 335.1829 | 4.105%
6413 | 20-69 | -69.0296 | 20.4273 | 650.6852 | 174.2285 | 203.0371 | 247.4005 | 287.2971 | 333.6316 | 4.018%
6414 | 20-69.5 | -69.3009 | 20.4273 | 665.8531 | 173.3172 | 202.1922 | 246.3155 | 285.989 | 332.0575 | 3.93%
6415 | 20-69.5 | -69.5722 | 20.4273 | 681.1494 | 172.3927 | 201.3475 | 245.2459 | 284.7122 | 330.5352 | 3.841%
6416 | 20-70 | -69.8435 | 20.4273 | 696.5656 | 171.3026 | 200.3511 | 243.9566 | 283.1499 | 328.6462 | 3.741%
6417 | 20-70 | -70.1149 | 20.4273 | 712.094 | 170.1143 | 199.2861 | 242.5709 | 281.4645 | 326.6016 | 3.634%
6418 | 20-70.5 | -70.3862 | 20.4273 | 727.7272 | 168.8665 | 198.1868 | 241.1401 | 279.7239 | 324.4894 | 3.525%
6419 | 20-70.5 | -70.6575 | 20.4273 | 743.4587 | 167.8747 | 197.2581 | 239.9322 | 278.2543 | 322.7055 | 3.439%
6420 | 20-71 | -70.9288 | 20.4273 | 759.2822 | 167.1876 | 196.5577 | 239.0463 | 277.1971 | 321.4445 | 3.378%
6421 | 20-71 | -71.2001 | 20.4273 | 775.1923 | 166.7816 | 196.0722 | 238.4677 | 276.5364 | 320.6901 | 3.34%
6422 | 20-71.5 | -71.4715 | 20.4273 | 791.1835 | 166.3466 | 195.544 | 237.8163 | 275.7729 | 319.7951 | 3.3%
6423 | 20-71.5 | -71.7428 | 20.4273 | 807.251 | 166.0519 | 195.1768 | 237.3964 | 275.3093 | 319.2844 | 3.272%
6424 | 20-72 | -72.0141 | 20.4273 | 823.3903 | 165.9221 | 194.9579 | 237.1885 | 275.119 | 319.1225 | 3.256%
6425 | 20-72.5 | -72.2854 | 20.4273 | 839.5973 | 165.7401 | 194.6935 | 236.8936 | 274.7999 | 318.7781 | 3.237%
6426 | 20-72.5 | -72.5568 | 20.4273 | 855.8681 | 165.4012 | 194.3365 | 236.461 | 274.299 | 318.1976 | 3.208%
6427 | 20-73 | -72.8281 | 20.4273 | 872.199 | 165.0191 | 193.9595 | 235.9866 | 273.7344 | 317.5256 | 3.176%
6428 | 20-73 | -73.0994 | 20.4273 | 888.5868 | 165.0249 | 193.8446 | 235.8397 | 273.557 | 317.3112 | 3.175%
6429 | 20-73.5 | -73.3707 | 20.4273 | 905.0282 | 165.4798 | 194.1503 | 236.2712 | 274.1094 | 318.0116 | 3.208%
6430 | 20-73.5 | -73.642 | 20.4273 | 921.5205 | 166.1803 | 194.6864 | 237.016 | 275.0543 | 319.201 | 3.261%
6431 | 20-74 | -73.9134 | 20.4273 | 938.0608 | 166.6049 | 194.8878 | 237.2758 | 275.3676 | 319.5776 | 3.293%
6432 | 20-74 | -74.1847 | 20.4273 | 954.6466 | 166.2738 | 194.5639 | 236.807 | 274.7586 | 318.7958 | 3.267%
6433 | 20-74.5 | -74.456 | 20.4273 | 971.2756 | 165.3531 | 193.8211 | 235.751 | 273.4012 | 317.0688 | 3.198%
6434 | 20-74.5 | -74.7273 | 20.4273 | 987.9456 | 164.212 | 192.9138 | 234.4447 | 271.7094 | 314.9025 | 3.115%
6435 | 20-75 | -74.9986 | 20.4273 | 1004.6544 | 163.1752 | 192.1028 | 233.2741 | 270.1913 | 312.9566 | 3.04%
6436 | 20-75.5 | -75.27 | 20.4273 | 1021.4002 | 162.3364 | 191.4229 | 232.2738 | 268.8799 | 311.2608 | 2.981%
6437 | 20-75.5 | -75.5413 | 20.4273 | 1038.1811 | 161.8877 | 190.9765 | 231.5703 | 267.9233 | 309.9888 | 2.951%
6438 | 20-76 | -75.8126 | 20.4273 | 1054.9954 | 161.9488 | 190.9654 | 231.4754 | 267.7426 | 309.6981 | 2.958%
6439 | 20-76 | -76.0839 | 20.4273 | 1071.8415 | 162.33 | 191.2161 | 231.7383 | 268.0114 | 309.9687 | 2.988%
6440 | 20-76.5 | -76.3553 | 20.4273 | 1088.7179 | 162.7061 | 191.4052 | 231.8993 | 268.1384 | 310.0474 | 3.018%
6441 | 20-76.5 | -76.6266 | 20.4273 | 1105.6232 | 162.6397 | 191.2587 | 231.599 | 267.6838 | 309.3978 | 3.016%
6442 | 20-77 | -76.8979 | 20.4273 | 1122.5559 | 162.2832 | 190.8228 | 230.8859 | 266.6973 | 308.0693 | 2.992%
6443 | 20-77 | -77.1692 | 20.4273 | 1139.5149 | 161.9122 | 190.344 | 230.0923 | 265.5922 | 306.5741 | 2.967%
6444 | 20-77.5 | -77.4405 | 20.4273 | 1156.499 | 162.0366 | 190.3807 | 230.0068 | 265.3798 | 306.1975 | 2.981%
6445 | 20-77.5 | -77.7119 | 20.4273 | 1173.507 | 162.832 | 190.9052 | 230.578 | 265.9843 | 306.8318 | 3.045%
6446 | 20-78 | -77.9832 | 20.4273 | 1190.5379 | 164.092 | 191.791 | 231.6263 | 267.1745 | 308.1825 | 3.147%
6447 | 20-78.5 | -78.2545 | 20.4273 | 1207.5907 | 165.447 | 192.8113 | 232.8542 | 268.5867 | 309.8065 | 3.262%
6448 | 20-78.5 | -78.5258 | 20.4273 | 1224.6644 | 166.8183 | 193.8782 | 234.133 | 270.0529 | 311.4874 | 3.383%
6449 | 20-79 | -78.7971 | 20.4273 | 1241.7581 | 168.066 | 194.8931 | 235.3344 | 271.4174 | 313.0365 | 3.499%
6450 | 20-79 | -79.0685 | 20.4273 | 1258.871 | 169.0331 | 195.7939 | 236.3924 | 272.6116 | 314.3837 | 3.594%
6451 | 20-79.5 | -79.3398 | 20.4273 | 1276.0022 | 169.7881 | 196.5036 | 237.1797 | 273.4582 | 315.2885 | 3.673%
6452 | 20-79.5 | -79.6111 | 20.4273 | 1293.151 | 170.4925 | 197.1541 | 237.8779 | 274.1861 | 316.0379 | 3.75%
6453 | 20-80 | -79.8824 | 20.4273 | 1310.3167 | 171.3541 | 198.0009 | 238.8555 | 275.2741 | 317.2467 | 3.843%
6454 | 20-80 | -80.1537 | 20.4273 | 1327.4986 | 172.3534 | 198.9985 | 240.041 | 276.6247 | 318.7849 | 3.951%
6455 | 20-80.5 | -80.4251 | 20.4273 | 1344.6959 | 173.4182 | 200.0792 | 241.3468 | 278.1312 | 320.523 | 4.068%
6456 | 20-80.5 | -80.6964 | 20.4273 | 1361.9082 | 174.4748 | 201.1927 | 242.7122 | 279.7242 | 322.3812 | 4.187%
6457 | 20-81 | -80.9677 | 20.4273 | 1379.1348 | 175.437 | 202.2325 | 243.9832 | 281.2034 | 324.1025 | 4.298%
6458 | 20-81 | -81.239 | 20.4273 | 1396.375 | 176.279 | 203.1767 | 245.1341 | 282.5401 | 325.655 | 4.398%
6459 | 20-81.5 | -81.5104 | 20.4273 | 1413.6285 | 177.0238 | 204.0441 | 246.1948 | 283.7749 | 327.0923 | 4.488%
6460 | 20-82 | -81.7817 | 20.4273 | 1430.8946 | 177.6483 | 204.7652 | 247.0666 | 284.7815 | 328.2544 | 4.566%
6461 | 20-82 | -82.053 | 20.4273 | 1448.1729 | 178.203 | 205.4084 | 247.8489 | 285.6884 | 329.3057 | 4.635%
6462 | 20-82.5 | -82.3243 | 20.4273 | 1465.463 | 178.7379 | 206.0396 | 248.634 | 286.614 | 330.3963 | 4.701%
6463 | 20-82.5 | -82.5956 | 20.4273 | 1482.7642 | 179.203 | 206.5874 | 249.3134 | 287.4131 | 331.336 | 4.76%
6464 | 20-83 | -82.867 | 20.4273 | 1500.0764 | 179.6332 | 207.1071 | 249.9789 | 288.2136 | 332.2972 | 4.812%
6465 | 20-83 | -83.1383 | 20.4273 | 1517.3989 | 180.0557 | 207.641 | 250.698 | 289.1079 | 333.4037 | 4.861%
6466 | 20-83.5 | -83.4096 | 20.4273 | 1534.7315 | 180.3752 | 208.0602 | 251.2848 | 289.8553 | 334.3471 | 4.895%
6467 | 20-83.5 | -83.6809 | 20.4273 | 1552.0737 | 180.6079 | 208.3897 | 251.7805 | 290.5125 | 335.2038 | 4.917%
6468 | 20-84 | -83.9522 | 20.4273 | 1569.4252 | 180.7666 | 208.6486 | 252.2148 | 291.1196 | 336.0268 | 4.927%
6469 | 20-84 | -84.2236 | 20.4273 | 1586.7857 | 180.7585 | 208.7102 | 252.4027 | 291.4358 | 336.5066 | 4.915%
6470 | 20-84.5 | -84.4949 | 20.4273 | 1604.1548 | 180.6525 | 208.6671 | 252.4776 | 291.6334 | 336.8632 | 4.889%
6471 | 20-85 | -84.7662 | 20.4273 | 1621.5322 | 180.4747 | 208.5567 | 252.496 | 291.7877 | 337.1953 | 4.853%
6472 | 20-85 | -85.0375 | 20.4273 | 1638.9176 | 180.0663 | 208.179 | 252.19 | 291.5666 | 337.0929 | 4.787%
6473 | 20-85.5 | -85.3089 | 20.4273 | 1656.3107 | 179.4732 | 207.5945 | 251.6443 | 291.0779 | 336.6929 | 4.699%
6474 | 20-85.5 | -85.5802 | 20.4273 | 1673.7113 | 178.6555 | 206.8122 | 250.8726 | 290.3404 | 336.02 | 4.585%
6475 | 20-86 | -85.8515 | 20.4273 | 1691.119 | 177.3959 | 205.5859 | 249.5078 | 288.8685 | 334.4411 | 4.428%
6476 | 20-86 | -86.1228 | 20.4273 | 1708.5336 | 175.5814 | 203.9847 | 247.6593 | 286.8115 | 332.1558 | 4.22%
6477 | 20-86.5 | -86.3941 | 20.4273 | 1725.9548 | 173.2741 | 202.0343 | 245.3684 | 284.2263 | 329.2407 | 3.975%
6478 | 20-86.5 | -86.6655 | 20.4273 | 1743.3825 | 170.687 | 199.8494 | 242.764 | 281.2529 | 325.8473 | 3.718%
6479 | 20-87 | -86.9368 | 20.4273 | 1760.8164 | 167.9163 | 197.5491 | 240.0192 | 278.1169 | 322.2656 | 3.461%
6480 | 20-87 | -87.2081 | 20.4273 | 1778.2562 | 164.9761 | 195.1335 | 237.137 | 274.8224 | 318.5011 | 3.208%
6481 | 20-87.5 | -87.4794 | 20.4273 | 1795.7018 | 161.828 | 192.5218 | 234.0164 | 271.2264 | 314.3579 | 2.957%
6482 | 20-88 | -87.7507 | 20.4273 | 1813.1529 | 158.5569 | 189.8137 | 230.8256 | 267.5498 | 310.122 | 2.716%
6483 | 20-88 | -88.0221 | 20.4273 | 1830.6094 | 155.1935 | 187.0193 | 227.5829 | 263.8139 | 305.8184 | 2.487%
6484 | 20-88.5 | -88.2934 | 20.4273 | 1848.071 | 151.8227 | 184.1848 | 224.3292 | 260.0505 | 301.4656 | 2.276%
6485 | 20-88.5 | -88.5647 | 20.4273 | 1865.5376 | 148.6076 | 181.5056 | 221.3201 | 256.579 | 297.4607 | 2.092%
6486 | 20-89 | -88.836 | 20.4273 | 1883.0089 | 145.5683 | 179.0167 | 218.5594 | 253.3992 | 293.7982 | 1.932%
6487 | 20-89 | -89.1074 | 20.4273 | 1900.4849 | 142.7859 | 176.8167 | 216.0609 | 250.5102 | 290.4576 | 1.798%
6488 | 20-89.5 | -89.3787 | 20.4273 | 1917.9653 | 140.4841 | 175.1299 | 214.1861 | 248.3958 | 288.0749 | 1.696%
6489 | 20-89.5 | -89.65 | 20.4273 | 1935.45 | 138.7695 | 173.861 | 212.8376 | 246.9222 | 286.4709 | 1.624%
6490 | 20-90 | -89.9213 | 20.4273 | 1952.9389 | 137.4441 | 172.8503 | 211.7782 | 245.7656 | 285.2128 | 1.57%
6491 | 20-90 | -90.1926 | 20.4273 | 1970.4317 | 136.303 | 171.9745 | 210.8747 | 244.7849 | 284.1528 | 1.525%
6492 | 20-90.5 | -90.464 | 20.4273 | 1987.9283 | 135.3262 | 171.205 | 210.1008 | 243.9485 | 283.2532 | 1.488%
6493 | 20-90.5 | -90.7353 | 20.4273 | 2005.4286 | 134.467 | 170.4956 | 209.4107 | 243.1994 | 282.4435 | 1.456%
6494 | 21-50 | -50.0371 | 20.6987 | 785.7072 | 136.931 | 173.5832 | 207.4919 | 237.0303 | 270.775 | 1.567%
6495 | 21-50.5 | -50.3084 | 20.6987 | 769.9758 | 138.3803 | 174.6521 | 208.6743 | 238.4704 | 272.5222 | 1.63%
6496 | 21-50.5 | -50.5797 | 20.6987 | 754.3365 | 139.7611 | 175.6279 | 209.8082 | 239.8604 | 274.2188 | 1.691%
6497 | 21-51 | -50.851 | 20.6987 | 738.7949 | 141.108 | 176.5447 | 210.9328 | 241.2534 | 275.9343 | 1.753%
6498 | 21-51 | -51.1224 | 20.6987 | 723.3576 | 142.466 | 177.4434 | 212.0976 | 242.7147 | 277.7537 | 1.817%
6499 | 21-51.5 | -51.3937 | 20.6987 | 708.0313 | 143.7578 | 178.2705 | 213.2046 | 244.1064 | 279.4896 | 1.879%
6500 | 21-51.5 | -51.665 | 20.6987 | 692.8234 | 145.0341 | 179.0736 | 214.3054 | 245.4956 | 281.2278 | 1.942%
6501 | 21-52 | -51.9363 | 20.6987 | 677.7421 | 146.3422 | 179.8943 | 215.4486 | 246.9449 | 283.0484 | 2.009%
6502 | 21-52 | -52.2077 | 20.6987 | 662.7958 | 147.6016 | 180.6823 | 216.5404 | 248.3247 | 284.7771 | 2.075%
6503 | 21-52.5 | -52.479 | 20.6987 | 647.9941 | 148.8561 | 181.4673 | 217.631 | 249.7054 | 286.5097 | 2.143%
6504 | 21-53 | -52.7503 | 20.6987 | 633.347 | 150.1349 | 182.2699 | 218.7553 | 251.1358 | 288.312 | 2.213%
6505 | 21-53 | -53.0216 | 20.6987 | 618.8656 | 151.3656 | 183.0367 | 219.8218 | 252.4869 | 290.0083 | 2.283%
6506 | 21-53.5 | -53.2929 | 20.6987 | 604.5619 | 152.6067 | 183.8046 | 220.8802 | 253.8206 | 291.6756 | 2.356%
6507 | 21-53.5 | -53.5643 | 20.6987 | 590.4487 | 153.8801 | 184.5878 | 221.9503 | 255.1622 | 293.3453 | 2.433%
6508 | 21-54 | -53.8356 | 20.6987 | 576.5401 | 155.085 | 185.3185 | 222.9297 | 256.3755 | 294.8405 | 2.507%
6509 | 21-54 | -54.1069 | 20.6987 | 562.8513 | 156.2727 | 186.0321 | 223.8754 | 257.5386 | 296.2649 | 2.583%
6510 | 21-54.5 | -54.3782 | 20.6987 | 549.3988 | 157.4528 | 186.7355 | 224.7982 | 258.6667 | 297.639 | 2.661%
6511 | 21-54.5 | -54.6495 | 20.6987 | 536.2004 | 158.5159 | 187.3588 | 225.599 | 259.6318 | 298.7998 | 2.733%
6512 | 21-55 | -54.9209 | 20.6987 | 523.2753 | 159.5438 | 187.9632 | 226.3783 | 260.5738 | 299.9357 | 2.804%
6513 | 21-55 | -55.1922 | 20.6987 | 510.6443 | 160.5474 | 188.5594 | 227.1534 | 261.5155 | 301.0768 | 2.876%
6514 | 21-55.5 | -55.4635 | 20.6987 | 498.3298 | 161.4615 | 189.1019 | 227.8473 | 262.3497 | 302.0777 | 2.943%
6515 | 21-55.5 | -55.7348 | 20.6987 | 486.3559 | 162.357 | 189.6519 | 228.5556 | 263.2048 | 303.108 | 3.01%
6516 | 21-56 | -56.0061 | 20.6987 | 474.7483 | 163.2237 | 190.2131 | 229.2812 | 264.0835 | 304.1696 | 3.076%
6517 | 21-56.5 | -56.2775 | 20.6987 | 463.5347 | 164.0168 | 190.7395 | 229.9475 | 264.8786 | 305.1172 | 3.139%
6518 | 21-56.5 | -56.5488 | 20.6987 | 452.7443 | 164.7963 | 191.2889 | 230.649 | 265.7208 | 306.1267 | 3.202%
6519 | 21-57 | -56.8201 | 20.6987 | 442.4081 | 165.5442 | 191.8571 | 231.3796 | 266.6022 | 307.1878 | 3.265%
6520 | 21-57 | -57.0914 | 20.6987 | 432.5587 | 166.2039 | 192.3883 | 232.0602 | 267.4211 | 308.1715 | 3.321%
6521 | 21-57.5 | -57.3628 | 20.6987 | 423.2301 | 166.8629 | 192.9527 | 232.7938 | 268.3126 | 309.2518 | 3.378%
6522 | 21-57.5 | -57.6341 | 20.6987 | 414.4575 | 167.498 | 193.5376 | 233.5617 | 269.2521 | 310.3975 | 3.434%
6523 | 21-58 | -57.9054 | 20.6987 | 406.277 | 168.0506 | 194.0821 | 234.2768 | 270.127 | 311.4644 | 3.484%
6524 | 21-58 | -58.1767 | 20.6987 | 398.7249 | 168.6156 | 194.6588 | 235.0408 | 271.067 | 312.6165 | 3.536%
6525 | 21-58.5 | -58.448 | 20.6987 | 391.8377 | 169.1646 | 195.248 | 235.8221 | 272.0292 | 313.7967 | 3.587%
6526 | 21-58.5 | -58.7194 | 20.6987 | 385.651 | 169.6487 | 195.7922 | 236.5328 | 272.8958 | 314.8502 | 3.633%
6527 | 21-59 | -58.9907 | 20.6987 | 380.199 | 170.1231 | 196.3434 | 237.2565 | 273.7812 | 315.9301 | 3.679%
6528 | 21-59.5 | -59.262 | 20.6987 | 375.5137 | 170.576 | 196.8842 | 237.9686 | 274.654 | 316.9964 | 3.724%
6529 | 21-59.5 | -59.5333 | 20.6987 | 371.6241 | 170.9849 | 197.3801 | 238.6227 | 275.4569 | 317.9785 | 3.764%
6530 | 21-60 | -59.8046 | 20.6987 | 368.5555 | 171.3855 | 197.8845 | 239.3058 | 276.3098 | 319.0373 | 3.803%
6531 | 21-60 | -60.076 | 20.6987 | 366.3284 | 171.7637 | 198.3725 | 239.9782 | 277.158 | 320.0999 | 3.839%
6532 | 21-60.5 | -60.3473 | 20.6987 | 364.9583 | 172.104 | 198.8125 | 240.5857 | 277.9254 | 321.0623 | 3.871%
6533 | 21-60.5 | -60.6186 | 20.6987 | 364.4548 | 172.4549 | 199.2686 | 241.2191 | 278.7282 | 322.072 | 3.905%
6534 | 21-61 | -60.8899 | 20.6987 | 364.8216 | 172.7938 | 199.7087 | 241.8294 | 279.5014 | 323.0438 | 3.937%
6535 | 21-61 | -61.1613 | 20.6987 | 366.056 | 173.106 | 200.1104 | 242.3813 | 280.1964 | 323.9132 | 3.967%
6536 | 21-61.5 | -61.4326 | 20.6987 | 368.1493 | 173.4436 | 200.5454 | 242.9797 | 280.9507 | 324.8575 | 4%
6537 | 21-61.5 | -61.7039 | 20.6987 | 371.0869 | 173.7718 | 200.9638 | 243.5489 | 281.6633 | 325.7443 | 4.033%
6538 | 21-62 | -61.9752 | 20.6987 | 374.849 | 174.0723 | 201.3389 | 244.0476 | 282.2786 | 326.5003 | 4.063%
6539 | 21-62 | -62.2465 | 20.6987 | 379.4111 | 174.3923 | 201.7403 | 244.584 | 282.9426 | 327.3187 | 4.096%
6540 | 21-62.5 | -62.5179 | 20.6987 | 384.7447 | 174.6969 | 202.1216 | 245.0925 | 283.5712 | 328.0924 | 4.127%
6541 | 21-63 | -62.7892 | 20.6987 | 390.8181 | 174.9739 | 202.4657 | 245.5474 | 284.1303 | 328.777 | 4.156%
6542 | 21-63 | -63.0605 | 20.6987 | 397.5976 | 175.2598 | 202.8207 | 246.0166 | 284.7069 | 329.4829 | 4.186%
6543 | 21-63.5 | -63.3318 | 20.6987 | 405.0476 | 175.5256 | 203.1441 | 246.4342 | 285.212 | 330.0927 | 4.214%
6544 | 21-63.5 | -63.6031 | 20.6987 | 413.1317 | 175.7712 | 203.4379 | 246.8054 | 285.6546 | 330.6198 | 4.242%
6545 | 21-64 | -63.8745 | 20.6987 | 421.8137 | 176.0287 | 203.7518 | 247.2118 | 286.1473 | 331.2158 | 4.269%
6546 | 21-64 | -64.1458 | 20.6987 | 431.0573 | 176.2641 | 204.0415 | 247.5909 | 286.6102 | 331.7794 | 4.295%
6547 | 21-64.5 | -64.4171 | 20.6987 | 440.8271 | 176.4812 | 204.3157 | 247.9605 | 287.0703 | 332.3496 | 4.317%
6548 | 21-64.5 | -64.6884 | 20.6987 | 451.089 | 176.7087 | 204.6167 | 248.3862 | 287.6162 | 333.0432 | 4.339%
6549 | 21-65 | -64.9598 | 20.6987 | 461.8101 | 176.899 | 204.8734 | 248.7565 | 288.0966 | 333.6594 | 4.357%
6550 | 21-65 | -65.2311 | 20.6987 | 472.9592 | 177.0652 | 205.105 | 249.1006 | 288.5504 | 334.2492 | 4.372%
6551 | 21-65.5 | -65.5024 | 20.6987 | 484.5067 | 177.2422 | 205.3624 | 249.4975 | 289.0844 | 334.9538 | 4.387%
6552 | 21-66 | -65.7737 | 20.6987 | 496.4248 | 177.3772 | 205.5692 | 249.8298 | 289.5406 | 335.5652 | 4.397%
6553 | 21-66 | -66.045 | 20.6987 | 508.6874 | 177.4862 | 205.7464 | 250.1271 | 289.957 | 336.1312 | 4.404%
6554 | 21-66.5 | -66.3164 | 20.6987 | 521.2702 | 177.5977 | 205.934 | 250.4491 | 290.4128 | 336.7553 | 4.41%
6555 | 21-66.5 | -66.5877 | 20.6987 | 534.1505 | 177.6661 | 206.07 | 250.7057 | 290.7905 | 337.2863 | 4.411%
6556 | 21-67 | -66.859 | 20.6987 | 547.3073 | 177.7069 | 206.1785 | 250.9363 | 291.1445 | 337.7974 | 4.409%
6557 | 21-67 | -67.1303 | 20.6987 | 560.7211 | 177.7378 | 206.286 | 251.1825 | 291.5314 | 338.3637 | 4.405%
6558 | 21-67.5 | -67.4016 | 20.6987 | 574.3738 | 177.7074 | 206.3152 | 251.3216 | 291.7838 | 338.7622 | 4.394%
6559 | 21-67.5 | -67.673 | 20.6987 | 588.2489 | 177.6388 | 206.2953 | 251.3936 | 291.9518 | 339.0551 | 4.379%
6560 | 21-68 | -67.9443 | 20.6987 | 602.3309 | 177.5509 | 206.2522 | 251.436 | 292.0844 | 339.3059 | 4.363%
6561 | 21-68 | -68.2156 | 20.6987 | 616.6056 | 177.2934 | 205.9947 | 251.1647 | 291.8066 | 339.0267 | 4.331%
6562 | 21-68.5 | -68.4869 | 20.6987 | 631.0598 | 176.8574 | 205.5715 | 250.6588 | 291.2279 | 338.365 | 4.283%
6563 | 21-69 | -68.7583 | 20.6987 | 645.6816 | 176.2476 | 205.0157 | 249.9727 | 290.4238 | 337.4233 | 4.219%
6564 | 21-69 | -69.0296 | 20.6987 | 660.4597 | 175.5616 | 204.3689 | 249.1544 | 289.4478 | 336.2604 | 4.148%
6565 | 21-69.5 | -69.3009 | 20.6987 | 675.3839 | 174.8558 | 203.7056 | 248.3212 | 288.4588 | 335.0877 | 4.077%
6566 | 21-69.5 | -69.5722 | 20.6987 | 690.4447 | 174.147 | 203.0501 | 247.5138 | 287.514 | 333.9827 | 4.005%
6567 | 21-70 | -69.8435 | 20.6987 | 705.6332 | 173.2749 | 202.2414 | 246.4853 | 286.2825 | 332.51 | 3.92%
6568 | 21-70 | -70.1149 | 20.6987 | 720.9414 | 172.2899 | 201.3412 | 245.3287 | 284.8878 | 330.8315 | 3.827%
6569 | 21-70.5 | -70.3862 | 20.6987 | 736.3617 | 171.2225 | 200.3758 | 244.0843 | 283.384 | 329.0178 | 3.729%
6570 | 21-70.5 | -70.6575 | 20.6987 | 751.8873 | 170.3156 | 199.4994 | 242.9473 | 282.0032 | 327.3445 | 3.646%
6571 | 21-71 | -70.9288 | 20.6987 | 767.5117 | 169.6374 | 198.7944 | 242.0521 | 280.932 | 326.0638 | 3.584%
6572 | 21-71 | -71.2001 | 20.6987 | 783.229 | 169.174 | 198.2563 | 241.3964 | 280.1706 | 325.1797 | 3.539%
6573 | 21-71.5 | -71.4715 | 20.6987 | 799.0337 | 168.6788 | 197.6698 | 240.6602 | 279.2967 | 324.1426 | 3.493%
6574 | 21-71.5 | -71.7428 | 20.6987 | 814.9205 | 168.3021 | 197.2296 | 240.1367 | 278.6999 | 323.4624 | 3.457%
6575 | 21-72 | -72.0141 | 20.6987 | 830.8849 | 168.0731 | 196.9261 | 239.8104 | 278.3589 | 323.1104 | 3.432%
6576 | 21-72.5 | -72.2854 | 20.6987 | 846.9224 | 167.808 | 196.5858 | 239.4098 | 277.9056 | 322.597 | 3.406%
6577 | 21-72.5 | -72.5568 | 20.6987 | 863.0288 | 167.41 | 196.1702 | 238.8961 | 277.3021 | 321.8877 | 3.37%
6578 | 21-73 | -72.8281 | 20.6987 | 879.2003 | 166.978 | 195.7417 | 238.3512 | 276.6488 | 321.1049 | 3.333%
6579 | 21-73 | -73.0994 | 20.6987 | 895.4335 | 166.8898 | 195.5422 | 238.0903 | 276.3297 | 320.7148 | 3.324%
6580 | 21-73.5 | -73.3707 | 20.6987 | 911.7249 | 167.2119 | 195.7392 | 238.3761 | 276.7012 | 321.1918 | 3.348%
6581 | 21-73.5 | -73.642 | 20.6987 | 928.0714 | 167.7485 | 196.1477 | 238.9498 | 277.4336 | 322.1187 | 3.39%
6582 | 21-74 | -73.9134 | 20.6987 | 944.4702 | 168.0079 | 196.2195 | 239.035 | 277.5297 | 322.2262 | 3.409%
6583 | 21-74 | -74.1847 | 20.6987 | 960.9185 | 167.571 | 195.8152 | 238.4624 | 276.7949 | 321.2919 | 3.375%
6584 | 21-74.5 | -74.456 | 20.6987 | 977.4139 | 166.6075 | 195.041 | 237.3725 | 275.4019 | 319.5278 | 3.3%
6585 | 21-74.5 | -74.7273 | 20.6987 | 993.9538 | 165.4832 | 194.1441 | 236.0916 | 273.7504 | 317.4209 | 3.216%
6586 | 21-75 | -74.9986 | 20.6987 | 1010.5362 | 164.4587 | 193.3428 | 234.9454 | 272.2715 | 315.533 | 3.14%
6587 | 21-75.5 | -75.27 | 20.6987 | 1027.1589 | 163.6239 | 192.6673 | 233.9624 | 270.9904 | 313.8841 | 3.08%
6588 | 21-75.5 | -75.5413 | 20.6987 | 1043.8199 | 163.1593 | 192.2085 | 233.2533 | 270.0358 | 312.6238 | 3.047%
6589 | 21-76 | -75.8126 | 20.6987 | 1060.5174 | 163.1511 | 192.1474 | 233.1026 | 269.7947 | 312.2677 | 3.049%
6590 | 21-76 | -76.0839 | 20.6987 | 1077.2497 | 163.4046 | 192.3007 | 233.2449 | 269.9217 | 312.3719 | 3.07%
6591 | 21-76.5 | -76.3553 | 20.6987 | 1094.0152 | 163.5977 | 192.341 | 233.214 | 269.8164 | 312.1698 | 3.086%
6592 | 21-76.5 | -76.6266 | 20.6987 | 1110.8122 | 163.3321 | 192.0349 | 232.7046 | 269.1064 | 311.2092 | 3.069%
6593 | 21-77 | -76.8979 | 20.6987 | 1127.6394 | 162.8064 | 191.4555 | 231.8021 | 267.8871 | 309.5958 | 3.032%
6594 | 21-77 | -77.1692 | 20.6987 | 1144.4954 | 162.3393 | 190.8758 | 230.8743 | 266.6166 | 307.8972 | 2.999%
6595 | 21-77.5 | -77.4405 | 20.6987 | 1161.3789 | 162.3902 | 190.8397 | 230.6919 | 266.2845 | 307.3733 | 3.007%
6596 | 21-77.5 | -77.7119 | 20.6987 | 1178.2887 | 163.1122 | 191.2899 | 231.162 | 266.7624 | 307.8501 | 3.066%
6597 | 21-78 | -77.9832 | 20.6987 | 1195.2235 | 164.2782 | 192.0726 | 232.0678 | 267.7724 | 308.9747 | 3.161%
6598 | 21-78.5 | -78.2545 | 20.6987 | 1212.1825 | 165.5136 | 192.9635 | 233.1165 | 268.9579 | 310.3141 | 3.266%
6599 | 21-78.5 | -78.5258 | 20.6987 | 1229.1644 | 166.7501 | 193.8888 | 234.1992 | 270.1763 | 311.684 | 3.375%
6600 | 21-79 | -78.7971 | 20.6987 | 1246.1683 | 167.8685 | 194.7648 | 235.2083 | 271.2974 | 312.9278 | 3.479%
6601 | 21-79 | -79.0685 | 20.6987 | 1263.1934 | 168.7202 | 195.5371 | 236.0878 | 272.2654 | 313.9906 | 3.564%
6602 | 21-79.5 | -79.3398 | 20.6987 | 1280.2386 | 169.3728 | 196.1274 | 236.7087 | 272.9007 | 314.6293 | 3.633%
6603 | 21-79.5 | -79.6111 | 20.6987 | 1297.3033 | 169.9942 | 196.6772 | 237.2658 | 273.4492 | 315.1526 | 3.701%
6604 | 21-80 | -79.8824 | 20.6987 | 1314.3865 | 170.8077 | 197.4558 | 238.148 | 274.4156 | 316.208 | 3.789%
6605 | 21-80 | -80.1537 | 20.6987 | 1331.4876 | 171.8238 | 198.4397 | 239.3131 | 275.7392 | 317.7112 | 3.897%
6606 | 21-80.5 | -80.4251 | 20.6987 | 1348.6058 | 172.935 | 199.5454 | 240.6525 | 277.2876 | 319.5011 | 4.017%
6607 | 21-80.5 | -80.6964 | 20.6987 | 1365.7404 | 174.0176 | 200.6918 | 242.0641 | 278.9393 | 321.4334 | 4.137%
6608 | 21-81 | -80.9677 | 20.6987 | 1382.8908 | 174.9716 | 201.7218 | 243.3224 | 280.4032 | 323.1363 | 4.246%
6609 | 21-81 | -81.239 | 20.6987 | 1400.0564 | 175.7802 | 202.6237 | 244.4162 | 281.6689 | 324.601 | 4.342%
6610 | 21-81.5 | -81.5104 | 20.6987 | 1417.2366 | 176.4882 | 203.4449 | 245.4154 | 282.8279 | 325.9451 | 4.427%
6611 | 21-82 | -81.7817 | 20.6987 | 1434.4308 | 177.0954 | 204.1378 | 246.2494 | 283.7875 | 327.0493 | 4.502%
6612 | 21-82 | -82.053 | 20.6987 | 1451.6385 | 177.6489 | 204.763 | 247.0054 | 284.6604 | 328.0571 | 4.571%
6613 | 21-82.5 | -82.3243 | 20.6987 | 1468.8591 | 178.182 | 205.3755 | 247.7609 | 285.5456 | 329.0939 | 4.637%
6614 | 21-82.5 | -82.5956 | 20.6987 | 1486.0922 | 178.6702 | 205.9392 | 248.4564 | 286.3605 | 330.0486 | 4.698%
6615 | 21-83 | -82.867 | 20.6987 | 1503.3373 | 179.1562 | 206.5185 | 249.1965 | 287.2494 | 331.1144 | 4.757%
6616 | 21-83 | -83.1383 | 20.6987 | 1520.594 | 179.6679 | 207.1562 | 250.0507 | 288.308 | 332.42 | 4.816%
6617 | 21-83.5 | -83.4096 | 20.6987 | 1537.8618 | 180.0798 | 207.6872 | 250.7837 | 289.2335 | 333.5799 | 4.861%
6618 | 21-83.5 | -83.6809 | 20.6987 | 1555.1403 | 180.3884 | 208.1093 | 251.3991 | 290.0356 | 334.6116 | 4.892%
6619 | 21-84 | -83.9522 | 20.6987 | 1572.4292 | 180.5989 | 208.4298 | 251.9105 | 290.7343 | 335.5433 | 4.908%
6620 | 21-84 | -84.2236 | 20.6987 | 1589.728 | 180.6165 | 208.5188 | 252.1282 | 291.0818 | 336.0558 | 4.9%
6621 | 21-84.5 | -84.4949 | 20.6987 | 1607.0364 | 180.5492 | 208.5201 | 252.2562 | 291.3403 | 336.4823 | 4.88%
6622 | 21-85 | -84.7662 | 20.6987 | 1624.3541 | 180.4381 | 208.4903 | 252.3782 | 291.6196 | 336.9649 | 4.851%
6623 | 21-85 | -85.0375 | 20.6987 | 1641.6807 | 180.1224 | 208.2254 | 252.2174 | 291.5737 | 337.0736 | 4.797%
6624 | 21-85.5 | -85.3089 | 20.6987 | 1659.0158 | 179.6308 | 207.764 | 251.83 | 291.276 | 336.9034 | 4.72%
6625 | 21-85.5 | -85.5802 | 20.6987 | 1676.3593 | 178.9192 | 207.1108 | 251.2244 | 290.7389 | 336.4713 | 4.618%
6626 | 21-86 | -85.8515 | 20.6987 | 1693.7107 | 177.8184 | 206.0582 | 250.0908 | 289.5523 | 335.2431 | 4.476%
6627 | 21-86 | -86.1228 | 20.6987 | 1711.0699 | 176.2004 | 204.6392 | 248.4879 | 287.801 | 333.3365 | 4.287%
6628 | 21-86.5 | -86.3941 | 20.6987 | 1728.4365 | 174.1131 | 202.8684 | 246.4405 | 285.52 | 330.7995 | 4.058%
6629 | 21-86.5 | -86.6655 | 20.6987 | 1745.8102 | 171.7287 | 200.8288 | 244.0323 | 282.7914 | 327.7099 | 3.815%
6630 | 21-87 | -86.9368 | 20.6987 | 1763.1909 | 169.1701 | 198.6764 | 241.4872 | 279.9043 | 324.4371 | 3.57%
6631 | 21-87 | -87.2081 | 20.6987 | 1780.5783 | 166.4542 | 196.4174 | 238.8137 | 276.8696 | 320.9947 | 3.328%
6632 | 21-87.5 | -87.4794 | 20.6987 | 1797.9721 | 163.5403 | 193.9774 | 235.9006 | 273.5297 | 317.1664 | 3.086%
6633 | 21-88 | -87.7507 | 20.6987 | 1815.3721 | 160.5134 | 191.457 | 232.9213 | 270.1127 | 313.2486 | 2.853%
6634 | 21-88 | -88.0221 | 20.6987 | 1832.7781 | 157.397 | 188.8629 | 229.8923 | 266.6382 | 309.2638 | 2.63%
6635 | 21-88.5 | -88.2934 | 20.6987 | 1850.1899 | 154.2667 | 186.232 | 226.8458 | 263.1273 | 305.2181 | 2.423%
6636 | 21-88.5 | -88.5647 | 20.6987 | 1867.6073 | 151.2881 | 183.7629 | 224.0465 | 259.9134 | 301.5286 | 2.242%
6637 | 21-89 | -88.836 | 20.6987 | 1885.0301 | 148.479 | 181.4858 | 221.4949 | 256.9923 | 298.1852 | 2.083%
6638 | 21-89 | -89.1074 | 20.6987 | 1902.4581 | 145.9114 | 179.4853 | 219.1912 | 254.3466 | 295.1467 | 1.95%
6639 | 21-89.5 | -89.3787 | 20.6987 | 1919.8911 | 143.7619 | 177.9466 | 217.4402 | 252.3848 | 292.9514 | 1.847%
6640 | 21-89.5 | -89.65 | 20.6987 | 1937.3289 | 142.1236 | 176.7715 | 216.1436 | 250.9727 | 291.4201 | 1.773%
6641 | 21-90 | -89.9213 | 20.6987 | 1954.7714 | 140.8017 | 175.7952 | 215.061 | 249.7817 | 290.1135 | 1.714%
6642 | 21-90 | -90.1926 | 20.6987 | 1972.2184 | 139.6328 | 174.9247 | 214.1029 | 248.726 | 288.9529 | 1.664%
6643 | 21-90.5 | -90.464 | 20.6987 | 1989.6698 | 138.6039 | 174.1387 | 213.2495 | 247.7825 | 287.9119 | 1.622%
6644 | 21-90.5 | -90.7353 | 20.6987 | 2007.1253 | 137.6795 | 173.4076 | 212.4699 | 246.9147 | 286.9468 | 1.584%
6645 | 21-50 | -50.0371 | 20.97 | 794.0714 | 134.9617 | 172.2066 | 206.1628 | 235.5539 | 269.136 | 1.487%
6646 | 21-50.5 | -50.3084 | 20.97 | 778.5352 | 136.4608 | 173.3693 | 207.375 | 237.0148 | 270.8923 | 1.549%
6647 | 21-50.5 | -50.5797 | 20.97 | 763.0972 | 137.8915 | 174.4287 | 208.5357 | 238.4225 | 272.594 | 1.61%
6648 | 21-51 | -50.851 | 20.97 | 747.7635 | 139.2871 | 175.4187 | 209.6856 | 239.8326 | 274.3158 | 1.671%
6649 | 21-51 | -51.1224 | 20.97 | 732.5407 | 140.6914 | 176.3793 | 210.8745 | 241.3121 | 276.1452 | 1.735%
6650 | 21-51.5 | -51.3937 | 20.97 | 717.436 | 142.0296 | 177.2573 | 212.0078 | 242.7272 | 277.9001 | 1.797%
6651 | 21-51.5 | -51.665 | 20.97 | 702.4569 | 143.3539 | 178.104 | 213.1392 | 244.1472 | 279.6689 | 1.86%
6652 | 21-52 | -51.9363 | 20.97 | 687.6118 | 144.7121 | 178.9628 | 214.3178 | 245.6357 | 281.5328 | 1.926%
6653 | 21-52 | -52.2077 | 20.97 | 672.9095 | 146.0227 | 179.782 | 215.4459 | 247.0562 | 283.3074 | 1.992%
6654 | 21-52.5 | -52.479 | 20.97 | 658.3596 | 147.3303 | 180.599 | 216.5752 | 248.4818 | 285.0917 | 2.06%
6655 | 21-53 | -52.7503 | 20.97 | 643.9724 | 148.6647 | 181.4351 | 217.7416 | 249.9621 | 286.9532 | 2.131%
6656 | 21-53 | -53.0216 | 20.97 | 629.7593 | 149.9539 | 182.2365 | 218.8512 | 251.3642 | 288.71 | 2.202%
6657 | 21-53.5 | -53.2929 | 20.97 | 615.7322 | 151.2592 | 183.0425 | 219.9589 | 252.7574 | 290.449 | 2.276%
6658 | 21-53.5 | -53.5643 | 20.97 | 601.9042 | 152.6044 | 183.8689 | 221.0868 | 254.1704 | 292.2067 | 2.354%
6659 | 21-54 | -53.8356 | 20.97 | 588.2894 | 153.8874 | 184.6469 | 222.1301 | 255.4634 | 293.8004 | 2.432%
6660 | 21-54 | -54.1069 | 20.97 | 574.9029 | 155.1602 | 185.412 | 223.1452 | 256.7128 | 295.3314 | 2.511%
6661 | 21-54.5 | -54.3782 | 20.97 | 561.7611 | 156.4325 | 186.1713 | 224.1425 | 257.9327 | 296.8181 | 2.592%
6662 | 21-54.5 | -54.6495 | 20.97 | 548.8816 | 157.5869 | 186.8487 | 225.0127 | 258.9816 | 298.0797 | 2.668%
6663 | 21-55 | -54.9209 | 20.97 | 536.2833 | 158.7025 | 187.5032 | 225.8534 | 259.9949 | 299.2986 | 2.744%
6664 | 21-55 | -55.1922 | 20.97 | 523.9866 | 159.7889 | 188.1447 | 226.6801 | 260.9937 | 300.5025 | 2.82%
6665 | 21-55.5 | -55.4635 | 20.97 | 512.0132 | 160.7767 | 188.724 | 227.4101 | 261.862 | 301.5344 | 2.891%
6666 | 21-55.5 | -55.7348 | 20.97 | 500.3863 | 161.7393 | 189.3043 | 228.1435 | 262.7363 | 302.5753 | 2.962%
6667 | 21-56 | -56.0061 | 20.97 | 489.1307 | 162.6682 | 189.8896 | 228.8852 | 263.622 | 303.6318 | 3.033%
6668 | 21-56.5 | -56.2775 | 20.97 | 478.2726 | 163.5214 | 190.438 | 229.5647 | 264.4207 | 304.5701 | 3.1%
6669 | 21-56.5 | -56.5488 | 20.97 | 467.8397 | 164.36 | 191.0074 | 230.2781 | 265.266 | 305.5709 | 3.168%
6670 | 21-57 | -56.8201 | 20.97 | 457.8612 | 165.1624 | 191.5931 | 231.0181 | 266.1479 | 306.6207 | 3.234%
6671 | 21-57 | -57.0914 | 20.97 | 448.3673 | 165.8692 | 192.1382 | 231.7022 | 266.9594 | 307.5825 | 3.295%
6672 | 21-57.5 | -57.3628 | 20.97 | 439.3894 | 166.5689 | 192.7141 | 232.4361 | 267.8394 | 308.6361 | 3.355%
6673 | 21-57.5 | -57.6341 | 20.97 | 430.96 | 167.2387 | 193.3083 | 233.202 | 268.7647 | 309.7517 | 3.415%
6674 | 21-58 | -57.9054 | 20.97 | 423.1118 | 167.8205 | 193.8614 | 233.9149 | 269.6263 | 310.7906 | 3.468%
6675 | 21-58 | -58.1767 | 20.97 | 415.8776 | 168.417 | 194.452 | 234.6866 | 270.5674 | 311.9348 | 3.523%
6676 | 21-58.5 | -58.448 | 20.97 | 409.2901 | 168.9986 | 195.0592 | 235.4837 | 271.5424 | 313.1237 | 3.577%
6677 | 21-58.5 | -58.7194 | 20.97 | 403.381 | 169.5152 | 195.6229 | 236.2134 | 272.4266 | 314.1927 | 3.626%
6678 | 21-59 | -58.9907 | 20.97 | 398.1805 | 170.0261 | 196.1985 | 236.9649 | 273.3427 | 315.3063 | 3.676%
6679 | 21-59.5 | -59.262 | 20.97 | 393.7167 | 170.5165 | 196.7674 | 237.7115 | 274.256 | 316.42 | 3.724%
6680 | 21-59.5 | -59.5333 | 20.97 | 390.0149 | 170.9609 | 197.2924 | 238.4024 | 275.1028 | 317.4542 | 3.768%
6681 | 21-60 | -59.8046 | 20.97 | 387.0969 | 171.3916 | 197.8235 | 239.1187 | 275.9945 | 318.5586 | 3.809%
6682 | 21-60 | -60.076 | 20.97 | 384.9806 | 171.7927 | 198.3358 | 239.8214 | 276.8785 | 319.6633 | 3.848%
6683 | 21-60.5 | -60.3473 | 20.97 | 383.6792 | 172.1509 | 198.7981 | 240.4584 | 277.6823 | 320.6702 | 3.882%
6684 | 21-60.5 | -60.6186 | 20.97 | 383.2012 | 172.517 | 199.2754 | 241.123 | 278.526 | 321.7327 | 3.917%
6685 | 21-61 | -60.8899 | 20.97 | 383.5494 | 172.8678 | 199.7343 | 241.7642 | 279.3418 | 322.7619 | 3.951%
6686 | 21-61 | -61.1613 | 20.97 | 384.7218 | 173.1879 | 200.1512 | 242.3442 | 280.0779 | 323.6886 | 3.981%
6687 | 21-61.5 | -61.4326 | 20.97 | 386.7108 | 173.5293 | 200.5972 | 242.9666 | 280.8692 | 324.6864 | 4.014%
6688 | 21-61.5 | -61.7039 | 20.97 | 389.5039 | 173.8578 | 201.0225 | 243.5548 | 281.6131 | 325.6202 | 4.046%
6689 | 21-62 | -61.9752 | 20.97 | 393.0839 | 174.1559 | 201.4015 | 244.0687 | 282.2551 | 326.4178 | 4.076%
6690 | 21-62 | -62.2465 | 20.97 | 397.4295 | 174.4729 | 201.807 | 244.6225 | 282.95 | 327.2843 | 4.108%
6691 | 21-62.5 | -62.5179 | 20.97 | 402.5161 | 174.7728 | 202.1905 | 245.1459 | 283.6064 | 328.1025 | 4.138%
6692 | 21-63 | -62.7892 | 20.97 | 408.3157 | 175.0434 | 202.534 | 245.6107 | 284.1864 | 328.8221 | 4.165%
6693 | 21-63 | -63.0605 | 20.97 | 414.7987 | 175.3227 | 202.8878 | 246.0886 | 284.782 | 329.5603 | 4.194%
6694 | 21-63.5 | -63.3318 | 20.97 | 421.9333 | 175.5817 | 203.2087 | 246.5119 | 285.3015 | 330.1955 | 4.221%
6695 | 21-63.5 | -63.6031 | 20.97 | 429.6873 | 175.8205 | 203.4984 | 246.8844 | 285.7509 | 330.7368 | 4.247%
6696 | 21-64 | -63.8745 | 20.97 | 438.0275 | 176.0719 | 203.807 | 247.2871 | 286.2416 | 331.3332 | 4.274%
6697 | 21-64 | -64.1458 | 20.97 | 446.9213 | 176.3022 | 204.0898 | 247.6564 | 286.6918 | 331.8807 | 4.299%
6698 | 21-64.5 | -64.4171 | 20.97 | 456.3362 | 176.5157 | 204.3567 | 248.0117 | 287.1308 | 332.4208 | 4.321%
6699 | 21-64.5 | -64.6884 | 20.97 | 466.2407 | 176.7427 | 204.6517 | 248.4217 | 287.6512 | 333.0763 | 4.344%
6700 | 21-65 | -64.9598 | 20.97 | 476.6041 | 176.9355 | 204.9045 | 248.7761 | 288.1032 | 333.6484 | 4.363%
6701 | 21-65 | -65.2311 | 20.97 | 487.3972 | 177.1077 | 205.135 | 249.106 | 288.5294 | 334.1931 | 4.379%
6702 | 21-65.5 | -65.5024 | 20.97 | 498.5921 | 177.2946 | 205.3952 | 249.4926 | 289.0394 | 334.8562 | 4.396%
6703 | 21-66 | -65.7737 | 20.97 | 510.1624 | 177.4417 | 205.6069 | 249.8162 | 289.4727 | 335.4261 | 4.409%
6704 | 21-66 | -66.045 | 20.97 | 522.0829 | 177.5659 | 205.7932 | 250.111 | 289.8745 | 335.9615 | 4.418%
6705 | 21-66.5 | -66.3164 | 20.97 | 534.3303 | 177.6968 | 205.9968 | 250.4419 | 290.3313 | 336.5764 | 4.427%
6706 | 21-66.5 | -66.5877 | 20.97 | 546.8825 | 177.7961 | 206.1649 | 250.7318 | 290.7425 | 337.1402 | 4.433%
6707 | 21-67 | -66.859 | 20.97 | 559.7191 | 177.8816 | 206.3253 | 251.0254 | 291.1696 | 337.736 | 4.436%
6708 | 21-67 | -67.1303 | 20.97 | 572.8209 | 177.9713 | 206.5047 | 251.365 | 291.6701 | 338.4403 | 4.437%
6709 | 21-67.5 | -67.4016 | 20.97 | 586.17 | 178.0042 | 206.6129 | 251.6092 | 292.0523 | 338.9983 | 4.433%
6710 | 21-67.5 | -67.673 | 20.97 | 599.75 | 178.002 | 206.6778 | 251.7968 | 292.3652 | 339.472 | 4.425%
6711 | 21-68 | -67.9443 | 20.97 | 613.5455 | 177.9839 | 206.7257 | 251.9661 | 292.6592 | 339.9264 | 4.415%
6712 | 21-68 | -68.2156 | 20.97 | 627.5422 | 177.8312 | 206.5888 | 251.8643 | 292.598 | 339.9214 | 4.393%
6713 | 21-68.5 | -68.4869 | 20.97 | 641.7269 | 177.5468 | 206.3175 | 251.5723 | 292.2928 | 339.6063 | 4.359%
6714 | 21-69 | -68.7583 | 20.97 | 656.0874 | 177.1317 | 205.9439 | 251.1426 | 291.8164 | 339.0796 | 4.312%
6715 | 21-69 | -69.0296 | 20.97 | 670.6125 | 176.6447 | 205.4793 | 250.5805 | 291.1674 | 338.3305 | 4.259%
6716 | 21-69.5 | -69.3009 | 20.97 | 685.2915 | 176.1412 | 204.999 | 250.0033 | 290.5045 | 337.5695 | 4.205%
6717 | 21-69.5 | -69.5722 | 20.97 | 700.1148 | 175.6375 | 204.5279 | 249.4523 | 289.8851 | 336.8745 | 4.15%
6718 | 21-70 | -69.8435 | 20.97 | 715.0734 | 174.9893 | 203.9143 | 248.6953 | 288.9983 | 335.8359 | 4.084%
6719 | 21-70 | -70.1149 | 20.97 | 730.1589 | 174.2383 | 203.2106 | 247.8124 | 287.9514 | 334.5957 | 4.009%
6720 | 21-70.5 | -70.3862 | 20.97 | 745.3636 | 173.4074 | 202.4371 | 246.8358 | 286.7882 | 333.2119 | 3.927%
6721 | 21-70.5 | -70.6575 | 20.97 | 760.6803 | 172.6535 | 201.6768 | 245.8593 | 285.6103 | 331.7934 | 3.855%
6722 | 21-71 | -70.9288 | 20.97 | 776.1023 | 172.0489 | 201.0241 | 245.0338 | 284.6254 | 330.6191 | 3.796%
6723 | 21-71 | -71.2001 | 20.97 | 791.6235 | 171.5845 | 200.4813 | 244.3669 | 283.846 | 329.7083 | 3.75%
6724 | 21-71.5 | -71.4715 | 20.97 | 807.2381 | 171.0846 | 199.8828 | 243.6085 | 282.9397 | 328.6261 | 3.701%
6725 | 21-71.5 | -71.7428 | 20.97 | 822.9408 | 170.6674 | 199.3996 | 243.0202 | 282.2569 | 327.8336 | 3.66%
6726 | 21-72 | -72.0141 | 20.97 | 838.7265 | 170.3522 | 199.0213 | 242.5856 | 281.7755 | 327.3013 | 3.627%
6727 | 21-72.5 | -72.2854 | 20.97 | 854.5906 | 169.9743 | 198.5845 | 242.0467 | 281.1432 | 326.5594 | 3.591%
6728 | 21-72.5 | -72.5568 | 20.97 | 870.5289 | 169.474 | 198.0804 | 241.4064 | 280.3765 | 325.6418 | 3.546%
6729 | 21-73 | -72.8281 | 20.97 | 886.5373 | 168.9456 | 197.5679 | 240.7424 | 279.5706 | 324.6653 | 3.499%
6730 | 21-73 | -73.0994 | 20.97 | 902.6119 | 168.7419 | 197.27 | 240.3454 | 279.0792 | 324.059 | 3.481%
6731 | 21-73.5 | -73.3707 | 20.97 | 918.7494 | 168.912 | 197.3447 | 240.4633 | 279.2394 | 324.2716 | 3.493%
6732 | 21-73.5 | -73.642 | 20.97 | 934.9464 | 169.2648 | 197.6087 | 240.839 | 279.7228 | 324.8875 | 3.521%
6733 | 21-74 | -73.9134 | 20.97 | 951.1998 | 169.3263 | 197.5232 | 240.7076 | 279.5457 | 324.6526 | 3.525%
6734 | 21-74 | -74.1847 | 20.97 | 967.5067 | 168.7619 | 197.0203 | 240.0022 | 278.6456 | 323.5135 | 3.479%
6735 | 21-74.5 | -74.456 | 20.97 | 983.8646 | 167.7458 | 196.2056 | 238.8632 | 277.1954 | 321.6828 | 3.398%
6736 | 21-74.5 | -74.7273 | 20.97 | 1000.2707 | 166.6385 | 195.3185 | 237.6045 | 275.5789 | 319.627 | 3.313%
6737 | 21-75 | -74.9986 | 20.97 | 1016.7228 | 165.6285 | 194.5273 | 236.4816 | 274.1366 | 317.7926 | 3.236%
6738 | 21-75.5 | -75.27 | 20.97 | 1033.2187 | 164.8038 | 193.8609 | 235.5215 | 272.8923 | 316.1983 | 3.175%
6739 | 21-75.5 | -75.5413 | 20.97 | 1049.7561 | 164.3402 | 193.4066 | 234.831 | 271.9707 | 314.9894 | 3.142%
6740 | 21-76 | -75.8126 | 20.97 | 1066.3332 | 164.307 | 193.336 | 234.6824 | 271.7439 | 314.6636 | 3.141%
6741 | 21-76 | -76.0839 | 20.97 | 1082.9481 | 164.4987 | 193.4496 | 234.7866 | 271.8355 | 314.7367 | 3.157%
6742 | 21-76.5 | -76.3553 | 20.97 | 1099.599 | 164.5861 | 193.4023 | 234.6505 | 271.6094 | 314.3958 | 3.165%
6743 | 21-76.5 | -76.6266 | 20.97 | 1116.2844 | 164.1908 | 192.9799 | 233.9947 | 270.7251 | 313.2277 | 3.137%
6744 | 21-77 | -76.8979 | 20.97 | 1133.0025 | 163.5446 | 192.2863 | 232.9458 | 269.3296 | 311.4025 | 3.09%
6745 | 21-77 | -77.1692 | 20.97 | 1149.7521 | 162.9998 | 191.6278 | 231.9181 | 267.9394 | 309.5608 | 3.051%
6746 | 21-77.5 | -77.4405 | 20.97 | 1166.5316 | 162.9953 | 191.5434 | 231.677 | 267.5394 | 308.9581 | 3.055%
6747 | 21-77.5 | -77.7119 | 20.97 | 1183.3397 | 163.6564 | 191.9376 | 232.0765 | 267.933 | 309.3344 | 3.109%
6748 | 21-78 | -77.9832 | 20.97 | 1200.1753 | 164.7296 | 192.622 | 232.8517 | 268.782 | 310.2611 | 3.198%
6749 | 21-78.5 | -78.2545 | 20.97 | 1217.0372 | 165.8363 | 193.3757 | 233.7161 | 269.7387 | 311.3179 | 3.292%
6750 | 21-78.5 | -78.5258 | 20.97 | 1233.9242 | 166.9192 | 194.1455 | 234.5892 | 270.6963 | 312.3651 | 3.389%
6751 | 21-79 | -78.7971 | 20.97 | 1250.8352 | 167.8857 | 194.8641 | 235.3852 | 271.5516 | 313.2792 | 3.479%
6752 | 21-79 | -79.0685 | 20.97 | 1267.7694 | 168.5911 | 195.4787 | 236.0495 | 272.2497 | 314.0057 | 3.551%
6753 | 21-79.5 | -79.3398 | 20.97 | 1284.7256 | 169.1032 | 195.9111 | 236.4532 | 272.6114 | 314.3023 | 3.607%
6754 | 21-79.5 | -79.6111 | 20.97 | 1301.7031 | 169.6018 | 196.3185 | 236.8143 | 272.9128 | 314.5164 | 3.663%
6755 | 21-80 | -79.8824 | 20.97 | 1318.7009 | 170.3264 | 196.9926 | 237.5537 | 273.7003 | 315.3492 | 3.741%
6756 | 21-80 | -80.1537 | 20.97 | 1335.7183 | 171.316 | 197.9326 | 238.6596 | 274.9503 | 316.7614 | 3.846%
6757 | 21-80.5 | -80.4251 | 20.97 | 1352.7545 | 172.4335 | 199.0366 | 239.9981 | 276.4986 | 318.5523 | 3.965%
6758 | 21-80.5 | -80.6964 | 20.97 | 1369.8087 | 173.5193 | 200.1885 | 241.4193 | 278.1641 | 320.5035 | 4.084%
6759 | 21-81 | -80.9677 | 20.97 | 1386.8802 | 174.4389 | 201.1751 | 242.6194 | 279.5557 | 322.1171 | 4.189%
6760 | 21-81 | -81.239 | 20.97 | 1403.9684 | 175.1882 | 202.0014 | 243.6106 | 280.6932 | 323.4224 | 4.277%
6761 | 21-81.5 | -81.5104 | 20.97 | 1421.0726 | 175.8398 | 202.7514 | 244.5137 | 281.7327 | 324.619 | 4.355%
6762 | 21-82 | -81.7817 | 20.97 | 1438.1922 | 176.4194 | 203.4017 | 245.2896 | 282.6195 | 325.6325 | 4.426%
6763 | 21-82 | -82.053 | 20.97 | 1455.3267 | 176.9704 | 203.9998 | 246.0064 | 283.4413 | 326.5749 | 4.494%
6764 | 21-82.5 | -82.3243 | 20.97 | 1472.4754 | 177.5012 | 204.5853 | 246.7201 | 284.2705 | 327.5381 | 4.559%
6765 | 21-82.5 | -82.5956 | 20.97 | 1489.6378 | 178.0146 | 205.1593 | 247.4229 | 285.0893 | 328.492 | 4.622%
6766 | 21-83 | -82.867 | 20.97 | 1506.8135 | 178.5607 | 205.7945 | 248.231 | 286.0571 | 329.6492 | 4.688%
6767 | 21-83 | -83.1383 | 20.97 | 1524.0019 | 179.1676 | 206.5344 | 249.2157 | 287.2723 | 331.1423 | 4.758%
6768 | 21-83.5 | -83.4096 | 20.97 | 1541.2026 | 179.6783 | 207.1767 | 250.0921 | 288.3708 | 332.5104 | 4.815%
6769 | 21-83.5 | -83.6809 | 20.97 | 1558.4151 | 180.0625 | 207.6903 | 250.8249 | 289.3144 | 333.7121 | 4.855%
6770 | 21-84 | -83.9522 | 20.97 | 1575.639 | 180.323 | 208.0703 | 251.4111 | 290.102 | 334.7495 | 4.878%
6771 | 21-84 | -84.2236 | 20.97 | 1592.8739 | 180.3627 | 208.1827 | 251.6537 | 290.4755 | 335.2888 | 4.873%
6772 | 21-84.5 | -84.4949 | 20.97 | 1610.1194 | 180.3324 | 208.227 | 251.8343 | 290.7952 | 335.7867 | 4.858%
6773 | 21-85 | -84.7662 | 20.97 | 1627.3751 | 180.2901 | 208.2817 | 252.0666 | 291.2088 | 336.4326 | 4.837%
6774 | 21-85 | -85.0375 | 20.97 | 1644.6407 | 180.0731 | 208.1373 | 252.062 | 291.3524 | 336.7705 | 4.795%
6775 | 21-85.5 | -85.3089 | 20.97 | 1661.9158 | 179.69 | 207.808 | 251.845 | 291.2606 | 336.8483 | 4.731%
6776 | 21-85.5 | -85.5802 | 20.97 | 1679.2 | 179.092 | 207.2929 | 251.4174 | 290.9383 | 336.6749 | 4.641%
6777 | 21-86 | -85.8515 | 20.97 | 1696.4932 | 178.1517 | 206.4245 | 250.5283 | 290.0528 | 335.8158 | 4.516%
6778 | 21-86 | -86.1228 | 20.97 | 1713.7948 | 176.7327 | 205.1977 | 249.1833 | 288.6216 | 334.3046 | 4.345%
6779 | 21-86.5 | -86.3941 | 20.97 | 1731.1047 | 174.8678 | 203.615 | 247.3894 | 286.6562 | 332.1586 | 4.136%
6780 | 21-86.5 | -86.6655 | 20.97 | 1748.4226 | 172.6874 | 201.7281 | 245.1865 | 284.1829 | 329.3851 | 3.907%
6781 | 21-87 | -86.9368 | 20.97 | 1765.7482 | 170.3429 | 199.7306 | 242.8492 | 281.5538 | 326.4312 | 3.675%
6782 | 21-87 | -87.2081 | 20.97 | 1783.0812 | 167.8535 | 197.6335 | 240.3913 | 278.7858 | 323.3175 | 3.445%
6783 | 21-87.5 | -87.4794 | 20.97 | 1800.4213 | 165.1735 | 195.363 | 237.6885 | 275.7027 | 319.8023 | 3.214%
6784 | 21-88 | -87.7507 | 20.97 | 1817.7684 | 162.3886 | 193.0257 | 234.9214 | 272.5435 | 316.1969 | 2.99%
6785 | 21-88 | -88.0221 | 20.97 | 1835.1221 | 159.5205 | 190.6253 | 232.1053 | 269.3259 | 312.5219 | 2.775%
6786 | 21-88.5 | -88.2934 | 20.97 | 1852.4823 | 156.6335 | 188.1916 | 229.2648 | 266.0616 | 308.7713 | 2.574%
6787 | 21-88.5 | -88.5647 | 20.97 | 1869.8488 | 153.8951 | 185.9276 | 226.676 | 263.1021 | 305.3889 | 2.396%
6788 | 21-89 | -88.836 | 20.97 | 1887.2212 | 151.3181 | 183.8547 | 224.3328 | 260.4353 | 302.3549 | 2.241%
6789 | 21-89 | -89.1074 | 20.97 | 1904.5995 | 148.9561 | 182.0301 | 222.2111 | 258.0132 | 299.5901 | 2.11%
6790 | 21-89.5 | -89.3787 | 20.97 | 1921.9834 | 146.9447 | 180.5982 | 220.5577 | 256.1678 | 297.5338 | 2.005%
6791 | 21-89.5 | -89.65 | 20.97 | 1939.3727 | 145.3611 | 179.4671 | 219.2812 | 254.7748 | 296.0199 | 1.927%
6792 | 21-90 | -89.9213 | 20.97 | 1956.7672 | 144.0293 | 178.4903 | 218.1573 | 253.5259 | 294.6345 | 1.863%
6793 | 21-90 | -90.1926 | 20.97 | 1974.1668 | 142.8281 | 177.6039 | 217.138 | 252.3875 | 293.3644 | 1.807%
6794 | 21-90.5 | -90.464 | 20.97 | 1991.5712 | 141.7476 | 176.7897 | 216.2059 | 251.3394 | 292.1865 | 1.759%
6795 | 21-90.5 | -90.7353 | 20.97 | 2008.9804 | 140.7579 | 176.0261 | 215.337 | 250.3543 | 291.0695 | 1.715%
6796 | 21-50 | -50.0371 | 21.2413 | 802.7817 | 132.9428 | 170.6994 | 204.7378 | 233.9496 | 267.3302 | 1.409%
6797 | 21-50.5 | -50.3084 | 21.2413 | 787.4434 | 134.4862 | 171.963 | 205.982 | 235.4373 | 269.106 | 1.47%
6798 | 21-50.5 | -50.5797 | 21.2413 | 772.2093 | 135.9612 | 173.1134 | 207.1711 | 236.8667 | 270.8204 | 1.53%
6799 | 21-51 | -50.851 | 21.2413 | 757.0859 | 137.3999 | 174.1837 | 208.3452 | 238.2938 | 272.5491 | 1.59%
6800 | 21-51 | -51.1224 | 21.2413 | 742.0798 | 138.8443 | 175.2125 | 209.5537 | 239.7849 | 274.3795 | 1.653%
6801 | 21-51.5 | -51.3937 | 21.2413 | 727.1985 | 140.222 | 176.1474 | 210.7077 | 241.2151 | 276.1418 | 1.714%
6802 | 21-51.5 | -51.665 | 21.2413 | 712.4498 | 141.586 | 177.0427 | 211.8621 | 242.6554 | 277.9269 | 1.776%
6803 | 21-52 | -51.9363 | 21.2413 | 697.842 | 142.9838 | 177.9424 | 213.0664 | 244.1694 | 279.8156 | 1.842%
6804 | 21-52 | -52.2077 | 21.2413 | 683.3843 | 144.3345 | 178.793 | 214.2209 | 245.6173 | 281.6181 | 1.908%
6805 | 21-52.5 | -52.479 | 21.2413 | 669.0865 | 145.6845 | 179.6362 | 215.3796 | 247.0745 | 283.4367 | 1.975%
6806 | 21-53 | -52.7503 | 21.2413 | 654.959 | 147.0646 | 180.5004 | 216.5788 | 248.5918 | 285.3398 | 2.046%
6807 | 21-53 | -53.0216 | 21.2413 | 641.0132 | 148.4007 | 181.3298 | 217.7211 | 250.0305 | 287.1376 | 2.116%
6808 | 21-53.5 | -53.2929 | 21.2413 | 627.2611 | 149.7569 | 182.1662 | 218.8658 | 251.4669 | 288.9268 | 2.19%
6809 | 21-53.5 | -53.5643 | 21.2413 | 613.7159 | 151.1589 | 183.0268 | 220.0379 | 252.9333 | 290.7489 | 2.269%
6810 | 21-54 | -53.8356 | 21.2413 | 600.3916 | 152.5057 | 183.8438 | 221.1343 | 254.2926 | 292.4248 | 2.347%
6811 | 21-54 | -54.1069 | 21.2413 | 587.3032 | 153.8505 | 184.6541 | 222.2122 | 255.6218 | 294.0561 | 2.428%
6812 | 21-54.5 | -54.3782 | 21.2413 | 574.4669 | 155.2032 | 185.4644 | 223.2817 | 256.934 | 295.6597 | 2.512%
6813 | 21-54.5 | -54.6495 | 21.2413 | 561.9 | 156.4391 | 186.1932 | 224.2237 | 258.074 | 297.0358 | 2.591%
6814 | 21-55 | -54.9209 | 21.2413 | 549.6211 | 157.6346 | 186.8962 | 225.1293 | 259.1677 | 298.3536 | 2.67%
6815 | 21-55 | -55.1922 | 21.2413 | 537.6498 | 158.8001 | 187.5823 | 226.0121 | 260.233 | 299.6365 | 2.749%
6816 | 21-55.5 | -55.4635 | 21.2413 | 526.0072 | 159.8614 | 188.1995 | 226.7848 | 261.1479 | 300.7189 | 2.824%
6817 | 21-55.5 | -55.7348 | 21.2413 | 514.7156 | 160.8922 | 188.8109 | 227.5494 | 262.0525 | 301.7883 | 2.899%
6818 | 21-56 | -56.0061 | 21.2413 | 503.7987 | 161.8844 | 189.4213 | 228.3122 | 262.9547 | 302.8547 | 2.973%
6819 | 21-56.5 | -56.2775 | 21.2413 | 493.2814 | 162.7976 | 189.9913 | 229.0085 | 263.7645 | 303.7963 | 3.044%
6820 | 21-56.5 | -56.5488 | 21.2413 | 483.1898 | 163.696 | 190.5809 | 229.7375 | 264.6203 | 304.8005 | 3.115%
6821 | 21-57 | -56.8201 | 21.2413 | 473.5511 | 164.5582 | 191.1847 | 230.4911 | 265.5105 | 305.8514 | 3.185%
6822 | 21-57 | -57.0914 | 21.2413 | 464.3936 | 165.3223 | 191.7458 | 231.1844 | 266.3238 | 306.8051 | 3.25%
6823 | 21-57.5 | -57.3628 | 21.2413 | 455.7462 | 166.0732 | 192.3344 | 231.9211 | 267.1961 | 307.8372 | 3.314%
6824 | 21-57.5 | -57.6341 | 21.2413 | 447.6386 | 166.7885 | 192.9382 | 232.6839 | 268.1051 | 308.9192 | 3.378%
6825 | 21-58 | -57.9054 | 21.2413 | 440.1006 | 167.4111 | 193.5004 | 233.3923 | 268.9478 | 309.9207 | 3.434%
6826 | 21-58 | -58.1767 | 21.2413 | 433.162 | 168.0506 | 194.1051 | 234.1681 | 269.8822 | 311.044 | 3.493%
6827 | 21-58.5 | -58.448 | 21.2413 | 426.8519 | 168.6766 | 194.7305 | 234.9765 | 270.861 | 312.2262 | 3.551%
6828 | 21-58.5 | -58.7194 | 21.2413 | 421.1988 | 169.2359 | 195.3143 | 235.7208 | 271.7537 | 313.2954 | 3.605%
6829 | 21-59 | -58.9907 | 21.2413 | 416.2294 | 169.7917 | 195.9144 | 236.4947 | 272.6892 | 314.424 | 3.659%
6830 | 21-59.5 | -59.262 | 21.2413 | 411.9683 | 170.3276 | 196.5114 | 237.2699 | 273.6308 | 315.5648 | 3.712%
6831 | 21-59.5 | -59.5333 | 21.2413 | 408.4379 | 170.8158 | 197.0661 | 237.9923 | 274.5098 | 316.6317 | 3.76%
6832 | 21-60 | -59.8046 | 21.2413 | 405.6571 | 171.2866 | 197.6255 | 238.737 | 275.4293 | 317.7621 | 3.806%
6833 | 21-60 | -60.076 | 21.2413 | 403.6415 | 171.7222 | 198.1648 | 239.4664 | 276.3389 | 318.8902 | 3.849%
6834 | 21-60.5 | -60.3473 | 21.2413 | 402.4026 | 172.1073 | 198.6528 | 240.1307 | 277.1708 | 319.9255 | 3.886%
6835 | 21-60.5 | -60.6186 | 21.2413 | 401.9475 | 172.4944 | 199.1543 | 240.8244 | 278.0479 | 321.0263 | 3.924%
6836 | 21-61 | -60.8899 | 21.2413 | 402.279 | 172.8628 | 199.6357 | 241.4962 | 278.9021 | 322.1032 | 3.959%
6837 | 21-61 | -61.1613 | 21.2413 | 403.3951 | 173.1966 | 200.0727 | 242.1071 | 279.6795 | 323.0842 | 3.991%
6838 | 21-61.5 | -61.4326 | 21.2413 | 405.2893 | 173.547 | 200.5343 | 242.7566 | 280.5094 | 324.1348 | 4.024%
6839 | 21-61.5 | -61.7039 | 21.2413 | 407.9507 | 173.8804 | 200.9712 | 243.3683 | 281.2885 | 325.1189 | 4.056%
6840 | 21-62 | -61.9752 | 21.2413 | 411.3646 | 174.1804 | 201.3591 | 243.9038 | 281.965 | 325.9673 | 4.086%
6841 | 21-62 | -62.2465 | 21.2413 | 415.5122 | 174.4978 | 201.7736 | 244.4821 | 282.7002 | 326.8942 | 4.117%
6842 | 21-62.5 | -62.5179 | 21.2413 | 420.3719 | 174.7961 | 202.164 | 245.0281 | 283.3952 | 327.7713 | 4.146%
6843 | 21-63 | -62.7892 | 21.2413 | 425.9193 | 175.0627 | 202.511 | 245.5102 | 284.0066 | 328.5405 | 4.172%
6844 | 21-63 | -63.0605 | 21.2413 | 432.1279 | 175.3369 | 202.8667 | 246.0029 | 284.6302 | 329.3238 | 4.199%
6845 | 21-63.5 | -63.3318 | 21.2413 | 438.9697 | 175.5899 | 203.188 | 246.4383 | 285.1738 | 329.9987 | 4.225%
6846 | 21-63.5 | -63.6031 | 21.2413 | 446.4154 | 175.8225 | 203.4763 | 246.8187 | 285.6407 | 330.5698 | 4.25%
6847 | 21-64 | -63.8745 | 21.2413 | 454.4355 | 176.0686 | 203.7825 | 247.224 | 286.1394 | 331.1811 | 4.276%
6848 | 21-64 | -64.1458 | 21.2413 | 463 | 176.295 | 204.0618 | 247.5904 | 286.5875 | 331.7275 | 4.3%
6849 | 21-64.5 | -64.4171 | 21.2413 | 472.0793 | 176.5068 | 204.3248 | 247.9384 | 287.0156 | 332.2523 | 4.322%
6850 | 21-64.5 | -64.6884 | 21.2413 | 481.6443 | 176.7345 | 204.6168 | 248.3383 | 287.5186 | 332.8811 | 4.346%
6851 | 21-65 | -64.9598 | 21.2413 | 491.6666 | 176.9305 | 204.8674 | 248.6808 | 287.9487 | 333.4182 | 4.366%
6852 | 21-65 | -65.2311 | 21.2413 | 502.1187 | 177.1086 | 205.0973 | 248.998 | 288.3498 | 333.9219 | 4.384%
6853 | 21-65.5 | -65.5024 | 21.2413 | 512.9745 | 177.3043 | 205.3589 | 249.372 | 288.8326 | 334.5389 | 4.403%
6854 | 21-66 | -65.7737 | 21.2413 | 524.2088 | 177.4623 | 205.5733 | 249.6831 | 289.2377 | 335.0602 | 4.418%
6855 | 21-66 | -66.045 | 21.2413 | 535.7977 | 177.6002 | 205.7664 | 249.9715 | 289.6191 | 335.5572 | 4.43%
6856 | 21-66.5 | -66.3164 | 21.2413 | 547.7188 | 177.749 | 205.9833 | 250.3067 | 290.0708 | 336.154 | 4.442%
6857 | 21-66.5 | -66.5877 | 21.2413 | 559.9507 | 177.8703 | 206.1712 | 250.6115 | 290.4911 | 336.7193 | 4.451%
6858 | 21-67 | -66.859 | 21.2413 | 572.4736 | 177.982 | 206.358 | 250.9307 | 290.9422 | 337.3363 | 4.457%
6859 | 21-67 | -67.1303 | 21.2413 | 585.2687 | 178.1023 | 206.5704 | 251.3067 | 291.4814 | 338.0814 | 4.463%
6860 | 21-67.5 | -67.4016 | 21.2413 | 598.3186 | 178.1688 | 206.7169 | 251.5964 | 291.9154 | 338.6984 | 4.462%
6861 | 21-67.5 | -67.673 | 21.2413 | 611.6069 | 178.2029 | 206.8254 | 251.8396 | 292.295 | 339.2519 | 4.458%
6862 | 21-68 | -67.9443 | 21.2413 | 625.1183 | 178.2235 | 206.9223 | 252.0747 | 292.6707 | 339.8074 | 4.452%
6863 | 21-68 | -68.2156 | 21.2413 | 638.8388 | 178.1406 | 206.8766 | 252.1004 | 292.7719 | 340.0075 | 4.437%
6864 | 21-68.5 | -68.4869 | 21.2413 | 652.755 | 177.9849 | 206.7421 | 252.0012 | 292.7134 | 340.0052 | 4.415%
6865 | 21-69 | -68.7583 | 21.2413 | 666.8547 | 177.7603 | 206.5496 | 251.827 | 292.564 | 339.8932 | 4.385%
6866 | 21-69 | -69.0296 | 21.2413 | 681.1265 | 177.4637 | 206.2635 | 251.5169 | 292.2378 | 339.5535 | 4.35%
6867 | 21-69.5 | -69.3009 | 21.2413 | 695.5597 | 177.1475 | 205.9574 | 251.1843 | 291.8871 | 339.1875 | 4.312%
6868 | 21-69.5 | -69.5722 | 21.2413 | 710.1444 | 176.8279 | 205.6565 | 250.87 | 291.5682 | 338.8709 | 4.273%
6869 | 21-70 | -69.8435 | 21.2413 | 724.8716 | 176.3972 | 205.2349 | 250.3797 | 291.0195 | 338.2578 | 4.225%
6870 | 21-70 | -70.1149 | 21.2413 | 739.7326 | 175.8949 | 204.7453 | 249.7942 | 290.3495 | 337.4915 | 4.171%
6871 | 21-70.5 | -70.3862 | 21.2413 | 754.7196 | 175.3365 | 204.2037 | 249.1397 | 289.5947 | 336.6216 | 4.112%
6872 | 21-70.5 | -70.6575 | 21.2413 | 769.825 | 174.7766 | 203.6096 | 248.3932 | 288.7082 | 335.5695 | 4.055%
6873 | 21-71 | -70.9288 | 21.2413 | 785.0421 | 174.2823 | 203.0572 | 247.7046 | 287.895 | 334.6094 | 4.004%
6874 | 21-71 | -71.2001 | 21.2413 | 800.3645 | 173.8513 | 202.5542 | 247.0877 | 287.175 | 333.7693 | 3.959%
6875 | 21-71.5 | -71.4715 | 21.2413 | 815.7861 | 173.3796 | 201.9881 | 246.3683 | 286.3137 | 332.7387 | 3.911%
6876 | 21-71.5 | -71.7428 | 21.2413 | 831.3015 | 172.9568 | 201.4926 | 245.7557 | 285.5943 | 331.8941 | 3.868%
6877 | 21-72 | -72.0141 | 21.2413 | 846.9054 | 172.575 | 201.0541 | 245.229 | 284.9895 | 331.1995 | 3.829%
6878 | 21-72.5 | -72.2854 | 21.2413 | 862.593 | 172.0704 | 200.5118 | 244.5341 | 284.1523 | 330.1922 | 3.78%
6879 | 21-72.5 | -72.5568 | 21.2413 | 878.3598 | 171.4439 | 199.9031 | 243.7393 | 283.1827 | 329.0119 | 3.723%
6880 | 21-73 | -72.8281 | 21.2413 | 894.2015 | 170.7917 | 199.2885 | 242.9257 | 282.181 | 327.7825 | 3.665%
6881 | 21-73 | -73.0994 | 21.2413 | 910.1143 | 170.4636 | 198.8879 | 242.3817 | 281.4998 | 326.9339 | 3.636%
6882 | 21-73.5 | -73.3707 | 21.2413 | 926.0943 | 170.4709 | 198.8336 | 242.3177 | 281.4274 | 326.8517 | 3.635%
6883 | 21-73.5 | -73.642 | 21.2413 | 942.1382 | 170.6264 | 198.9436 | 242.4781 | 281.6368 | 327.1217 | 3.647%
6884 | 21-74 | -73.9134 | 21.2413 | 958.2428 | 170.4717 | 198.6868 | 242.1082 | 281.1568 | 326.5053 | 3.634%
6885 | 21-74 | -74.1847 | 21.2413 | 974.4049 | 169.7733 | 198.0793 | 241.259 | 280.0752 | 325.1389 | 3.576%
6886 | 21-74.5 | -74.456 | 21.2413 | 990.6217 | 168.7082 | 197.2258 | 240.07 | 278.5649 | 323.2358 | 3.489%
6887 | 21-74.5 | -74.7273 | 21.2413 | 1006.8905 | 167.6244 | 196.3544 | 238.8403 | 276.9907 | 321.2391 | 3.403%
6888 | 21-75 | -74.9986 | 21.2413 | 1023.2089 | 166.6368 | 195.5796 | 237.7487 | 275.5946 | 319.4698 | 3.326%
6889 | 21-75.5 | -75.27 | 21.2413 | 1039.5744 | 165.8307 | 194.929 | 236.8208 | 274.399 | 317.9452 | 3.265%
6890 | 21-75.5 | -75.5413 | 21.2413 | 1055.9848 | 165.379 | 194.4871 | 236.1608 | 273.5263 | 316.8088 | 3.231%
6891 | 21-76 | -75.8126 | 21.2413 | 1072.438 | 165.3449 | 194.4238 | 236.039 | 273.3463 | 316.5553 | 3.23%
6892 | 21-76 | -76.0839 | 21.2413 | 1088.9321 | 165.5172 | 194.53 | 236.1518 | 273.4632 | 316.6754 | 3.244%
6893 | 21-76.5 | -76.3553 | 21.2413 | 1105.4652 | 165.5622 | 194.4479 | 235.9864 | 273.2143 | 316.3213 | 3.248%
6894 | 21-76.5 | -76.6266 | 21.2413 | 1122.0355 | 165.1064 | 193.9665 | 235.2659 | 272.2615 | 315.0811 | 3.214%
6895 | 21-77 | -76.8979 | 21.2413 | 1138.6413 | 164.3972 | 193.2081 | 234.143 | 270.7842 | 313.1656 | 3.161%
6896 | 21-77 | -77.1692 | 21.2413 | 1155.2811 | 163.8019 | 192.4998 | 233.0605 | 269.3353 | 311.2615 | 3.117%
6897 | 21-77.5 | -77.4405 | 21.2413 | 1171.9534 | 163.7513 | 192.3772 | 232.7801 | 268.8959 | 310.6203 | 3.117%
6898 | 21-77.5 | -77.7119 | 21.2413 | 1188.6569 | 164.354 | 192.7214 | 233.1231 | 269.2278 | 310.9293 | 3.167%
6899 | 21-78 | -77.9832 | 21.2413 | 1205.39 | 165.3432 | 193.3245 | 233.7974 | 269.958 | 311.7161 | 3.25%
6900 | 21-78.5 | -78.2545 | 21.2413 | 1222.1517 | 166.3464 | 193.9715 | 234.5251 | 270.7501 | 312.575 | 3.336%
6901 | 21-78.5 | -78.5258 | 21.2413 | 1238.9407 | 167.3168 | 194.6209 | 235.2417 | 271.5173 | 313.3913 | 3.424%
6902 | 21-79 | -78.7971 | 21.2413 | 1255.7559 | 168.1714 | 195.2158 | 235.8744 | 272.1723 | 314.0603 | 3.505%
6903 | 21-79 | -79.0685 | 21.2413 | 1272.5961 | 168.7685 | 195.7056 | 236.3708 | 272.6617 | 314.5289 | 3.566%
6904 | 21-79.5 | -79.3398 | 21.2413 | 1289.4605 | 169.1779 | 196.0138 | 236.6056 | 272.812 | 314.5625 | 3.613%
6905 | 21-79.5 | -79.6111 | 21.2413 | 1306.3479 | 169.587 | 196.3082 | 236.8129 | 272.921 | 314.5372 | 3.661%
6906 | 21-80 | -79.8824 | 21.2413 | 1323.2575 | 170.2418 | 196.8941 | 237.4335 | 273.5608 | 315.1874 | 3.732%
6907 | 21-80 | -80.1537 | 21.2413 | 1340.1885 | 171.191 | 197.7839 | 238.4731 | 274.7292 | 316.4998 | 3.833%
6908 | 21-80.5 | -80.4251 | 21.2413 | 1357.1399 | 172.2887 | 198.864 | 239.7809 | 276.2407 | 318.2466 | 3.95%
6909 | 21-80.5 | -80.6964 | 21.2413 | 1374.1109 | 173.3589 | 199.9968 | 241.1775 | 277.8764 | 320.1617 | 4.066%
6910 | 21-81 | -80.9677 | 21.2413 | 1391.1009 | 174.2413 | 200.9358 | 242.3124 | 279.1861 | 321.6732 | 4.167%
6911 | 21-81 | -81.239 | 21.2413 | 1408.1091 | 174.9397 | 201.6963 | 243.2126 | 280.2086 | 322.8343 | 4.249%
6912 | 21-81.5 | -81.5104 | 21.2413 | 1425.1347 | 175.5439 | 202.3844 | 244.03 | 281.1396 | 323.8946 | 4.323%
6913 | 21-82 | -81.7817 | 21.2413 | 1442.1772 | 176.0915 | 202.9917 | 244.7443 | 281.9469 | 324.8069 | 4.39%
6914 | 21-82 | -82.053 | 21.2413 | 1459.2359 | 176.6202 | 203.558 | 245.4128 | 282.7047 | 325.6656 | 4.455%
6915 | 21-82.5 | -82.3243 | 21.2413 | 1476.3102 | 177.1314 | 204.1139 | 246.0797 | 283.4702 | 326.5443 | 4.518%
6916 | 21-82.5 | -82.5956 | 21.2413 | 1493.3996 | 177.6452 | 204.6832 | 246.7685 | 284.2657 | 327.4629 | 4.582%
6917 | 21-83 | -82.867 | 21.2413 | 1510.5034 | 178.2148 | 205.342 | 247.5994 | 285.2546 | 328.6387 | 4.651%
6918 | 21-83 | -83.1383 | 21.2413 | 1527.6212 | 178.8678 | 206.1329 | 248.6425 | 286.5342 | 330.2026 | 4.727%
6919 | 21-83.5 | -83.4096 | 21.2413 | 1544.7524 | 179.4303 | 206.8343 | 249.5889 | 287.7124 | 331.6612 | 4.791%
6920 | 21-83.5 | -83.6809 | 21.2413 | 1561.8966 | 179.8586 | 207.3983 | 250.3817 | 288.7243 | 332.9408 | 4.837%
6921 | 21-84 | -83.9522 | 21.2413 | 1579.0533 | 180.1496 | 207.8126 | 251.0081 | 289.557 | 334.0288 | 4.863%
6922 | 21-84 | -84.2236 | 21.2413 | 1596.2221 | 180.2043 | 207.94 | 251.265 | 289.9438 | 334.5796 | 4.861%
6923 | 21-84.5 | -84.4949 | 21.2413 | 1613.4025 | 180.1995 | 208.0134 | 251.4802 | 290.3031 | 335.1227 | 4.849%
6924 | 21-85 | -84.7662 | 21.2413 | 1630.5941 | 180.2032 | 208.1243 | 251.7853 | 290.8051 | 335.8757 | 4.834%
6925 | 21-85 | -85.0375 | 21.2413 | 1647.7966 | 180.0513 | 208.0588 | 251.8822 | 291.071 | 336.3607 | 4.799%
6926 | 21-85.5 | -85.3089 | 21.2413 | 1665.0095 | 179.7407 | 207.8171 | 251.7771 | 291.1133 | 336.5989 | 4.744%
6927 | 21-85.5 | -85.5802 | 21.2413 | 1682.2325 | 179.2204 | 207.3958 | 251.4691 | 290.9344 | 336.5969 | 4.663%
6928 | 21-86 | -85.8515 | 21.2413 | 1699.4653 | 178.3972 | 206.6666 | 250.7644 | 290.2756 | 336.0155 | 4.55%
6929 | 21-86 | -86.1228 | 21.2413 | 1716.7075 | 177.1465 | 205.6015 | 249.6359 | 289.1128 | 334.8352 | 4.395%
6930 | 21-86.5 | -86.3941 | 21.2413 | 1733.9588 | 175.4884 | 204.1944 | 248.0778 | 287.4402 | 333.0513 | 4.203%
6931 | 21-86.5 | -86.6655 | 21.2413 | 1751.2188 | 173.5112 | 202.4663 | 246.089 | 285.2333 | 330.6077 | 3.989%
6932 | 21-87 | -86.9368 | 21.2413 | 1768.4874 | 171.3815 | 200.6311 | 243.9686 | 282.873 | 327.9854 | 3.772%
6933 | 21-87 | -87.2081 | 21.2413 | 1785.7641 | 169.1191 | 198.7018 | 241.7326 | 280.378 | 325.2066 | 3.555%
6934 | 21-87.5 | -87.4794 | 21.2413 | 1803.0487 | 166.672 | 196.5978 | 239.2442 | 277.5552 | 322.0067 | 3.336%
6935 | 21-88 | -87.7507 | 21.2413 | 1820.341 | 164.1268 | 194.4378 | 236.6908 | 274.6531 | 318.7104 | 3.123%
6936 | 21-88 | -88.0221 | 21.2413 | 1837.6407 | 161.5036 | 192.2238 | 234.0872 | 271.6891 | 315.3378 | 2.917%
6937 | 21-88.5 | -88.2934 | 21.2413 | 1854.9476 | 158.8609 | 189.9811 | 231.4534 | 268.6698 | 311.8775 | 2.723%
6938 | 21-88.5 | -88.5647 | 21.2413 | 1872.2613 | 156.3638 | 187.9162 | 229.076 | 265.9631 | 308.7971 | 2.551%
6939 | 21-89 | -88.836 | 21.2413 | 1889.5817 | 154.018 | 186.038 | 226.939 | 263.5445 | 306.0617 | 2.401%
6940 | 21-89 | -89.1074 | 21.2413 | 1906.9086 | 151.8503 | 184.3639 | 224.9835 | 261.3222 | 303.5371 | 2.271%
6941 | 21-89.5 | -89.3787 | 21.2413 | 1924.2417 | 149.9624 | 182.9974 | 223.4 | 259.5549 | 301.5676 | 2.165%
6942 | 21-89.5 | -89.65 | 21.2413 | 1941.5808 | 148.4125 | 181.8665 | 222.1114 | 258.1371 | 300.0121 | 2.082%
6943 | 21-90 | -89.9213 | 21.2413 | 1958.9257 | 147.0579 | 180.8548 | 220.9285 | 256.8066 | 298.5171 | 2.012%
6944 | 21-90 | -90.1926 | 21.2413 | 1976.2762 | 145.8197 | 179.9328 | 219.8433 | 255.5792 | 297.1293 | 1.95%
6945 | 21-90.5 | -90.464 | 21.2413 | 1993.6322 | 144.6886 | 179.0802 | 218.8366 | 254.4324 | 295.8225 | 1.895%
6946 | 21-90.5 | -90.7353 | 21.2413 | 2010.9934 | 143.6342 | 178.2751 | 217.8839 | 253.3385 | 294.5657 | 1.845%
6947 | 22-50 | -50.0371 | 21.5126 | 811.8269 | 130.9868 | 169.1451 | 203.337 | 232.3866 | 265.5873 | 1.337%
6948 | 22-50.5 | -50.3084 | 21.5126 | 796.6886 | 132.5717 | 170.5168 | 204.62 | 233.9134 | 267.4016 | 1.396%
6949 | 22-50.5 | -50.5797 | 21.5126 | 781.6606 | 134.0893 | 171.7659 | 205.8442 | 235.376 | 269.1462 | 1.456%
6950 | 22-51 | -50.851 | 21.5126 | 766.7491 | 135.5689 | 172.9243 | 207.0481 | 236.8289 | 270.8951 | 1.515%
6951 | 22-51 | -51.1224 | 21.5126 | 751.9613 | 137.0511 | 174.0291 | 208.2796 | 238.337 | 272.7342 | 1.577%
6952 | 22-51.5 | -51.3937 | 21.5126 | 737.3046 | 138.4648 | 175.0273 | 209.4536 | 239.7812 | 274.5023 | 1.637%
6953 | 22-51.5 | -51.665 | 21.5126 | 722.787 | 139.8628 | 175.9758 | 210.627 | 241.2354 | 276.2944 | 1.698%
6954 | 22-52 | -51.9363 | 21.5126 | 708.4171 | 141.2924 | 176.9188 | 211.8494 | 242.7637 | 278.192 | 1.763%
6955 | 22-52 | -52.2077 | 21.5126 | 694.2041 | 142.6756 | 177.8029 | 213.0228 | 244.2276 | 280.0066 | 1.828%
6956 | 22-52.5 | -52.479 | 21.5126 | 680.1578 | 144.0614 | 178.6747 | 214.2043 | 245.7069 | 281.8456 | 1.894%
6957 | 22-53 | -52.7503 | 21.5126 | 666.2889 | 145.4815 | 179.5652 | 215.4318 | 247.2539 | 283.7797 | 1.964%
6958 | 22-53 | -53.0216 | 21.5126 | 652.6086 | 146.8586 | 180.4205 | 216.6016 | 248.721 | 285.6064 | 2.034%
6959 | 22-53.5 | -53.2929 | 21.5126 | 639.1292 | 148.2589 | 181.2848 | 217.7785 | 250.1933 | 287.4356 | 2.108%
6960 | 22-53.5 | -53.5643 | 21.5126 | 625.8636 | 149.7099 | 182.1767 | 218.9905 | 251.7076 | 289.3153 | 2.187%
6961 | 22-54 | -53.8356 | 21.5126 | 612.8258 | 151.1116 | 183.0295 | 220.1363 | 253.1292 | 291.0692 | 2.265%
6962 | 22-54 | -54.1069 | 21.5126 | 600.0306 | 152.5194 | 183.8818 | 221.2751 | 254.5373 | 292.8015 | 2.347%
6963 | 22-54.5 | -54.3782 | 21.5126 | 587.494 | 153.9439 | 184.7411 | 222.4175 | 255.9455 | 294.5295 | 2.432%
6964 | 22-54.5 | -54.6495 | 21.5126 | 575.2328 | 155.2546 | 185.5206 | 223.4345 | 257.1841 | 296.0333 | 2.514%
6965 | 22-55 | -54.9209 | 21.5126 | 563.265 | 156.5259 | 186.2738 | 224.413 | 258.3724 | 297.4724 | 2.595%
6966 | 22-55 | -55.1922 | 21.5126 | 551.6099 | 157.7672 | 187.0089 | 225.3647 | 259.5258 | 298.8666 | 2.677%
6967 | 22-55.5 | -55.4635 | 21.5126 | 540.2876 | 158.9007 | 187.6697 | 226.1954 | 260.5121 | 300.0367 | 2.755%
6968 | 22-55.5 | -55.7348 | 21.5126 | 529.3195 | 159.9981 | 188.3176 | 227.0051 | 261.4698 | 301.1684 | 2.832%
6969 | 22-56 | -56.0061 | 21.5126 | 518.7282 | 161.0518 | 188.9571 | 227.8006 | 262.4074 | 302.2729 | 2.909%
6970 | 22-56.5 | -56.2775 | 21.5126 | 508.5372 | 162.0215 | 189.5506 | 228.5197 | 263.2389 | 303.2342 | 2.982%
6971 | 22-56.5 | -56.5488 | 21.5126 | 498.771 | 162.9762 | 190.1613 | 229.2682 | 264.1117 | 304.2517 | 3.056%
6972 | 22-57 | -56.8201 | 21.5126 | 489.4551 | 163.8949 | 190.7838 | 230.037 | 265.0133 | 305.3087 | 3.13%
6973 | 22-57 | -57.0914 | 21.5126 | 480.6158 | 164.7146 | 191.3609 | 230.7399 | 265.829 | 306.2553 | 3.198%
6974 | 22-57.5 | -57.3628 | 21.5126 | 472.2798 | 165.5184 | 191.9618 | 231.4789 | 266.6928 | 307.2648 | 3.266%
6975 | 22-57.5 | -57.6341 | 21.5126 | 464.4742 | 166.2812 | 192.575 | 232.237 | 267.5825 | 308.3083 | 3.333%
6976 | 22-58 | -57.9054 | 21.5126 | 457.2262 | 166.9475 | 193.1452 | 232.9363 | 268.3983 | 309.2599 | 3.394%
6977 | 22-58 | -58.1767 | 21.5126 | 450.5628 | 167.6325 | 193.7621 | 233.7092 | 269.3139 | 310.3437 | 3.456%
6978 | 22-58.5 | -58.448 | 21.5126 | 444.5102 | 168.3051 | 194.4034 | 234.5203 | 270.2815 | 311.4964 | 3.519%
6979 | 22-58.5 | -58.7194 | 21.5126 | 439.0937 | 168.911 | 195.005 | 235.2705 | 271.1672 | 312.5415 | 3.578%
6980 | 22-59 | -58.9907 | 21.5126 | 434.3371 | 169.5169 | 195.6287 | 236.0603 | 272.1101 | 313.6659 | 3.637%
6981 | 22-59.5 | -59.262 | 21.5126 | 430.2623 | 170.104 | 196.2543 | 236.86 | 273.0711 | 314.8189 | 3.694%
6982 | 22-59.5 | -59.5333 | 21.5126 | 426.8889 | 170.6426 | 196.8407 | 237.6117 | 273.9761 | 315.9066 | 3.748%
6983 | 22-60 | -59.8046 | 21.5126 | 424.2336 | 171.1626 | 197.4332 | 238.3876 | 274.9237 | 317.0604 | 3.8%
6984 | 22-60 | -60.076 | 21.5126 | 422.31 | 171.6433 | 198.0063 | 239.1496 | 275.8637 | 318.2151 | 3.847%
6985 | 22-60.5 | -60.3473 | 21.5126 | 421.128 | 172.0671 | 198.5275 | 239.8479 | 276.7294 | 319.2832 | 3.889%
6986 | 22-60.5 | -60.6186 | 21.5126 | 420.6939 | 172.4864 | 199.0613 | 240.5779 | 277.646 | 320.4267 | 3.931%
6987 | 22-61 | -60.8899 | 21.5126 | 421.0101 | 172.8816 | 199.5739 | 241.2877 | 278.5442 | 321.5547 | 3.969%
6988 | 22-61 | -61.1613 | 21.5126 | 422.0749 | 173.2389 | 200.04 | 241.9369 | 279.3686 | 322.5929 | 4.003%
6989 | 22-61.5 | -61.4326 | 21.5126 | 423.8825 | 173.6082 | 200.5269 | 242.6226 | 280.2451 | 323.703 | 4.039%
6990 | 22-61.5 | -61.7039 | 21.5126 | 426.4237 | 173.956 | 200.9851 | 243.2675 | 281.0692 | 324.7464 | 4.072%
6991 | 22-62 | -61.9752 | 21.5126 | 429.6853 | 174.2665 | 201.391 | 243.8342 | 281.7899 | 325.6553 | 4.102%
6992 | 22-62 | -62.2465 | 21.5126 | 433.651 | 174.592 | 201.8226 | 244.4455 | 282.5739 | 326.651 | 4.134%
6993 | 22-62.5 | -62.5179 | 21.5126 | 438.3018 | 174.8951 | 202.2267 | 245.0208 | 283.314 | 327.5933 | 4.162%
6994 | 22-63 | -62.7892 | 21.5126 | 443.6162 | 175.1634 | 202.5828 | 245.5258 | 283.962 | 328.4166 | 4.188%
6995 | 22-63 | -63.0605 | 21.5126 | 449.5704 | 175.4371 | 202.9452 | 246.0384 | 284.619 | 329.2503 | 4.215%
6996 | 22-63.5 | -63.3318 | 21.5126 | 456.1396 | 175.6873 | 203.2705 | 246.49 | 285.1913 | 329.9699 | 4.239%
6997 | 22-63.5 | -63.6031 | 21.5126 | 463.2975 | 175.9163 | 203.5609 | 246.8828 | 285.6813 | 330.5778 | 4.263%
6998 | 22-64 | -63.8745 | 21.5126 | 471.0173 | 176.16 | 203.8689 | 247.2979 | 286.1978 | 331.2174 | 4.288%
6999 | 22-64 | -64.1458 | 21.5126 | 479.2717 | 176.3849 | 204.1489 | 247.669 | 286.6548 | 331.778 | 4.312%
7000 | 22-64.5 | -64.4171 | 21.5126 | 488.0337 | 176.5965 | 204.4118 | 248.0168 | 287.0825 | 332.3022 | 4.335%
7001 | 22-64.5 | -64.6884 | 21.5126 | 497.2764 | 176.826 | 204.7037 | 248.4132 | 287.5785 | 332.9194 | 4.358%
7002 | 22-65 | -64.9598 | 21.5126 | 506.9735 | 177.0251 | 204.9539 | 248.7487 | 287.9948 | 333.4337 | 4.379%
7003 | 22-65 | -65.2311 | 21.5126 | 517.0994 | 177.208 | 205.1835 | 249.0562 | 288.3763 | 333.9052 | 4.399%
7004 | 22-65.5 | -65.5024 | 21.5126 | 527.6294 | 177.411 | 205.446 | 249.4191 | 288.8357 | 334.4827 | 4.419%
7005 | 22-66 | -65.7737 | 21.5126 | 538.5398 | 177.5775 | 205.661 | 249.7161 | 289.2114 | 334.9548 | 4.436%
7006 | 22-66 | -66.045 | 21.5126 | 549.8079 | 177.7258 | 205.8566 | 249.9922 | 289.5653 | 335.4045 | 4.451%
7007 | 22-66.5 | -66.3164 | 21.5126 | 561.4121 | 177.8877 | 206.0803 | 250.3223 | 289.9991 | 335.967 | 4.466%
7008 | 22-66.5 | -66.5877 | 21.5126 | 573.332 | 178.0253 | 206.2796 | 250.6287 | 290.4107 | 336.5097 | 4.477%
7009 | 22-67 | -66.859 | 21.5126 | 585.5483 | 178.157 | 206.483 | 250.9578 | 290.8641 | 337.1189 | 4.487%
7010 | 22-67 | -67.1303 | 21.5126 | 598.0428 | 178.301 | 206.7178 | 251.3526 | 291.4179 | 337.8726 | 4.496%
7011 | 22-67.5 | -67.4016 | 21.5126 | 610.7985 | 178.3932 | 206.8902 | 251.6675 | 291.8756 | 338.5107 | 4.499%
7012 | 22-67.5 | -67.673 | 21.5126 | 623.7992 | 178.4554 | 207.0296 | 251.9455 | 292.2932 | 339.1055 | 4.498%
7013 | 22-68 | -67.9443 | 21.5126 | 637.0299 | 178.5066 | 207.1629 | 252.2266 | 292.7236 | 339.7259 | 4.495%
7014 | 22-68 | -68.2156 | 21.5126 | 650.4766 | 178.4758 | 207.1841 | 252.3441 | 292.9403 | 340.0705 | 4.485%
7015 | 22-68.5 | -68.4869 | 21.5126 | 664.1261 | 178.4016 | 207.1502 | 252.3867 | 293.0633 | 340.2984 | 4.47%
7016 | 22-69 | -68.7583 | 21.5126 | 677.9661 | 178.3037 | 207.0913 | 252.4029 | 293.1592 | 340.4991 | 4.453%
7017 | 22-69 | -69.0296 | 21.5126 | 691.9852 | 178.136 | 206.9379 | 252.2821 | 293.0769 | 340.4706 | 4.429%
7018 | 22-69.5 | -69.3009 | 21.5126 | 706.1727 | 177.9496 | 206.7633 | 252.1366 | 292.9667 | 340.4108 | 4.403%
7019 | 22-69.5 | -69.5722 | 21.5126 | 720.5186 | 177.7601 | 206.5937 | 252.0078 | 292.8854 | 340.3956 | 4.376%
7020 | 22-70 | -69.8435 | 21.5126 | 735.0136 | 177.4859 | 206.3203 | 251.7267 | 292.6046 | 340.1223 | 4.342%
7021 | 22-70 | -70.1149 | 21.5126 | 749.649 | 177.1644 | 205.9957 | 251.3742 | 292.2332 | 339.735 | 4.303%
7022 | 22-70.5 | -70.3862 | 21.5126 | 764.4167 | 176.8057 | 205.6328 | 250.9723 | 291.8021 | 339.276 | 4.261%
7023 | 22-70.5 | -70.6575 | 21.5126 | 779.3092 | 176.3924 | 205.1737 | 250.4167 | 291.1601 | 338.5344 | 4.215%
7024 | 22-71 | -70.9288 | 21.5126 | 794.3194 | 175.9897 | 204.7139 | 249.8578 | 290.5124 | 337.7837 | 4.171%
7025 | 22-71 | -71.2001 | 21.5126 | 809.4407 | 175.6001 | 204.2639 | 249.3132 | 289.8833 | 337.0569 | 4.129%
7026 | 22-71.5 | -71.4715 | 21.5126 | 824.667 | 175.1652 | 203.7432 | 248.6535 | 289.0949 | 336.1155 | 4.084%
7027 | 22-71.5 | -71.7428 | 21.5126 | 839.9925 | 174.7564 | 203.2606 | 248.0526 | 288.3858 | 335.2788 | 4.041%
7028 | 22-72 | -72.0141 | 21.5126 | 855.4119 | 174.3616 | 202.8023 | 247.4898 | 287.7285 | 334.511 | 3.999%
7029 | 22-72.5 | -72.2854 | 21.5126 | 870.9202 | 173.8213 | 202.2207 | 246.7301 | 286.8013 | 333.3821 | 3.947%
7030 | 22-72.5 | -72.5568 | 21.5126 | 886.5126 | 173.1776 | 201.5868 | 245.8906 | 285.7675 | 332.1133 | 3.886%
7031 | 22-73 | -72.8281 | 21.5126 | 902.1848 | 172.5151 | 200.9531 | 245.0419 | 284.7148 | 330.8129 | 3.826%
7032 | 22-73 | -73.0994 | 21.5126 | 917.9325 | 172.1319 | 200.5016 | 244.4212 | 283.9317 | 329.8311 | 3.791%
7033 | 22-73.5 | -73.3707 | 21.5126 | 933.7521 | 172.0212 | 200.3479 | 244.2138 | 283.6734 | 329.5106 | 3.781%
7034 | 22-73.5 | -73.642 | 21.5126 | 949.6398 | 172.0216 | 200.3259 | 244.1865 | 283.6414 | 329.4733 | 3.78%
7035 | 22-74 | -73.9134 | 21.5126 | 965.5923 | 171.7225 | 199.9547 | 243.6539 | 282.952 | 328.5904 | 3.755%
7036 | 22-74 | -74.1847 | 21.5126 | 981.6063 | 170.9792 | 199.3069 | 242.7469 | 281.7961 | 327.1291 | 3.691%
7037 | 22-74.5 | -74.456 | 21.5126 | 997.6789 | 169.9525 | 198.4744 | 241.5884 | 280.3252 | 325.2764 | 3.606%
7038 | 22-74.5 | -74.7273 | 21.5126 | 1013.8072 | 168.9479 | 197.6543 | 240.4338 | 278.8493 | 323.4066 | 3.523%
7039 | 22-75 | -74.9986 | 21.5126 | 1029.9886 | 168.033 | 196.9284 | 239.4165 | 277.5522 | 321.767 | 3.45%
7040 | 22-75.5 | -75.27 | 21.5126 | 1046.2206 | 167.2866 | 196.3198 | 238.5557 | 276.4486 | 320.3653 | 3.391%
7041 | 22-75.5 | -75.5413 | 21.5126 | 1062.5008 | 166.8688 | 195.9029 | 237.942 | 275.6433 | 319.3231 | 3.358%
7042 | 22-76 | -75.8126 | 21.5126 | 1078.827 | 166.8207 | 195.835 | 237.8273 | 275.4825 | 319.1047 | 3.355%
7043 | 22-76 | -76.0839 | 21.5126 | 1095.1971 | 166.9359 | 195.907 | 237.9076 | 275.5696 | 319.1993 | 3.365%
7044 | 22-76.5 | -76.3553 | 21.5126 | 1111.6091 | 166.9014 | 195.7714 | 237.683 | 275.2574 | 318.7776 | 3.363%
7045 | 22-76.5 | -76.6266 | 21.5126 | 1128.0613 | 166.3989 | 195.2547 | 236.9285 | 274.2726 | 317.509 | 3.324%
7046 | 22-77 | -76.8979 | 21.5126 | 1144.5517 | 165.6737 | 194.4859 | 235.8056 | 272.8066 | 315.6196 | 3.267%
7047 | 22-77 | -77.1692 | 21.5126 | 1161.0787 | 165.0743 | 193.7827 | 234.7451 | 271.3969 | 313.7768 | 3.222%
7048 | 22-77.5 | -77.4405 | 21.5126 | 1177.6408 | 164.989 | 193.634 | 234.4441 | 270.9432 | 313.13 | 3.219%
7049 | 22-77.5 | -77.7119 | 21.5126 | 1194.2365 | 165.5028 | 193.9121 | 234.7107 | 271.1899 | 313.344 | 3.263%
7050 | 22-78 | -77.9832 | 21.5126 | 1210.8643 | 166.3622 | 194.4135 | 235.2583 | 271.7704 | 313.954 | 3.337%
7051 | 22-78.5 | -78.2545 | 21.5126 | 1227.5228 | 167.2322 | 194.9518 | 235.8488 | 272.3993 | 314.6186 | 3.413%
7052 | 22-78.5 | -78.5258 | 21.5126 | 1244.2109 | 168.0698 | 195.4875 | 236.4201 | 272.9918 | 315.2252 | 3.491%
7053 | 22-79 | -78.7971 | 21.5126 | 1260.9273 | 168.7992 | 195.9696 | 236.9066 | 273.4692 | 315.679 | 3.562%
7054 | 22-79 | -79.0685 | 21.5126 | 1277.6709 | 169.288 | 196.3551 | 237.266 | 273.791 | 315.943 | 3.614%
7055 | 22-79.5 | -79.3398 | 21.5126 | 1294.4405 | 169.6093 | 196.5689 | 237.3758 | 273.7874 | 315.7879 | 3.653%
7056 | 22-79.5 | -79.6111 | 21.5126 | 1311.2351 | 169.9474 | 196.7796 | 237.472 | 273.7595 | 315.5945 | 3.694%
7057 | 22-80 | -79.8824 | 21.5126 | 1328.0538 | 170.5427 | 197.2923 | 237.9961 | 274.2808 | 316.0998 | 3.76%
7058 | 22-80 | -80.1537 | 21.5126 | 1344.8956 | 171.4446 | 198.1237 | 238.9588 | 275.3553 | 317.2977 | 3.856%
7059 | 22-80.5 | -80.4251 | 21.5126 | 1361.7596 | 172.5038 | 199.1558 | 240.2032 | 276.7887 | 318.9488 | 3.969%
7060 | 22-80.5 | -80.6964 | 21.5126 | 1378.6449 | 173.539 | 200.2442 | 241.5395 | 278.349 | 320.7703 | 4.083%
7061 | 22-81 | -80.9677 | 21.5126 | 1395.5508 | 174.381 | 201.1304 | 242.6008 | 279.5652 | 322.164 | 4.179%
7062 | 22-81 | -81.239 | 21.5126 | 1412.4764 | 175.0368 | 201.8348 | 243.4223 | 280.4874 | 323.1983 | 4.258%
7063 | 22-81.5 | -81.5104 | 21.5126 | 1429.421 | 175.6028 | 202.4729 | 244.1696 | 281.3292 | 324.1461 | 4.327%
7064 | 22-82 | -81.7817 | 21.5126 | 1446.3839 | 176.1199 | 203.0387 | 244.8236 | 282.0581 | 324.9577 | 4.392%
7065 | 22-82 | -82.053 | 21.5126 | 1463.3644 | 176.6247 | 203.5706 | 245.4398 | 282.7461 | 325.7251 | 4.455%
7066 | 22-82.5 | -82.3243 | 21.5126 | 1480.362 | 177.1171 | 204.0979 | 246.0613 | 283.4497 | 326.5215 | 4.517%
7067 | 22-82.5 | -82.5956 | 21.5126 | 1497.3759 | 177.6228 | 204.6521 | 246.7224 | 284.205 | 327.3845 | 4.58%
7068 | 22-83 | -82.867 | 21.5126 | 1514.4055 | 178.1956 | 205.3095 | 247.5438 | 285.1762 | 328.5318 | 4.65%
7069 | 22-83 | -83.1383 | 21.5126 | 1531.4504 | 178.8626 | 206.1125 | 248.5948 | 286.4591 | 330.0928 | 4.728%
7070 | 22-83.5 | -83.4096 | 21.5126 | 1548.5099 | 179.4431 | 206.8316 | 249.5577 | 287.6521 | 331.5635 | 4.795%
7071 | 22-83.5 | -83.6809 | 21.5126 | 1565.5836 | 179.8887 | 207.4134 | 250.3687 | 288.6819 | 332.8603 | 4.844%
7072 | 22-84 | -83.9522 | 21.5126 | 1582.6709 | 180.1943 | 207.8432 | 251.0117 | 289.5321 | 333.9665 | 4.872%
7073 | 22-84 | -84.2236 | 21.5126 | 1599.7714 | 180.2601 | 207.9821 | 251.2804 | 289.9306 | 334.5288 | 4.872%
7074 | 22-84.5 | -84.4949 | 21.5126 | 1616.8845 | 180.2721 | 208.0748 | 251.5188 | 290.3166 | 335.1025 | 4.862%
7075 | 22-85 | -84.7662 | 21.5126 | 1634.01 | 180.302 | 208.2175 | 251.8649 | 290.8681 | 335.9152 | 4.85%
7076 | 22-85 | -85.0375 | 21.5126 | 1651.1473 | 180.1842 | 208.1917 | 252.0103 | 291.1904 | 336.4659 | 4.819%
7077 | 22-85.5 | -85.3089 | 21.5126 | 1668.296 | 179.9126 | 207.9953 | 251.9603 | 291.2968 | 336.7784 | 4.768%
7078 | 22-85.5 | -85.5802 | 21.5126 | 1685.4558 | 179.4361 | 207.6255 | 251.7161 | 291.1926 | 336.8639 | 4.692%
7079 | 22-86 | -85.8515 | 21.5126 | 1702.6262 | 178.6923 | 206.9895 | 251.1326 | 290.6814 | 336.4617 | 4.588%
7080 | 22-86 | -86.1228 | 21.5126 | 1719.807 | 177.5813 | 206.0505 | 250.1707 | 289.723 | 335.5314 | 4.446%
7081 | 22-86.5 | -86.3941 | 21.5126 | 1736.9977 | 176.1127 | 204.7976 | 248.8163 | 288.3008 | 334.0542 | 4.271%
7082 | 22-86.5 | -86.6655 | 21.5126 | 1754.198 | 174.3326 | 203.2212 | 247.028 | 286.3405 | 331.9126 | 4.073%
7083 | 22-87 | -86.9368 | 21.5126 | 1771.4077 | 172.4131 | 201.5431 | 245.1141 | 284.2332 | 329.5995 | 3.871%
7084 | 22-87 | -87.2081 | 21.5126 | 1788.6263 | 170.3729 | 199.7767 | 243.0908 | 281.9974 | 327.1359 | 3.668%
7085 | 22-87.5 | -87.4794 | 21.5126 | 1805.8536 | 168.1554 | 197.8352 | 240.8106 | 279.4254 | 324.2376 | 3.461%
7086 | 22-88 | -87.7507 | 21.5126 | 1823.0894 | 165.847 | 195.8456 | 238.4657 | 276.7725 | 321.2391 | 3.259%
7087 | 22-88 | -88.0221 | 21.5126 | 1840.3332 | 163.466 | 193.8113 | 236.07 | 274.0553 | 318.1594 | 3.063%
7088 | 22-88.5 | -88.2934 | 21.5126 | 1857.5849 | 161.0673 | 191.7525 | 233.6376 | 271.2735 | 314.979 | 2.878%
7089 | 22-88.5 | -88.5647 | 21.5126 | 1874.8443 | 158.8136 | 189.8793 | 231.466 | 268.8119 | 312.1904 | 2.714%
7090 | 22-89 | -88.836 | 21.5126 | 1892.1109 | 156.7004 | 188.1874 | 229.5284 | 266.6322 | 309.7408 | 2.57%
7091 | 22-89 | -89.1074 | 21.5126 | 1909.3847 | 154.7272 | 186.6531 | 227.7286 | 264.5943 | 307.4345 | 2.443%
7092 | 22-89.5 | -89.3787 | 21.5126 | 1926.6653 | 152.9657 | 185.3439 | 226.2085 | 262.895 | 305.5374 | 2.336%
7093 | 22-89.5 | -89.65 | 21.5126 | 1943.9526 | 151.4536 | 184.2125 | 224.9052 | 261.4475 | 303.9332 | 2.248%
7094 | 22-90 | -89.9213 | 21.5126 | 1961.2463 | 150.0812 | 183.1664 | 223.6654 | 260.0381 | 302.3311 | 2.171%
7095 | 22-90 | -90.1926 | 21.5126 | 1978.5462 | 148.8123 | 182.2063 | 222.5202 | 258.7294 | 300.8355 | 2.102%
7096 | 22-90.5 | -90.464 | 21.5126 | 1995.8522 | 147.6376 | 181.3145 | 221.4474 | 257.4952 | 299.4151 | 2.041%
7097 | 22-90.5 | -90.7353 | 21.5126 | 2013.1639 | 146.5259 | 180.4674 | 220.4202 | 256.3046 | 298.0343 | 1.984%
7098 | 22-50 | -50.0371 | 21.7839 | 821.1958 | 129.0495 | 167.5079 | 201.8752 | 230.7286 | 263.707 | 1.269%
7099 | 22-50.5 | -50.3084 | 21.7839 | 806.2594 | 130.6721 | 168.9926 | 203.2013 | 232.3033 | 265.5745 | 1.327%
7100 | 22-50.5 | -50.5797 | 21.7839 | 791.4388 | 132.2287 | 170.3464 | 204.4664 | 233.8104 | 267.3672 | 1.385%
7101 | 22-51 | -50.851 | 21.7839 | 776.7406 | 133.7463 | 171.5994 | 205.7061 | 235.3005 | 269.1543 | 1.444%
7102 | 22-51 | -51.1224 | 21.7839 | 762.1719 | 135.263 | 172.7865 | 206.9657 | 236.8353 | 271.0178 | 1.504%
7103 | 22-51.5 | -51.3937 | 21.7839 | 747.7404 | 136.7083 | 173.8541 | 208.1627 | 238.2994 | 272.8014 | 1.563%
7104 | 22-51.5 | -51.665 | 21.7839 | 733.4541 | 138.1346 | 174.8603 | 209.3551 | 239.7692 | 274.6044 | 1.623%
7105 | 22-52 | -51.9363 | 21.7839 | 719.3218 | 139.5887 | 175.8495 | 210.5927 | 241.3093 | 276.509 | 1.687%
7106 | 22-52 | -52.2077 | 21.7839 | 705.3528 | 140.9969 | 176.7692 | 211.7814 | 242.7858 | 278.3323 | 1.75%
7107 | 22-52.5 | -52.479 | 21.7839 | 691.5569 | 142.4106 | 177.6717 | 212.9822 | 244.2834 | 280.188 | 1.815%
7108 | 22-53 | -52.7503 | 21.7839 | 677.9448 | 143.8634 | 178.5896 | 214.2345 | 245.8564 | 282.1492 | 1.884%
7109 | 22-53 | -53.0216 | 21.7839 | 664.5278 | 145.274 | 179.4681 | 215.4289 | 247.3492 | 284.0023 | 1.953%
7110 | 22-53.5 | -53.2929 | 21.7839 | 651.3179 | 146.7104 | 180.3574 | 216.6358 | 248.8558 | 285.8709 | 2.026%
7111 | 22-53.5 | -53.5643 | 21.7839 | 638.3282 | 148.2022 | 181.2778 | 217.8861 | 250.4177 | 287.8094 | 2.104%
7112 | 22-54 | -53.8356 | 21.7839 | 625.5723 | 149.6499 | 182.1633 | 219.0788 | 251.9 | 289.6408 | 2.182%
7113 | 22-54 | -54.1069 | 21.7839 | 613.0649 | 151.1116 | 183.0541 | 220.2754 | 253.3845 | 291.4726 | 2.264%
7114 | 22-54.5 | -54.3782 | 21.7839 | 600.8214 | 152.5986 | 183.9586 | 221.4871 | 254.8856 | 293.3226 | 2.35%
7115 | 22-54.5 | -54.6495 | 21.7839 | 588.8585 | 153.976 | 184.7863 | 222.5778 | 256.2226 | 294.9552 | 2.432%
7116 | 22-55 | -54.9209 | 21.7839 | 577.1935 | 155.3176 | 185.5894 | 223.6315 | 257.5107 | 296.5244 | 2.516%
7117 | 22-55 | -55.1922 | 21.7839 | 565.8449 | 156.6318 | 186.3752 | 224.6586 | 258.7632 | 298.047 | 2.599%
7118 | 22-55.5 | -55.4635 | 21.7839 | 554.8323 | 157.8365 | 187.0831 | 225.5565 | 259.8362 | 299.3275 | 2.679%
7119 | 22-55.5 | -55.7348 | 21.7839 | 544.1758 | 159.0004 | 187.771 | 226.421 | 260.8626 | 300.545 | 2.759%
7120 | 22-56 | -56.0061 | 21.7839 | 533.8971 | 160.116 | 188.4431 | 227.258 | 261.85 | 301.709 | 2.838%
7121 | 22-56.5 | -56.2775 | 21.7839 | 524.0182 | 161.1425 | 189.0625 | 228.0066 | 262.7139 | 302.7059 | 2.914%
7122 | 22-56.5 | -56.5488 | 21.7839 | 514.5623 | 162.1541 | 189.696 | 228.7785 | 263.6101 | 303.7464 | 2.99%
7123 | 22-57 | -56.8201 | 21.7839 | 505.5531 | 163.1297 | 190.3379 | 229.5642 | 264.5255 | 304.8126 | 3.067%
7124 | 22-57 | -57.0914 | 21.7839 | 497.0149 | 164.0051 | 190.9306 | 230.2758 | 265.3425 | 305.7507 | 3.138%
7125 | 22-57.5 | -57.3628 | 21.7839 | 488.9724 | 164.8646 | 191.5432 | 231.0158 | 266.196 | 306.735 | 3.21%
7126 | 22-57.5 | -57.6341 | 21.7839 | 481.4505 | 165.6786 | 192.1647 | 231.7675 | 267.0639 | 307.7368 | 3.28%
7127 | 22-58 | -57.9054 | 21.7839 | 474.4739 | 166.3929 | 192.742 | 232.4554 | 267.8491 | 308.6328 | 3.344%
7128 | 22-58 | -58.1767 | 21.7839 | 468.0671 | 167.1271 | 193.3692 | 233.2203 | 268.7377 | 309.6649 | 3.411%
7129 | 22-58.5 | -58.448 | 21.7839 | 462.2538 | 167.8496 | 194.0234 | 234.027 | 269.6825 | 310.7709 | 3.478%
7130 | 22-58.5 | -58.7194 | 21.7839 | 457.0565 | 168.5054 | 194.6402 | 234.7756 | 270.5491 | 311.774 | 3.542%
7131 | 22-59 | -58.9907 | 21.7839 | 452.4966 | 169.165 | 195.2859 | 235.5754 | 271.4889 | 312.878 | 3.606%
7132 | 22-59.5 | -59.262 | 21.7839 | 448.5936 | 169.8074 | 195.9393 | 236.395 | 272.4609 | 314.0298 | 3.669%
7133 | 22-59.5 | -59.5333 | 21.7839 | 445.3646 | 170.4012 | 196.5578 | 237.1731 | 273.3856 | 315.1278 | 3.729%
7134 | 22-60 | -59.8046 | 21.7839 | 442.8244 | 170.9764 | 197.1859 | 237.9804 | 274.3593 | 316.3 | 3.786%
7135 | 22-60 | -60.076 | 21.7839 | 440.985 | 171.5098 | 197.7968 | 238.7776 | 275.3308 | 317.4806 | 3.84%
7136 | 22-60.5 | -60.3473 | 21.7839 | 439.8552 | 171.9806 | 198.356 | 239.5135 | 276.2324 | 318.5814 | 3.887%
7137 | 22-60.5 | -60.6186 | 21.7839 | 439.4403 | 172.442 | 198.9279 | 240.2839 | 277.1907 | 319.7672 | 3.933%
7138 | 22-61 | -60.8899 | 21.7839 | 439.7425 | 172.8724 | 199.4785 | 241.0366 | 278.1357 | 320.9458 | 3.976%
7139 | 22-61 | -61.1613 | 21.7839 | 440.7603 | 173.2616 | 199.9812 | 241.7299 | 279.0106 | 322.0421 | 4.014%
7140 | 22-61.5 | -61.4326 | 21.7839 | 442.4887 | 173.6581 | 200.5012 | 242.4583 | 279.9387 | 323.2142 | 4.053%
7141 | 22-61.5 | -61.7039 | 21.7839 | 444.9194 | 174.0284 | 200.9887 | 243.1436 | 280.8138 | 324.3215 | 4.088%
7142 | 22-62 | -61.9752 | 21.7839 | 448.041 | 174.3572 | 201.4202 | 243.7487 | 281.5851 | 325.2962 | 4.12%
7143 | 22-62 | -62.2465 | 21.7839 | 451.8393 | 174.6976 | 201.8753 | 244.3982 | 282.422 | 326.363 | 4.153%
7144 | 22-62.5 | -62.5179 | 21.7839 | 456.2972 | 175.0116 | 202.2985 | 245.0071 | 283.21 | 327.3711 | 4.182%
7145 | 22-63 | -62.7892 | 21.7839 | 461.3956 | 175.2869 | 202.6687 | 245.5388 | 283.8973 | 328.2495 | 4.208%
7146 | 22-63 | -63.0605 | 21.7839 | 467.1136 | 175.5645 | 203.0421 | 246.075 | 284.5905 | 329.1354 | 4.235%
7147 | 22-63.5 | -63.3318 | 21.7839 | 473.4287 | 175.8157 | 203.3751 | 246.5463 | 285.1947 | 329.9025 | 4.259%
7148 | 22-63.5 | -63.6031 | 21.7839 | 480.3173 | 176.0443 | 203.6713 | 246.9562 | 285.7131 | 330.5533 | 4.282%
7149 | 22-64 | -63.8745 | 21.7839 | 487.7551 | 176.2888 | 203.9858 | 247.3881 | 286.257 | 331.2336 | 4.307%
7150 | 22-64 | -64.1458 | 21.7839 | 495.7175 | 176.515 | 204.2713 | 247.7723 | 286.7347 | 331.8246 | 4.33%
7151 | 22-64.5 | -64.4171 | 21.7839 | 504.1794 | 176.7287 | 204.5384 | 248.1282 | 287.1745 | 332.3658 | 4.353%
7152 | 22-64.5 | -64.6884 | 21.7839 | 513.1162 | 176.9617 | 204.8344 | 248.5295 | 287.6758 | 332.9889 | 4.377%
7153 | 22-65 | -64.9598 | 21.7839 | 522.5035 | 177.1652 | 205.0874 | 248.8645 | 288.0884 | 333.4952 | 4.399%
7154 | 22-65 | -65.2311 | 21.7839 | 532.3175 | 177.3533 | 205.3186 | 249.167 | 288.4579 | 333.9454 | 4.42%
7155 | 22-65.5 | -65.5024 | 21.7839 | 542.5349 | 177.5633 | 205.5829 | 249.5218 | 288.8987 | 334.4909 | 4.442%
7156 | 22-66 | -65.7737 | 21.7839 | 553.1334 | 177.737 | 205.7978 | 249.8051 | 289.2467 | 334.9171 | 4.461%
7157 | 22-66 | -66.045 | 21.7839 | 564.0914 | 177.8931 | 205.9932 | 250.0659 | 289.5697 | 335.3157 | 4.478%
7158 | 22-66.5 | -66.3164 | 21.7839 | 575.3885 | 178.0643 | 206.2185 | 250.3832 | 289.9759 | 335.8312 | 4.495%
7159 | 22-66.5 | -66.5877 | 21.7839 | 587.005 | 178.2133 | 206.4219 | 250.68 | 290.3636 | 336.3315 | 4.509%
7160 | 22-67 | -66.859 | 21.7839 | 598.9223 | 178.3589 | 206.6328 | 251.0046 | 290.7997 | 336.9066 | 4.521%
7161 | 22-67 | -67.1303 | 21.7839 | 611.1228 | 178.5193 | 206.879 | 251.4007 | 291.344 | 337.6364 | 4.533%
7162 | 22-67.5 | -67.4016 | 21.7839 | 623.5898 | 178.6294 | 207.065 | 251.7211 | 291.7981 | 338.259 | 4.539%
7163 | 22-67.5 | -67.673 | 21.7839 | 636.3076 | 178.7115 | 207.2227 | 252.0135 | 292.2256 | 338.8572 | 4.541%
7164 | 22-68 | -67.9443 | 21.7839 | 649.2616 | 178.7852 | 207.3801 | 252.3205 | 292.6832 | 339.5058 | 4.541%
7165 | 22-68 | -68.2156 | 21.7839 | 662.4377 | 178.7885 | 207.4432 | 252.4926 | 292.9665 | 339.9315 | 4.534%
7166 | 22-68.5 | -68.4869 | 21.7839 | 675.8229 | 178.7622 | 207.4718 | 252.6227 | 293.2008 | 340.3 | 4.524%
7167 | 22-69 | -68.7583 | 21.7839 | 689.4051 | 178.7262 | 207.4963 | 252.7588 | 293.4521 | 340.6996 | 4.512%
7168 | 22-69 | -69.0296 | 21.7839 | 703.1729 | 178.6214 | 207.428 | 252.7613 | 293.53 | 340.877 | 4.493%
7169 | 22-69.5 | -69.3009 | 21.7839 | 717.1154 | 178.5002 | 207.3415 | 252.743 | 293.585 | 341.0291 | 4.473%
7170 | 22-69.5 | -69.5722 | 21.7839 | 731.2227 | 178.3805 | 207.2636 | 252.7462 | 293.6747 | 341.233 | 4.452%
7171 | 22-70 | -69.8435 | 21.7839 | 745.4853 | 178.1938 | 207.0938 | 252.6147 | 293.588 | 341.2089 | 4.426%
7172 | 22-70 | -70.1149 | 21.7839 | 759.8946 | 177.9758 | 206.8838 | 252.4284 | 293.4327 | 341.0993 | 4.396%
7173 | 22-70.5 | -70.3862 | 21.7839 | 774.4422 | 177.7329 | 206.6446 | 252.206 | 293.2352 | 340.9406 | 4.364%
7174 | 22-70.5 | -70.6575 | 21.7839 | 789.1206 | 177.4114 | 206.2886 | 251.8002 | 292.7884 | 340.4502 | 4.325%
7175 | 22-71 | -70.9288 | 21.7839 | 803.9224 | 177.0761 | 205.9119 | 251.3616 | 292.2971 | 339.9004 | 4.287%
7176 | 22-71 | -71.2001 | 21.7839 | 818.841 | 176.7346 | 205.5261 | 250.9085 | 291.7859 | 339.3241 | 4.248%
7177 | 22-71.5 | -71.4715 | 21.7839 | 833.8701 | 176.3438 | 205.0621 | 250.3267 | 291.0956 | 338.5056 | 4.206%
7178 | 22-71.5 | -71.7428 | 21.7839 | 849.0038 | 175.9658 | 204.6161 | 249.7721 | 290.4417 | 337.7346 | 4.165%
7179 | 22-72 | -72.0141 | 21.7839 | 864.2365 | 175.5934 | 204.1782 | 249.2295 | 289.8037 | 336.9844 | 4.125%
7180 | 22-72.5 | -72.2854 | 21.7839 | 879.563 | 175.1071 | 203.628 | 248.5031 | 288.9111 | 335.8907 | 4.077%
7181 | 22-72.5 | -72.5568 | 21.7839 | 894.9786 | 174.559 | 203.0547 | 247.7378 | 287.9638 | 334.7228 | 4.025%
7182 | 22-73 | -72.8281 | 21.7839 | 910.4786 | 174.0065 | 202.4918 | 246.9783 | 287.0172 | 333.5486 | 3.973%
7183 | 22-73 | -73.0994 | 21.7839 | 926.0588 | 173.644 | 202.0453 | 246.3569 | 286.2275 | 332.5523 | 3.939%
7184 | 22-73.5 | -73.3707 | 21.7839 | 941.7151 | 173.4728 | 201.8217 | 246.0444 | 285.8294 | 332.0492 | 3.924%
7185 | 22-73.5 | -73.642 | 21.7839 | 957.4439 | 173.3724 | 201.6876 | 245.8528 | 285.5823 | 331.7337 | 3.915%
7186 | 22-74 | -73.9134 | 21.7839 | 973.2414 | 173.0076 | 201.2578 | 245.2313 | 284.7745 | 330.6956 | 3.883%
7187 | 22-74 | -74.1847 | 21.7839 | 989.1045 | 172.3109 | 200.6325 | 244.3502 | 283.6471 | 329.2657 | 3.822%
7188 | 22-74.5 | -74.456 | 21.7839 | 1005.03 | 171.4079 | 199.8798 | 243.2991 | 282.3097 | 327.578 | 3.745%
7189 | 22-74.5 | -74.7273 | 21.7839 | 1021.0148 | 170.5328 | 199.1456 | 242.2633 | 280.9839 | 325.8965 | 3.671%
7190 | 22-75 | -74.9986 | 21.7839 | 1037.0563 | 169.736 | 198.4999 | 241.3601 | 279.8336 | 324.4439 | 3.604%
7191 | 22-75.5 | -75.27 | 21.7839 | 1053.1518 | 169.0857 | 197.9565 | 240.596 | 278.8573 | 323.2073 | 3.551%
7192 | 22-75.5 | -75.5413 | 21.7839 | 1069.2988 | 168.7175 | 197.5692 | 240.0321 | 278.1219 | 322.2601 | 3.521%
7193 | 22-76 | -75.8126 | 21.7839 | 1085.495 | 168.6299 | 197.4678 | 239.8811 | 277.9228 | 322.0017 | 3.514%
7194 | 22-76 | -76.0839 | 21.7839 | 1101.7382 | 168.634 | 197.4562 | 239.8565 | 277.8857 | 321.949 | 3.515%
7195 | 22-76.5 | -76.3553 | 21.7839 | 1118.0263 | 168.4682 | 197.2243 | 239.5105 | 277.4287 | 321.3549 | 3.501%
7196 | 22-76.5 | -76.6266 | 21.7839 | 1134.3574 | 167.9195 | 196.675 | 238.7233 | 276.412 | 320.0563 | 3.457%
7197 | 22-77 | -76.8979 | 21.7839 | 1150.7295 | 167.2089 | 195.9349 | 237.6544 | 275.0253 | 318.2782 | 3.4%
7198 | 22-77 | -77.1692 | 21.7839 | 1167.1408 | 166.6424 | 195.2857 | 236.6849 | 273.7436 | 316.6098 | 3.355%
7199 | 22-77.5 | -77.4405 | 21.7839 | 1183.5898 | 166.5359 | 195.1216 | 236.3798 | 273.2978 | 315.9868 | 3.35%
7200 | 22-77.5 | -77.7119 | 21.7839 | 1200.0749 | 166.9333 | 195.3157 | 236.5473 | 273.4323 | 316.0737 | 3.386%
7201 | 22-78 | -77.9832 | 21.7839 | 1216.5945 | 167.6174 | 195.6878 | 236.9324 | 273.8197 | 316.4543 | 3.446%
7202 | 22-78.5 | -78.2545 | 21.7839 | 1233.1472 | 168.3199 | 196.1017 | 237.3664 | 274.2623 | 316.8977 | 3.511%
7203 | 22-78.5 | -78.5258 | 21.7839 | 1249.7316 | 168.9971 | 196.5146 | 237.7819 | 274.6687 | 317.2819 | 3.575%
7204 | 22-79 | -78.7971 | 21.7839 | 1266.3465 | 169.5821 | 196.8818 | 238.1216 | 274.9695 | 317.5237 | 3.635%
7205 | 22-79 | -79.0685 | 21.7839 | 1282.9907 | 169.9606 | 197.1759 | 238.3648 | 275.1524 | 317.6216 | 3.678%
7206 | 22-79.5 | -79.3398 | 21.7839 | 1299.6629 | 170.2096 | 197.3229 | 238.3911 | 275.0498 | 317.3495 | 3.71%
7207 | 22-79.5 | -79.6111 | 21.7839 | 1316.3621 | 170.4989 | 197.4798 | 238.4203 | 274.943 | 317.0631 | 3.747%
7208 | 22-80 | -79.8824 | 21.7839 | 1333.0872 | 171.0453 | 197.9339 | 238.8698 | 275.3748 | 317.4614 | 3.809%
7209 | 22-80 | -80.1537 | 21.7839 | 1349.8373 | 171.8955 | 198.7019 | 239.7502 | 276.3492 | 318.5378 | 3.9%
7210 | 22-80.5 | -80.4251 | 21.7839 | 1366.6113 | 172.9028 | 199.6692 | 240.9082 | 277.6761 | 320.058 | 4.009%
7211 | 22-80.5 | -80.6964 | 21.7839 | 1383.4084 | 173.8889 | 200.6949 | 242.1589 | 279.1291 | 321.7459 | 4.118%
7212 | 22-81 | -80.9677 | 21.7839 | 1400.2276 | 174.6858 | 201.5221 | 243.1381 | 280.2411 | 323.0082 | 4.211%
7213 | 22-81 | -81.239 | 21.7839 | 1417.0682 | 175.3013 | 202.1738 | 243.8858 | 281.0693 | 323.924 | 4.286%
7214 | 22-81.5 | -81.5104 | 21.7839 | 1433.9294 | 175.8322 | 202.7667 | 244.571 | 281.8327 | 324.7738 | 4.351%
7215 | 22-82 | -81.7817 | 21.7839 | 1450.8103 | 176.3176 | 203.2905 | 245.1657 | 282.4858 | 325.4893 | 4.413%
7216 | 22-82 | -82.053 | 21.7839 | 1467.7103 | 176.7958 | 203.786 | 245.7286 | 283.1043 | 326.1672 | 4.474%
7217 | 22-82.5 | -82.3243 | 21.7839 | 1484.6288 | 177.2685 | 204.2852 | 246.3076 | 283.7513 | 326.8896 | 4.534%
7218 | 22-82.5 | -82.5956 | 21.7839 | 1501.5649 | 177.7603 | 204.8185 | 246.9361 | 284.4627 | 327.6944 | 4.596%
7219 | 22-83 | -82.867 | 21.7839 | 1518.5182 | 178.3238 | 205.4614 | 247.7336 | 285.4007 | 328.7972 | 4.666%
7220 | 22-83 | -83.1383 | 21.7839 | 1535.4879 | 178.9859 | 206.2555 | 248.7686 | 286.6605 | 330.3262 | 4.744%
7221 | 22-83.5 | -83.4096 | 21.7839 | 1552.4735 | 179.5649 | 206.9704 | 249.7226 | 287.8398 | 331.7771 | 4.811%
7222 | 22-83.5 | -83.6809 | 21.7839 | 1569.4745 | 180.0122 | 207.5526 | 250.5314 | 288.8649 | 333.0659 | 4.86%
7223 | 22-84 | -83.9522 | 21.7839 | 1586.4903 | 180.3227 | 207.9874 | 251.1792 | 289.7196 | 334.1761 | 4.89%
7224 | 22-84 | -84.2236 | 21.7839 | 1603.5203 | 180.3977 | 208.1371 | 251.4615 | 290.1342 | 334.7574 | 4.89%
7225 | 22-84.5 | -84.4949 | 21.7839 | 1620.5642 | 180.4224 | 208.2453 | 251.7201 | 290.5448 | 335.3611 | 4.882%
7226 | 22-85 | -84.7662 | 21.7839 | 1637.6214 | 180.4682 | 208.4076 | 252.0918 | 291.1276 | 336.2119 | 4.872%
7227 | 22-85 | -85.0375 | 21.7839 | 1654.6915 | 180.3676 | 208.4003 | 252.2573 | 291.4711 | 336.7849 | 4.843%
7228 | 22-85.5 | -85.3089 | 21.7839 | 1671.7741 | 180.1164 | 208.2254 | 252.2303 | 291.6014 | 337.122 | 4.795%
7229 | 22-85.5 | -85.5802 | 21.7839 | 1688.8686 | 179.6649 | 207.883 | 252.0168 | 291.5305 | 337.2433 | 4.722%
7230 | 22-86 | -85.8515 | 21.7839 | 1705.9748 | 178.9767 | 207.3134 | 251.5171 | 291.1192 | 336.9601 | 4.623%
7231 | 22-86 | -86.1228 | 21.7839 | 1723.0922 | 177.9871 | 206.4805 | 250.6919 | 290.3259 | 336.229 | 4.493%
7232 | 22-86.5 | -86.3941 | 21.7839 | 1740.2205 | 176.6968 | 205.37 | 249.5219 | 289.1274 | 335.0224 | 4.335%
7233 | 22-86.5 | -86.6655 | 21.7839 | 1757.3592 | 175.109 | 203.942 | 247.9261 | 287.4008 | 333.1641 | 4.153%
7234 | 22-87 | -86.9368 | 21.7839 | 1774.5081 | 173.3955 | 202.4193 | 246.214 | 285.5386 | 331.1479 | 3.966%
7235 | 22-87 | -87.2081 | 21.7839 | 1791.6669 | 171.5735 | 200.8151 | 244.4008 | 283.5577 | 328.9929 | 3.778%
7236 | 22-87.5 | -87.4794 | 21.7839 | 1808.8351 | 169.5829 | 199.0375 | 242.3306 | 281.2383 | 326.3983 | 3.586%
7237 | 22-88 | -87.7507 | 21.7839 | 1826.0125 | 167.5082 | 197.2129 | 240.1948 | 278.8356 | 323.6985 | 3.396%
7238 | 22-88 | -88.0221 | 21.7839 | 1843.1988 | 165.366 | 195.3519 | 238.0068 | 276.3647 | 320.9108 | 3.212%
7239 | 22-88.5 | -88.2934 | 21.7839 | 1860.3937 | 163.2077 | 193.4701 | 235.7747 | 273.8189 | 318.0084 | 3.036%
7240 | 22-88.5 | -88.5647 | 21.7839 | 1877.5969 | 161.1971 | 191.7818 | 233.8078 | 271.6008 | 315.5095 | 2.881%
7241 | 22-89 | -88.836 | 21.7839 | 1894.8082 | 159.3186 | 190.2691 | 232.0677 | 269.6573 | 313.342 | 2.744%
7242 | 22-89 | -89.1074 | 21.7839 | 1912.0272 | 157.5408 | 188.8654 | 230.4191 | 267.7967 | 311.2437 | 2.622%
7243 | 22-89.5 | -89.3787 | 21.7839 | 1929.2538 | 155.9098 | 187.612 | 228.958 | 266.158 | 309.4077 | 2.515%
7244 | 22-89.5 | -89.65 | 21.7839 | 1946.4876 | 154.4395 | 186.4789 | 227.6357 | 264.6736 | 307.743 | 2.422%
7245 | 22-90 | -89.9213 | 21.7839 | 1963.7285 | 153.0535 | 185.3981 | 226.3362 | 263.1794 | 306.0249 | 2.338%
7246 | 22-90 | -90.1926 | 21.7839 | 1980.9763 | 151.7586 | 184.4001 | 225.1289 | 261.7846 | 304.413 | 2.263%
7247 | 22-90.5 | -90.464 | 21.7839 | 1998.2306 | 150.5457 | 183.4657 | 223.9888 | 260.4587 | 302.8705 | 2.195%
7248 | 22-90.5 | -90.7353 | 21.7839 | 2015.4914 | 149.382 | 182.5704 | 222.8865 | 259.1678 | 301.3579 | 2.131%
7249 | 22-50 | -50.0371 | 22.0553 | 830.8777 | 127.1101 | 165.768 | 200.2991 | 228.877 | 261.5333 | 1.203%
7250 | 22-50.5 | -50.3084 | 22.0553 | 816.1443 | 128.764 | 167.3688 | 201.6671 | 230.5006 | 263.4579 | 1.26%
7251 | 22-50.5 | -50.5797 | 22.0553 | 801.5321 | 130.3538 | 168.8311 | 202.974 | 232.057 | 265.3085 | 1.317%
7252 | 22-51 | -50.851 | 22.0553 | 787.0478 | 131.9035 | 170.1827 | 204.2519 | 233.5918 | 267.1479 | 1.374%
7253 | 22-51 | -51.1224 | 22.0553 | 772.6986 | 133.4488 | 171.4564 | 205.5426 | 235.1618 | 269.051 | 1.433%
7254 | 22-51.5 | -51.3937 | 22.0553 | 758.4922 | 134.9197 | 172.5978 | 206.7652 | 236.6537 | 270.865 | 1.491%
7255 | 22-51.5 | -51.665 | 22.0553 | 744.4369 | 136.368 | 173.6657 | 207.9784 | 238.146 | 272.6919 | 1.55%
7256 | 22-52 | -51.9363 | 22.0553 | 730.5415 | 137.8395 | 174.7043 | 209.2318 | 239.7028 | 274.6141 | 1.611%
7257 | 22-52 | -52.2077 | 22.0553 | 716.8151 | 139.2646 | 175.6621 | 210.4357 | 241.1958 | 276.4553 | 1.673%
7258 | 22-52.5 | -52.479 | 22.0553 | 703.2678 | 140.6975 | 176.5965 | 211.6541 | 242.7136 | 278.3342 | 1.736%
7259 | 22-53 | -52.7503 | 22.0553 | 689.9102 | 142.1728 | 177.5422 | 212.9286 | 244.313 | 280.3267 | 1.803%
7260 | 22-53 | -53.0216 | 22.0553 | 676.7535 | 143.6067 | 178.4409 | 214.1467 | 245.8345 | 282.2146 | 1.871%
7261 | 22-53.5 | -53.2929 | 22.0553 | 663.8096 | 145.0697 | 179.3512 | 215.3837 | 247.3799 | 284.1327 | 1.942%
7262 | 22-53.5 | -53.5643 | 22.0553 | 651.0914 | 146.5928 | 180.297 | 216.6731 | 248.9944 | 286.1402 | 2.019%
7263 | 22-54 | -53.8356 | 22.0553 | 638.6123 | 148.0774 | 181.2115 | 217.9118 | 250.5391 | 288.0544 | 2.096%
7264 | 22-54 | -54.1069 | 22.0553 | 626.3867 | 149.5833 | 182.1367 | 219.1624 | 252.0966 | 289.9826 | 2.177%
7265 | 22-54.5 | -54.3782 | 22.0553 | 614.4297 | 151.123 | 183.0815 | 220.4366 | 253.6817 | 291.9432 | 2.263%
7266 | 22-54.5 | -54.6495 | 22.0553 | 602.7573 | 152.5591 | 183.9537 | 221.5954 | 255.1099 | 293.6955 | 2.346%
7267 | 22-55 | -54.9209 | 22.0553 | 591.3864 | 153.9646 | 184.8046 | 222.7212 | 256.4935 | 295.3893 | 2.43%
7268 | 22-55 | -55.1922 | 22.0553 | 580.3348 | 155.3484 | 185.6406 | 223.8227 | 257.8439 | 297.0387 | 2.515%
7269 | 22-55.5 | -55.4635 | 22.0553 | 569.621 | 156.6231 | 186.3962 | 224.7894 | 259.006 | 298.433 | 2.597%
7270 | 22-55.5 | -55.7348 | 22.0553 | 559.2645 | 157.8542 | 187.1261 | 225.7124 | 260.1066 | 299.7438 | 2.678%
7271 | 22-56 | -56.0061 | 22.0553 | 549.2856 | 159.0342 | 187.8338 | 226.5964 | 261.1518 | 300.9785 | 2.759%
7272 | 22-56.5 | -56.2775 | 22.0553 | 539.7052 | 160.1214 | 188.4828 | 227.3813 | 262.0579 | 302.0247 | 2.837%
7273 | 22-56.5 | -56.5488 | 22.0553 | 530.545 | 161.194 | 189.142 | 228.1812 | 262.9839 | 303.0965 | 2.916%
7274 | 22-57 | -56.8201 | 22.0553 | 521.827 | 162.2307 | 189.8053 | 228.986 | 263.9153 | 304.1744 | 2.995%
7275 | 22-57 | -57.0914 | 22.0553 | 513.5738 | 163.1648 | 190.4139 | 229.7057 | 264.7321 | 305.1012 | 3.068%
7276 | 22-57.5 | -57.3628 | 22.0553 | 505.8082 | 164.0821 | 191.0379 | 230.4457 | 265.5737 | 306.0579 | 3.143%
7277 | 22-57.5 | -57.6341 | 22.0553 | 498.553 | 164.9529 | 191.6669 | 231.1903 | 266.4192 | 307.0176 | 3.217%
7278 | 22-58 | -57.9054 | 22.0553 | 491.8308 | 165.7214 | 192.2514 | 231.8685 | 267.1771 | 307.8635 | 3.285%
7279 | 22-58 | -58.1767 | 22.0553 | 485.6637 | 166.5098 | 192.8875 | 232.6244 | 268.0381 | 308.844 | 3.356%
7280 | 22-58.5 | -58.448 | 22.0553 | 480.0732 | 167.2863 | 193.5526 | 233.4237 | 268.9565 | 309.8989 | 3.428%
7281 | 22-58.5 | -58.7194 | 22.0553 | 475.0797 | 167.9948 | 194.1825 | 234.1677 | 269.7999 | 310.8546 | 3.496%
7282 | 22-59 | -58.9907 | 22.0553 | 470.702 | 168.7105 | 194.8482 | 234.974 | 270.7318 | 311.9316 | 3.565%
7283 | 22-59.5 | -59.262 | 22.0553 | 466.9576 | 169.4108 | 195.5279 | 235.8103 | 271.7098 | 313.0751 | 3.634%
7284 | 22-59.5 | -59.5333 | 22.0553 | 463.8619 | 170.0624 | 196.1775 | 236.6126 | 272.6508 | 314.1783 | 3.699%
7285 | 22-60 | -59.8046 | 22.0553 | 461.4278 | 170.696 | 196.8411 | 237.4504 | 273.6489 | 315.3661 | 3.763%
7286 | 22-60 | -60.076 | 22.0553 | 459.6659 | 171.2861 | 197.4907 | 238.2833 | 274.6517 | 316.5715 | 3.823%
7287 | 22-60.5 | -60.3473 | 22.0553 | 458.5839 | 171.8093 | 198.0902 | 239.0583 | 275.5902 | 317.7053 | 3.877%
7288 | 22-60.5 | -60.6186 | 22.0553 | 458.1867 | 172.3205 | 198.7043 | 239.8722 | 276.592 | 318.9336 | 3.928%
7289 | 22-61 | -60.8899 | 22.0553 | 458.4761 | 172.7958 | 199.2984 | 240.6723 | 277.587 | 320.1646 | 3.976%
7290 | 22-61 | -61.1613 | 22.0553 | 459.4506 | 173.2237 | 199.8445 | 241.4157 | 278.5177 | 321.3227 | 4.019%
7291 | 22-61.5 | -61.4326 | 22.0553 | 461.1061 | 173.6539 | 200.4037 | 242.1919 | 279.5013 | 322.5589 | 4.061%
7292 | 22-61.5 | -61.7039 | 22.0553 | 463.4352 | 174.0535 | 200.9267 | 242.9229 | 280.4312 | 323.732 | 4.101%
7293 | 22-62 | -61.9752 | 22.0553 | 466.4278 | 174.4073 | 201.3902 | 243.5713 | 281.2567 | 324.7739 | 4.135%
7294 | 22-62 | -62.2465 | 22.0553 | 470.0712 | 174.7687 | 201.8736 | 244.2617 | 282.1464 | 325.908 | 4.17%
7295 | 22-62.5 | -62.5179 | 22.0553 | 474.3504 | 175.0993 | 202.3204 | 244.9062 | 282.9816 | 326.9777 | 4.201%
7296 | 22-63 | -62.7892 | 22.0553 | 479.2484 | 175.3869 | 202.7092 | 245.4672 | 283.7088 | 327.9091 | 4.228%
7297 | 22-63 | -63.0605 | 22.0553 | 484.7464 | 175.6734 | 203.0977 | 246.0294 | 284.4386 | 328.8451 | 4.255%
7298 | 22-63.5 | -63.3318 | 22.0553 | 490.8243 | 175.9305 | 203.4426 | 246.5233 | 285.0761 | 329.6588 | 4.279%
7299 | 22-63.5 | -63.6031 | 22.0553 | 497.4607 | 176.1633 | 203.7489 | 246.954 | 285.6261 | 330.3547 | 4.302%
7300 | 22-64 | -63.8745 | 22.0553 | 504.6336 | 176.4123 | 204.0743 | 247.408 | 286.2033 | 331.0825 | 4.327%
7301 | 22-64 | -64.1458 | 22.0553 | 512.3205 | 176.6428 | 204.3696 | 247.8119 | 286.7106 | 331.7157 | 4.351%
7302 | 22-64.5 | -64.4171 | 22.0553 | 520.4986 | 176.8607 | 204.6451 | 248.1833 | 287.173 | 332.2884 | 4.374%
7303 | 22-64.5 | -64.6884 | 22.0553 | 529.145 | 177.0997 | 204.9493 | 248.5967 | 287.6903 | 332.9322 | 4.399%
7304 | 22-65 | -64.9598 | 22.0553 | 538.2372 | 177.3097 | 205.209 | 248.9386 | 288.1096 | 333.4448 | 4.422%
7305 | 22-65 | -65.2311 | 22.0553 | 547.7531 | 177.5047 | 205.4452 | 249.2421 | 288.4759 | 333.8863 | 4.443%
7306 | 22-65.5 | -65.5024 | 22.0553 | 557.6707 | 177.7225 | 205.7133 | 249.5931 | 288.905 | 334.4094 | 4.467%
7307 | 22-66 | -65.7737 | 22.0553 | 567.9692 | 177.9034 | 205.9293 | 249.8662 | 289.2308 | 334.7981 | 4.488%
7308 | 22-66 | -66.045 | 22.0553 | 578.6281 | 178.0659 | 206.1235 | 250.112 | 289.5244 | 335.1487 | 4.507%
7309 | 22-66.5 | -66.3164 | 22.0553 | 589.6279 | 178.2432 | 206.3467 | 250.4119 | 289.8973 | 335.6104 | 4.526%
7310 | 22-66.5 | -66.5877 | 22.0553 | 600.9498 | 178.3992 | 206.5485 | 250.691 | 290.2507 | 336.0549 | 4.542%
7311 | 22-67 | -66.859 | 22.0553 | 612.576 | 178.5529 | 206.759 | 250.9992 | 290.654 | 336.5758 | 4.556%
7312 | 22-67 | -67.1303 | 22.0553 | 624.4893 | 178.7227 | 207.0062 | 251.3807 | 291.1675 | 337.2538 | 4.571%
7313 | 22-67.5 | -67.4016 | 22.0553 | 636.6738 | 178.8428 | 207.1948 | 251.6893 | 291.5949 | 337.8303 | 4.579%
7314 | 22-67.5 | -67.673 | 22.0553 | 649.114 | 178.9368 | 207.359 | 251.978 | 292.0077 | 338.3996 | 4.583%
7315 | 22-68 | -67.9443 | 22.0553 | 661.7956 | 179.0249 | 207.5283 | 252.2921 | 292.4669 | 339.0422 | 4.586%
7316 | 22-68 | -68.2156 | 22.0553 | 674.7048 | 179.0459 | 207.6102 | 252.4843 | 292.7711 | 339.4893 | 4.581%
7317 | 22-68.5 | -68.4869 | 22.0553 | 687.8289 | 179.042 | 207.6665 | 252.6504 | 293.0493 | 339.9113 | 4.573%
7318 | 22-69 | -68.7583 | 22.0553 | 701.1557 | 179.0335 | 207.7276 | 252.8387 | 293.3678 | 340.3967 | 4.563%
7319 | 22-69 | -69.0296 | 22.0553 | 714.6739 | 178.9594 | 207.7015 | 252.9035 | 293.5275 | 340.68 | 4.547%
7320 | 22-69.5 | -69.3009 | 22.0553 | 728.3728 | 178.8738 | 207.6647 | 252.9589 | 293.6797 | 340.9585 | 4.53%
7321 | 22-69.5 | -69.5722 | 22.0553 | 742.2423 | 178.7957 | 207.6445 | 253.0479 | 293.8826 | 341.3094 | 4.512%
7322 | 22-70 | -69.8435 | 22.0553 | 756.2731 | 178.6552 | 207.5401 | 253.0148 | 293.9268 | 341.4564 | 4.489%
7323 | 22-70 | -70.1149 | 22.0553 | 770.4563 | 178.4872 | 207.4015 | 252.9368 | 293.9157 | 341.5358 | 4.463%
7324 | 22-70.5 | -70.3862 | 22.0553 | 784.7835 | 178.2978 | 207.2384 | 252.8298 | 293.872 | 341.5786 | 4.435%
7325 | 22-70.5 | -70.6575 | 22.0553 | 799.2471 | 178.0291 | 206.9575 | 252.5375 | 293.5764 | 341.2863 | 4.401%
7326 | 22-71 | -70.9288 | 22.0553 | 813.8397 | 177.7464 | 206.6544 | 252.2087 | 293.2302 | 340.9253 | 4.366%
7327 | 22-71 | -71.2001 | 22.0553 | 828.5544 | 177.4571 | 206.3398 | 251.8594 | 292.8544 | 340.5237 | 4.331%
7328 | 22-71.5 | -71.4715 | 22.0553 | 843.3849 | 177.1153 | 205.9404 | 251.3685 | 292.2807 | 339.8528 | 4.293%
7329 | 22-71.5 | -71.7428 | 22.0553 | 858.3251 | 176.782 | 205.5505 | 250.8889 | 291.7196 | 339.1964 | 4.256%
7330 | 22-72 | -72.0141 | 22.0553 | 873.3693 | 176.4555 | 205.1673 | 250.4156 | 291.1642 | 338.5447 | 4.22%
7331 | 22-72.5 | -72.2854 | 22.0553 | 888.5123 | 176.0732 | 204.7112 | 249.8112 | 290.4197 | 337.6307 | 4.182%
7332 | 22-72.5 | -72.5568 | 22.0553 | 903.7489 | 175.6862 | 204.2737 | 249.2251 | 289.6925 | 336.7319 | 4.144%
7333 | 22-73 | -72.8281 | 22.0553 | 919.0746 | 175.3147 | 203.8609 | 248.6638 | 288.9893 | 335.8558 | 4.108%
7334 | 22-73 | -73.0994 | 22.0553 | 934.4849 | 175.0135 | 203.4702 | 248.1103 | 288.2784 | 334.951 | 4.08%
7335 | 22-73.5 | -73.3707 | 22.0553 | 949.9757 | 174.8178 | 203.2067 | 247.7308 | 287.7863 | 334.3197 | 4.063%
7336 | 22-73.5 | -73.642 | 22.0553 | 965.543 | 174.6545 | 202.9819 | 247.3999 | 287.3521 | 333.7572 | 4.049%
7337 | 22-74 | -73.9134 | 22.0553 | 981.1832 | 174.2885 | 202.5425 | 246.7534 | 286.5036 | 332.6584 | 4.017%
7338 | 22-74 | -74.1847 | 22.0553 | 996.8927 | 173.704 | 201.9904 | 245.9637 | 285.4842 | 331.356 | 3.965%
7339 | 22-74.5 | -74.456 | 22.0553 | 1012.6684 | 172.9829 | 201.3626 | 245.0767 | 284.3476 | 329.9133 | 3.902%
7340 | 22-74.5 | -74.7273 | 22.0553 | 1028.5072 | 172.2742 | 200.7408 | 244.1909 | 283.2073 | 328.4601 | 3.84%
7341 | 22-75 | -74.9986 | 22.0553 | 1044.4061 | 171.629 | 200.1988 | 243.4296 | 282.2353 | 327.23 | 3.784%
7342 | 22-75.5 | -75.27 | 22.0553 | 1060.3624 | 171.0973 | 199.7337 | 242.7761 | 281.4006 | 326.1731 | 3.739%
7343 | 22-75.5 | -75.5413 | 22.0553 | 1076.3736 | 170.7766 | 199.3622 | 242.2393 | 280.7036 | 325.2784 | 3.711%
7344 | 22-76 | -75.8126 | 22.0553 | 1092.4371 | 170.6036 | 199.1737 | 241.9736 | 280.3638 | 324.848 | 3.696%
7345 | 22-76 | -76.0839 | 22.0553 | 1108.5507 | 170.4288 | 199.0016 | 241.7341 | 280.0601 | 324.4663 | 3.681%
7346 | 22-76.5 | -76.3553 | 22.0553 | 1124.7121 | 170.072 | 198.606 | 241.17 | 279.3338 | 323.5408 | 3.651%
7347 | 22-76.5 | -76.6266 | 22.0553 | 1140.9193 | 169.4595 | 197.998 | 240.3111 | 278.2338 | 322.1455 | 3.599%
7348 | 22-77 | -76.8979 | 22.0553 | 1157.1704 | 168.7713 | 197.2959 | 239.3079 | 276.9405 | 320.4958 | 3.541%
7349 | 22-77 | -77.1692 | 22.0553 | 1173.4634 | 168.2562 | 196.7251 | 238.4641 | 275.8315 | 319.0591 | 3.5%
7350 | 22-77.5 | -77.4405 | 22.0553 | 1189.7966 | 168.1302 | 196.5482 | 238.1593 | 275.3999 | 318.4685 | 3.492%
7351 | 22-77.5 | -77.7119 | 22.0553 | 1206.1684 | 168.3889 | 196.6408 | 238.205 | 275.3945 | 318.3947 | 3.517%
7352 | 22-78 | -77.9832 | 22.0553 | 1222.5771 | 168.8592 | 196.8538 | 238.3885 | 275.5412 | 318.4883 | 3.561%
7353 | 22-78.5 | -78.2545 | 22.0553 | 1239.0213 | 169.3584 | 197.1156 | 238.6295 | 275.7529 | 318.6559 | 3.609%
7354 | 22-78.5 | -78.5258 | 22.0553 | 1255.4994 | 169.8418 | 197.3804 | 238.8561 | 275.9326 | 318.7685 | 3.657%
7355 | 22-79 | -78.7971 | 22.0553 | 1272.0102 | 170.259 | 197.6176 | 239.0303 | 276.0355 | 318.7736 | 3.702%
7356 | 22-79 | -79.0685 | 22.0553 | 1288.5524 | 170.5284 | 197.8289 | 239.1728 | 276.1012 | 318.7356 | 3.736%
7357 | 22-79.5 | -79.3398 | 22.0553 | 1305.1247 | 170.7317 | 197.9413 | 239.1636 | 275.9634 | 318.4292 | 3.764%
7358 | 22-79.5 | -79.6111 | 22.0553 | 1321.726 | 171.0028 | 198.0823 | 239.1819 | 275.851 | 318.1448 | 3.799%
7359 | 22-80 | -79.8824 | 22.0553 | 1338.3551 | 171.5141 | 198.4973 | 239.5863 | 276.2329 | 318.4874 | 3.858%
7360 | 22-80 | -80.1537 | 22.0553 | 1355.0109 | 172.3135 | 199.2048 | 240.3904 | 277.1164 | 319.4559 | 3.945%
7361 | 22-80.5 | -80.4251 | 22.0553 | 1371.6925 | 173.2631 | 200.1009 | 241.4553 | 278.3296 | 320.8377 | 4.048%
7362 | 22-80.5 | -80.6964 | 22.0553 | 1388.3989 | 174.1939 | 201.0565 | 242.6113 | 279.6647 | 322.3795 | 4.152%
7363 | 22-81 | -80.9677 | 22.0553 | 1405.1292 | 174.9397 | 201.8181 | 243.5004 | 280.6632 | 323.5002 | 4.24%
7364 | 22-81 | -81.239 | 22.0553 | 1421.8824 | 175.5095 | 202.4112 | 244.1681 | 281.391 | 324.2907 | 4.311%
7365 | 22-81.5 | -81.5104 | 22.0553 | 1438.6578 | 175.9999 | 202.9535 | 244.786 | 282.0716 | 325.0387 | 4.373%
7366 | 22-82 | -81.7817 | 22.0553 | 1455.4545 | 176.4488 | 203.4315 | 245.3194 | 282.6488 | 325.6607 | 4.43%
7367 | 22-82 | -82.053 | 22.0553 | 1472.2717 | 176.8964 | 203.8879 | 245.8294 | 283.201 | 326.2563 | 4.488%
7368 | 22-82.5 | -82.3243 | 22.0553 | 1489.1088 | 177.3462 | 204.3577 | 246.3679 | 283.7971 | 326.915 | 4.546%
7369 | 22-82.5 | -82.5956 | 22.0553 | 1505.965 | 177.821 | 204.8696 | 246.9673 | 284.4722 | 327.6748 | 4.607%
7370 | 22-83 | -82.867 | 22.0553 | 1522.8396 | 178.3728 | 205.498 | 247.746 | 285.3873 | 328.7498 | 4.675%
7371 | 22-83 | -83.1383 | 22.0553 | 1539.732 | 179.0281 | 206.2844 | 248.7721 | 286.6371 | 330.2676 | 4.753%
7372 | 22-83.5 | -83.4096 | 22.0553 | 1556.6416 | 179.6042 | 206.997 | 249.7247 | 287.8161 | 331.7197 | 4.819%
7373 | 22-83.5 | -83.6809 | 22.0553 | 1573.5678 | 180.0519 | 207.5804 | 250.5365 | 288.8459 | 333.0153 | 4.868%
7374 | 22-84 | -83.9522 | 22.0553 | 1590.51 | 180.3654 | 208.0195 | 251.1906 | 289.7087 | 334.1359 | 4.898%
7375 | 22-84 | -84.2236 | 22.0553 | 1607.4676 | 180.4496 | 208.182 | 251.4919 | 290.1484 | 334.7497 | 4.899%
7376 | 22-84.5 | -84.4949 | 22.0553 | 1624.4402 | 180.4882 | 208.3091 | 251.7778 | 290.5944 | 335.3987 | 4.892%
7377 | 22-85 | -84.7662 | 22.0553 | 1641.4272 | 180.5519 | 208.4948 | 252.1822 | 291.2188 | 336.302 | 4.884%
7378 | 22-85 | -85.0375 | 22.0553 | 1658.4281 | 180.4725 | 208.5118 | 252.377 | 291.596 | 336.9138 | 4.858%
7379 | 22-85.5 | -85.3089 | 22.0553 | 1675.4425 | 180.2471 | 208.3658 | 252.383 | 291.7629 | 337.2912 | 4.813%
7380 | 22-85.5 | -85.5802 | 22.0553 | 1692.4699 | 179.8276 | 208.0589 | 252.2103 | 291.737 | 337.4622 | 4.744%
7381 | 22-86 | -85.8515 | 22.0553 | 1709.5099 | 179.2006 | 207.5617 | 251.8013 | 291.4331 | 337.306 | 4.652%
7382 | 22-86 | -86.1228 | 22.0553 | 1726.5621 | 178.3339 | 206.8394 | 251.1169 | 290.8088 | 336.7776 | 4.535%
7383 | 22-86.5 | -86.3941 | 22.0553 | 1743.6261 | 177.2214 | 205.8747 | 250.1339 | 289.8355 | 335.8417 | 4.393%
7384 | 22-86.5 | -86.6655 | 22.0553 | 1760.7015 | 175.8253 | 204.5986 | 248.7337 | 288.3452 | 334.2683 | 4.229%
7385 | 22-87 | -86.9368 | 22.0553 | 1777.7879 | 174.3171 | 203.236 | 247.2293 | 286.7351 | 332.5576 | 4.059%
7386 | 22-87 | -87.2081 | 22.0553 | 1794.8849 | 172.7127 | 201.7997 | 245.6352 | 285.0213 | 330.7275 | 3.886%
7387 | 22-87.5 | -87.4794 | 22.0553 | 1811.9923 | 170.9492 | 200.1937 | 243.7882 | 282.9737 | 328.4629 | 3.709%
7388 | 22-88 | -87.7507 | 22.0553 | 1829.1097 | 169.1071 | 198.5398 | 241.8722 | 280.8362 | 326.0828 | 3.533%
7389 | 22-88 | -88.0221 | 22.0553 | 1846.2367 | 167.2011 | 196.8479 | 239.8987 | 278.6224 | 323.6028 | 3.361%
7390 | 22-88.5 | -88.2934 | 22.0553 | 1863.3731 | 165.2779 | 195.1352 | 237.8709 | 276.3198 | 320.9897 | 3.196%
7391 | 22-88.5 | -88.5647 | 22.0553 | 1880.5185 | 163.5015 | 193.6185 | 236.1069 | 274.3453 | 318.7828 | 3.051%
7392 | 22-89 | -88.836 | 22.0553 | 1897.6727 | 161.8479 | 192.2676 | 234.5581 | 272.632 | 316.8922 | 2.923%
7393 | 22-89 | -89.1074 | 22.0553 | 1914.8354 | 160.2585 | 190.9793 | 233.0528 | 270.9404 | 314.993 | 2.805%
7394 | 22-89.5 | -89.3787 | 22.0553 | 1932.0063 | 158.7537 | 189.7771 | 231.6448 | 269.3551 | 313.2095 | 2.699%
7395 | 22-89.5 | -89.65 | 22.0553 | 1949.1852 | 157.3258 | 188.6394 | 230.2982 | 267.826 | 311.4738 | 2.602%
7396 | 22-90 | -89.9213 | 22.0553 | 1966.3717 | 155.928 | 187.5208 | 228.9321 | 266.2364 | 309.6237 | 2.512%
7397 | 22-90 | -90.1926 | 22.0553 | 1983.5658 | 154.6089 | 186.4812 | 227.6528 | 264.7393 | 307.8713 | 2.429%
7398 | 22-90.5 | -90.464 | 22.0553 | 2000.767 | 153.3592 | 185.5002 | 226.4337 | 263.3022 | 306.1771 | 2.354%
7399 | 22-90.5 | -90.7353 | 22.0553 | 2017.9752 | 152.145 | 184.552 | 225.2449 | 261.8916 | 304.5032 | 2.283%
7400 | 22-50 | -50.0371 | 22.3266 | 840.8616 | 125.32 | 164.0635 | 198.8416 | 227.1794 | 259.5566 | 1.145%
7401 | 22-50.5 | -50.3084 | 22.3266 | 826.332 | 126.9952 | 165.7777 | 200.2399 | 228.8355 | 261.516 | 1.201%
7402 | 22-50.5 | -50.5797 | 22.3266 | 811.9286 | 128.6066 | 167.3441 | 201.5748 | 230.422 | 263.399 | 1.256%
7403 | 22-51 | -50.851 | 22.3266 | 797.6583 | 130.1758 | 168.7892 | 202.8762 | 231.9817 | 265.2644 | 1.312%
7404 | 22-51 | -51.1224 | 22.3266 | 783.5285 | 131.7369 | 170.1444 | 204.184 | 233.5686 | 267.1839 | 1.369%
7405 | 22-51.5 | -51.3937 | 22.3266 | 769.5469 | 133.2224 | 171.3554 | 205.4202 | 235.073 | 269.0085 | 1.425%
7406 | 22-51.5 | -51.665 | 22.3266 | 755.7217 | 134.6829 | 172.4824 | 206.6444 | 236.5755 | 270.8443 | 1.482%
7407 | 22-52 | -51.9363 | 22.3266 | 742.0617 | 136.1634 | 173.5684 | 207.9064 | 238.1411 | 272.7754 | 1.542%
7408 | 22-52 | -52.2077 | 22.3266 | 728.5763 | 137.5969 | 174.5622 | 209.1183 | 239.6427 | 274.6258 | 1.601%
7409 | 22-52.5 | -52.479 | 22.3266 | 715.2753 | 139.0396 | 175.5262 | 210.3479 | 241.1743 | 276.5214 | 1.663%
7410 | 22-53 | -52.7503 | 22.3266 | 702.1693 | 140.5276 | 176.4973 | 211.6388 | 242.7949 | 278.541 | 1.728%
7411 | 22-53 | -53.0216 | 22.3266 | 689.2694 | 141.9743 | 177.4134 | 212.876 | 244.3423 | 280.4633 | 1.794%
7412 | 22-53.5 | -53.2929 | 22.3266 | 676.5875 | 143.453 | 178.3405 | 214.1405 | 245.9267 | 282.4345 | 1.863%
7413 | 22-53.5 | -53.5643 | 22.3266 | 664.136 | 144.9969 | 179.3075 | 215.4687 | 247.5972 | 284.5197 | 1.937%
7414 | 22-54 | -53.8356 | 22.3266 | 651.9283 | 146.5085 | 180.248 | 216.7533 | 249.2074 | 286.5239 | 2.013%
7415 | 22-54 | -54.1069 | 22.3266 | 639.9782 | 148.05 | 181.2055 | 218.0585 | 250.8415 | 288.556 | 2.093%
7416 | 22-54.5 | -54.3782 | 22.3266 | 628.3005 | 149.6354 | 182.1898 | 219.3968 | 252.5147 | 290.6346 | 2.178%
7417 | 22-54.5 | -54.6495 | 22.3266 | 616.9107 | 151.1255 | 183.1073 | 220.6266 | 254.0389 | 292.5139 | 2.26%
7418 | 22-55 | -54.9209 | 22.3266 | 605.8251 | 152.5916 | 184.0073 | 221.8274 | 255.5228 | 294.3389 | 2.345%
7419 | 22-55 | -55.1922 | 22.3266 | 595.0607 | 154.0412 | 184.8953 | 223.0064 | 256.9753 | 296.1208 | 2.431%
7420 | 22-55.5 | -55.4635 | 22.3266 | 584.6353 | 155.382 | 185.7005 | 224.0437 | 258.2282 | 297.6307 | 2.514%
7421 | 22-55.5 | -55.7348 | 22.3266 | 574.5673 | 156.6782 | 186.4751 | 225.0285 | 259.4069 | 299.0395 | 2.597%
7422 | 22-56 | -56.0061 | 22.3266 | 564.8759 | 157.9223 | 187.2221 | 225.9648 | 260.5165 | 300.3534 | 2.68%
7423 | 22-56.5 | -56.2775 | 22.3266 | 555.5808 | 159.0707 | 187.9046 | 226.7915 | 261.4721 | 301.458 | 2.759%
7424 | 22-56.5 | -56.5488 | 22.3266 | 546.7022 | 160.2059 | 188.5938 | 227.6253 | 262.4352 | 302.5704 | 2.84%
7425 | 22-57 | -56.8201 | 22.3266 | 538.2609 | 161.3067 | 189.2828 | 228.4546 | 263.3894 | 303.6681 | 2.922%
7426 | 22-57 | -57.0914 | 22.3266 | 530.2776 | 162.3025 | 189.9111 | 229.1861 | 264.2092 | 304.5861 | 2.998%
7427 | 22-57.5 | -57.3628 | 22.3266 | 522.7734 | 163.2804 | 190.55 | 229.9296 | 265.0421 | 305.5182 | 3.076%
7428 | 22-57.5 | -57.6341 | 22.3266 | 515.7692 | 164.2118 | 191.1899 | 230.6705 | 265.8688 | 306.4397 | 3.154%
7429 | 22-58 | -57.9054 | 22.3266 | 509.2857 | 165.0387 | 191.7845 | 231.3424 | 266.6033 | 307.24 | 3.225%
7430 | 22-58 | -58.1767 | 22.3266 | 503.343 | 165.8845 | 192.4319 | 232.0928 | 267.4412 | 308.1744 | 3.3%
7431 | 22-58.5 | -58.448 | 22.3266 | 497.9605 | 166.717 | 193.1096 | 232.8874 | 268.3369 | 309.1831 | 3.376%
7432 | 22-58.5 | -58.7194 | 22.3266 | 493.1565 | 167.4804 | 193.7534 | 233.628 | 269.1587 | 310.0935 | 3.449%
7433 | 22-59 | -58.9907 | 22.3266 | 488.9481 | 168.2546 | 194.4398 | 234.4417 | 270.0839 | 311.1452 | 3.523%
7434 | 22-59.5 | -59.262 | 22.3266 | 485.3508 | 169.0144 | 195.1463 | 235.2954 | 271.0689 | 312.2817 | 3.598%
7435 | 22-59.5 | -59.5333 | 22.3266 | 482.3783 | 169.7246 | 195.8272 | 236.1227 | 272.0275 | 313.3922 | 3.669%
7436 | 22-60 | -59.8046 | 22.3266 | 480.0422 | 170.4175 | 196.5272 | 236.9936 | 273.0542 | 314.6021 | 3.739%
7437 | 22-60 | -60.076 | 22.3266 | 478.3518 | 171.0657 | 197.2175 | 237.8663 | 274.0948 | 315.8417 | 3.805%
7438 | 22-60.5 | -60.3473 | 22.3266 | 477.3141 | 171.6441 | 197.8605 | 238.6857 | 275.0774 | 317.0182 | 3.864%
7439 | 22-60.5 | -60.6186 | 22.3266 | 476.9331 | 172.2102 | 198.5221 | 239.5511 | 276.1334 | 318.3029 | 3.922%
7440 | 22-61 | -60.8899 | 22.3266 | 477.2106 | 172.7375 | 199.1667 | 240.4087 | 277.1916 | 319.6031 | 3.976%
7441 | 22-61 | -61.1613 | 22.3266 | 478.1454 | 173.2111 | 199.7642 | 241.2136 | 278.1928 | 320.8418 | 4.024%
7442 | 22-61.5 | -61.4326 | 22.3266 | 479.7336 | 173.6826 | 200.3724 | 242.051 | 279.2487 | 322.1635 | 4.071%
7443 | 22-61.5 | -61.7039 | 22.3266 | 481.9688 | 174.1196 | 200.9409 | 242.8407 | 280.2495 | 323.422 | 4.114%
7444 | 22-62 | -61.9752 | 22.3266 | 484.842 | 174.5065 | 201.4456 | 243.5435 | 281.1418 | 324.5455 | 4.153%
7445 | 22-62 | -62.2465 | 22.3266 | 488.3419 | 174.897 | 201.9662 | 244.2847 | 282.0951 | 325.7588 | 4.19%
7446 | 22-62.5 | -62.5179 | 22.3266 | 492.4553 | 175.2523 | 202.4452 | 244.974 | 282.9872 | 326.8999 | 4.224%
7447 | 22-63 | -62.7892 | 22.3266 | 497.1667 | 175.5605 | 202.8611 | 245.5731 | 283.7628 | 327.8925 | 4.253%
7448 | 22-63 | -63.0605 | 22.3266 | 502.4595 | 175.8648 | 203.2734 | 246.1693 | 284.5365 | 328.8843 | 4.282%
7449 | 22-63.5 | -63.3318 | 22.3266 | 508.3154 | 176.1363 | 203.6383 | 246.6925 | 285.2123 | 329.7475 | 4.308%
7450 | 22-63.5 | -63.6031 | 22.3266 | 514.7153 | 176.3809 | 203.9618 | 247.1495 | 285.7976 | 330.4897 | 4.332%
7451 | 22-64 | -63.8745 | 22.3266 | 521.639 | 176.6409 | 204.3041 | 247.6311 | 286.4128 | 331.2684 | 4.358%
7452 | 22-64 | -64.1458 | 22.3266 | 529.066 | 176.8799 | 204.6135 | 248.0587 | 286.9532 | 331.9466 | 4.382%
7453 | 22-64.5 | -64.4171 | 22.3266 | 536.9753 | 177.105 | 204.9001 | 248.4482 | 287.4407 | 332.5531 | 4.406%
7454 | 22-64.5 | -64.6884 | 22.3266 | 545.3461 | 177.3515 | 205.2144 | 248.876 | 287.9764 | 333.2202 | 4.432%
7455 | 22-65 | -64.9598 | 22.3266 | 554.1573 | 177.5685 | 205.4815 | 249.2257 | 288.4037 | 333.7409 | 4.456%
7456 | 22-65 | -65.2311 | 22.3266 | 563.3883 | 177.7699 | 205.7228 | 249.5316 | 288.7695 | 334.1778 | 4.479%
7457 | 22-65.5 | -65.5024 | 22.3266 | 573.0188 | 177.9946 | 205.9952 | 249.8823 | 289.1931 | 334.6888 | 4.504%
7458 | 22-66 | -65.7737 | 22.3266 | 583.0288 | 178.1806 | 206.2119 | 250.1472 | 289.5018 | 335.0486 | 4.526%
7459 | 22-66 | -66.045 | 22.3266 | 593.3994 | 178.3465 | 206.403 | 250.3779 | 289.7679 | 335.3559 | 4.546%
7460 | 22-66.5 | -66.3164 | 22.3266 | 604.1117 | 178.5262 | 206.6208 | 250.6582 | 290.1066 | 335.7646 | 4.567%
7461 | 22-66.5 | -66.5877 | 22.3266 | 615.1479 | 178.6842 | 206.816 | 250.915 | 290.4216 | 336.1499 | 4.584%
7462 | 22-67 | -66.859 | 22.3266 | 626.491 | 178.8406 | 207.0201 | 251.2002 | 290.7848 | 336.609 | 4.6%
7463 | 22-67 | -67.1303 | 22.3266 | 638.1245 | 179.014 | 207.2616 | 251.5588 | 291.2577 | 337.2235 | 4.616%
7464 | 22-67.5 | -67.4016 | 22.3266 | 650.0328 | 179.1376 | 207.4439 | 251.8434 | 291.6429 | 337.7344 | 4.626%
7465 | 22-67.5 | -67.673 | 22.3266 | 662.201 | 179.2363 | 207.6048 | 252.1137 | 292.022 | 338.2502 | 4.632%
7466 | 22-68 | -67.9443 | 22.3266 | 674.615 | 179.3311 | 207.7754 | 252.4189 | 292.4617 | 338.8596 | 4.636%
7467 | 22-68 | -68.2156 | 22.3266 | 687.2616 | 179.3614 | 207.8636 | 252.6114 | 292.7598 | 339.2921 | 4.633%
7468 | 22-68.5 | -68.4869 | 22.3266 | 700.128 | 179.3711 | 207.9333 | 252.7903 | 293.0497 | 339.7241 | 4.627%
7469 | 22-69 | -68.7583 | 22.3266 | 713.2024 | 179.381 | 208.0158 | 253.0051 | 293.3991 | 340.2456 | 4.619%
7470 | 22-69 | -69.0296 | 22.3266 | 726.4734 | 179.3293 | 208.0181 | 253.1076 | 293.6056 | 340.5867 | 4.605%
7471 | 22-69.5 | -69.3009 | 22.3266 | 739.9305 | 179.2728 | 208.0194 | 253.217 | 293.8271 | 340.9532 | 4.59%
7472 | 22-69.5 | -69.5722 | 22.3266 | 753.5637 | 179.2309 | 208.0487 | 253.378 | 294.1238 | 341.425 | 4.576%
7473 | 22-70 | -69.8435 | 22.3266 | 767.3635 | 179.1318 | 208.0022 | 253.4313 | 294.2821 | 341.7205 | 4.556%
7474 | 22-70 | -70.1149 | 22.3266 | 781.3211 | 179.0098 | 207.9288 | 253.4515 | 294.4016 | 341.9706 | 4.533%
7475 | 22-70.5 | -70.3862 | 22.3266 | 795.4282 | 178.8705 | 207.837 | 253.4523 | 294.5014 | 342.2011 | 4.509%
7476 | 22-70.5 | -70.6575 | 22.3266 | 809.6769 | 178.6521 | 207.6275 | 253.268 | 294.3496 | 342.0971 | 4.478%
7477 | 22-71 | -70.9288 | 22.3266 | 824.0598 | 178.4211 | 207.397 | 253.0478 | 294.1469 | 341.9232 | 4.447%
7478 | 22-71 | -71.2001 | 22.3266 | 838.57 | 178.1847 | 207.1552 | 252.8056 | 293.9117 | 341.7034 | 4.416%
7479 | 22-71.5 | -71.4715 | 22.3266 | 853.201 | 177.8943 | 206.8244 | 252.413 | 293.4648 | 341.1946 | 4.383%
7480 | 22-71.5 | -71.7428 | 22.3266 | 867.9465 | 177.61 | 206.4984 | 252.022 | 293.0162 | 340.68 | 4.35%
7481 | 22-72 | -72.0141 | 22.3266 | 882.8009 | 177.3343 | 206.1795 | 251.6353 | 292.5688 | 340.1621 | 4.319%
7482 | 22-72.5 | -72.2854 | 22.3266 | 897.7588 | 177.044 | 205.8199 | 251.1609 | 291.9858 | 339.4479 | 4.289%
7483 | 22-72.5 | -72.5568 | 22.3266 | 912.8149 | 176.7918 | 205.5126 | 250.7499 | 291.4764 | 338.819 | 4.263%
7484 | 22-73 | -72.8281 | 22.3266 | 927.9644 | 176.5706 | 205.2411 | 250.3781 | 291.0085 | 338.2335 | 4.242%
7485 | 22-73 | -73.0994 | 22.3266 | 943.2029 | 176.3301 | 204.916 | 249.9078 | 290.3971 | 337.4475 | 4.22%
7486 | 22-73.5 | -73.3707 | 22.3266 | 958.5261 | 176.1333 | 204.6441 | 249.5067 | 289.8699 | 336.7639 | 4.202%
7487 | 22-73.5 | -73.642 | 22.3266 | 973.9298 | 175.9398 | 204.372 | 249.0985 | 289.3284 | 336.0567 | 4.186%
7488 | 22-74 | -73.9134 | 22.3266 | 989.4104 | 175.5988 | 203.9475 | 248.4612 | 288.483 | 334.9525 | 4.157%
7489 | 22-74 | -74.1847 | 22.3266 | 1004.9642 | 175.1351 | 203.4759 | 247.7725 | 287.5833 | 333.7919 | 4.116%
7490 | 22-74.5 | -74.456 | 22.3266 | 1020.5879 | 174.5914 | 202.969 | 247.0432 | 286.6387 | 332.5822 | 4.067%
7491 | 22-74.5 | -74.7273 | 22.3266 | 1036.2782 | 174.0476 | 202.4573 | 246.3023 | 285.6758 | 331.3455 | 4.019%
7492 | 22-75 | -74.9986 | 22.3266 | 1052.0321 | 173.556 | 202.0186 | 245.6797 | 284.8761 | 330.3282 | 3.975%
7493 | 22-75.5 | -75.27 | 22.3266 | 1067.8468 | 173.1352 | 201.6214 | 245.1191 | 284.1581 | 329.4169 | 3.938%
7494 | 22-75.5 | -75.5413 | 22.3266 | 1083.7196 | 172.8207 | 201.2259 | 244.5496 | 283.42 | 328.471 | 3.91%
7495 | 22-76 | -75.8126 | 22.3266 | 1099.6479 | 172.5176 | 200.8891 | 244.0793 | 282.8221 | 327.7173 | 3.882%
7496 | 22-76 | -76.0839 | 22.3266 | 1115.6294 | 172.1404 | 200.4969 | 243.5367 | 282.136 | 326.8566 | 3.848%
7497 | 22-76.5 | -76.3553 | 22.3266 | 1131.6616 | 171.5946 | 199.9071 | 242.7064 | 281.0749 | 325.5128 | 3.799%
7498 | 22-76.5 | -76.6266 | 22.3266 | 1147.7425 | 170.9104 | 199.2173 | 241.7389 | 279.8411 | 323.9532 | 3.739%
7499 | 22-77 | -76.8979 | 22.3266 | 1163.87 | 170.2241 | 198.5233 | 240.7554 | 278.5792 | 322.35 | 3.679%
7500 | 22-77 | -77.1692 | 22.3266 | 1180.0421 | 169.7307 | 197.9894 | 239.9753 | 277.5607 | 321.0374 | 3.638%
7501 | 22-77.5 | -77.4405 | 22.3266 | 1196.2571 | 169.5617 | 197.7771 | 239.6366 | 277.0977 | 320.4197 | 3.626%
7502 | 22-77.5 | -77.7119 | 22.3266 | 1212.5131 | 169.6756 | 197.7626 | 239.5509 | 276.939 | 320.167 | 3.638%
7503 | 22-78 | -77.9832 | 22.3266 | 1228.8084 | 169.9383 | 197.8208 | 239.5374 | 276.8496 | 319.9784 | 3.665%
7504 | 22-78.5 | -78.2545 | 22.3266 | 1245.1416 | 170.236 | 197.9317 | 239.5863 | 276.8315 | 319.8708 | 3.696%
7505 | 22-78.5 | -78.5258 | 22.3266 | 1261.511 | 170.5236 | 198.0468 | 239.6215 | 276.7811 | 319.7075 | 3.728%
7506 | 22-79 | -78.7971 | 22.3266 | 1277.9153 | 170.7802 | 198.1612 | 239.641 | 276.6998 | 319.4936 | 3.759%
7507 | 22-79 | -79.0685 | 22.3266 | 1294.3531 | 170.9815 | 198.3277 | 239.7372 | 276.719 | 319.4098 | 3.785%
7508 | 22-79.5 | -79.3398 | 22.3266 | 1310.823 | 171.2014 | 198.4728 | 239.7889 | 276.6702 | 319.2278 | 3.815%
7509 | 22-79.5 | -79.6111 | 22.3266 | 1327.3239 | 171.5082 | 198.6705 | 239.9006 | 276.6873 | 319.1178 | 3.853%
7510 | 22-80 | -79.8824 | 22.3266 | 1343.8546 | 172.0161 | 199.0906 | 240.3255 | 277.1053 | 319.5166 | 3.911%
7511 | 22-80 | -80.1537 | 22.3266 | 1360.4139 | 172.7745 | 199.7529 | 241.0785 | 277.933 | 320.4242 | 3.994%
7512 | 22-80.5 | -80.4251 | 22.3266 | 1377.0007 | 173.6639 | 200.5771 | 242.0526 | 279.0378 | 321.6769 | 4.093%
7513 | 22-80.5 | -80.6964 | 22.3266 | 1393.6141 | 174.5361 | 201.4604 | 243.1137 | 280.2569 | 323.0774 | 4.191%
7514 | 22-81 | -80.9677 | 22.3266 | 1410.2531 | 175.227 | 202.1526 | 243.9096 | 281.1397 | 324.055 | 4.274%
7515 | 22-81 | -81.239 | 22.3266 | 1426.9167 | 175.7466 | 202.6825 | 244.4923 | 281.762 | 324.7152 | 4.339%
7516 | 22-81.5 | -81.5104 | 22.3266 | 1443.6041 | 176.1918 | 203.1691 | 245.0373 | 282.3535 | 325.3549 | 4.396%
7517 | 22-82 | -81.7817 | 22.3266 | 1460.3143 | 176.5994 | 203.5962 | 245.504 | 282.8493 | 325.8777 | 4.45%
7518 | 22-82 | -82.053 | 22.3266 | 1477.0466 | 177.0111 | 204.0085 | 245.9561 | 283.3307 | 326.3871 | 4.504%
7519 | 22-82.5 | -82.3243 | 22.3266 | 1493.8001 | 177.4326 | 204.4435 | 246.4495 | 283.8721 | 326.9796 | 4.558%
7520 | 22-82.5 | -82.5956 | 22.3266 | 1510.5742 | 177.8845 | 204.9275 | 247.0131 | 284.5038 | 327.687 | 4.617%
7521 | 22-83 | -82.867 | 22.3266 | 1527.3681 | 178.4187 | 205.5351 | 247.7657 | 285.3881 | 328.7254 | 4.683%
7522 | 22-83 | -83.1383 | 22.3266 | 1544.1812 | 179.0622 | 206.3085 | 248.7771 | 286.6219 | 330.2258 | 4.759%
7523 | 22-83.5 | -83.4096 | 22.3266 | 1561.0127 | 179.631 | 207.0133 | 249.7214 | 287.7921 | 331.669 | 4.825%
7524 | 22-83.5 | -83.6809 | 22.3266 | 1577.862 | 180.0749 | 207.593 | 250.5295 | 288.8185 | 332.9614 | 4.873%
7525 | 22-84 | -83.9522 | 22.3266 | 1594.7285 | 180.3882 | 208.0323 | 251.1845 | 289.6829 | 334.0845 | 4.903%
7526 | 22-84 | -84.2236 | 22.3266 | 1611.6117 | 180.4799 | 208.206 | 251.5034 | 290.1464 | 334.7297 | 4.905%
7527 | 22-84.5 | -84.4949 | 22.3266 | 1628.511 | 180.5323 | 208.3529 | 251.8194 | 290.6323 | 335.4309 | 4.899%
7528 | 22-85 | -84.7662 | 22.3266 | 1645.4258 | 180.6156 | 208.5654 | 252.2631 | 291.3082 | 336.4005 | 4.893%
7529 | 22-85 | -85.0375 | 22.3266 | 1662.3557 | 180.5701 | 208.6248 | 252.514 | 291.7547 | 337.0975 | 4.871%
7530 | 22-85.5 | -85.3089 | 22.3266 | 1679.3001 | 180.3946 | 208.5397 | 252.5993 | 292.0179 | 337.5917 | 4.831%
7531 | 22-85.5 | -85.5802 | 22.3266 | 1696.2585 | 180.0415 | 208.3136 | 252.5309 | 292.1184 | 337.9156 | 4.77%
7532 | 22-86 | -85.8515 | 22.3266 | 1713.2305 | 179.5167 | 207.9205 | 252.2562 | 291.9769 | 337.9556 | 4.689%
7533 | 22-86 | -86.1228 | 22.3266 | 1730.2157 | 178.7956 | 207.3283 | 251.7397 | 291.5558 | 337.6725 | 4.587%
7534 | 22-86.5 | -86.3941 | 22.3266 | 1747.2136 | 177.8676 | 206.5185 | 250.9567 | 290.8245 | 337.0289 | 4.464%
7535 | 22-86.5 | -86.6655 | 22.3266 | 1764.2237 | 176.6688 | 205.4023 | 249.7636 | 289.5853 | 335.7594 | 4.316%
7536 | 22-87 | -86.9368 | 22.3266 | 1781.2459 | 175.371 | 204.208 | 248.4795 | 288.2446 | 334.3771 | 4.164%
7537 | 22-87 | -87.2081 | 22.3266 | 1798.2795 | 173.9888 | 202.948 | 247.1187 | 286.8178 | 332.8989 | 4.008%
7538 | 22-87.5 | -87.4794 | 22.3266 | 1815.3243 | 172.4561 | 201.5211 | 245.5091 | 285.0623 | 330.9926 | 3.847%
7539 | 22-88 | -87.7507 | 22.3266 | 1832.3799 | 170.8486 | 200.0434 | 243.824 | 283.2074 | 328.9571 | 3.685%
7540 | 22-88 | -88.0221 | 22.3266 | 1849.446 | 169.1768 | 198.5218 | 242.0716 | 281.262 | 326.8024 | 3.526%
7541 | 22-88.5 | -88.2934 | 22.3266 | 1866.5222 | 167.4731 | 196.961 | 240.2383 | 279.1935 | 324.4709 | 3.372%
7542 | 22-88.5 | -88.5647 | 22.3266 | 1883.6083 | 165.8919 | 195.5693 | 238.6344 | 277.4117 | 322.4956 | 3.235%
7543 | 22-89 | -88.836 | 22.3266 | 1900.7038 | 164.407 | 194.3144 | 237.2069 | 275.8434 | 320.778 | 3.111%
7544 | 22-89 | -89.1074 | 22.3266 | 1917.8086 | 162.9536 | 193.0853 | 235.7719 | 274.2316 | 318.9695 | 2.996%
7545 | 22-89.5 | -89.3787 | 22.3266 | 1934.9222 | 161.5322 | 191.9022 | 234.3776 | 272.654 | 317.1853 | 2.888%
7546 | 22-89.5 | -89.65 | 22.3266 | 1952.0446 | 160.1329 | 190.7472 | 232.9941 | 271.0681 | 315.3674 | 2.787%
7547 | 22-90 | -89.9213 | 22.3266 | 1969.1752 | 158.7245 | 189.5864 | 231.5574 | 269.3798 | 313.3836 | 2.69%
7548 | 22-90 | -90.1926 | 22.3266 | 1986.314 | 157.3816 | 188.4995 | 230.199 | 267.7719 | 311.4808 | 2.601%
7549 | 22-90.5 | -90.464 | 22.3266 | 2003.4607 | 156.0949 | 187.4654 | 228.8916 | 266.2116 | 309.6195 | 2.518%
7550 | 22-90.5 | -90.7353 | 22.3266 | 2020.6149 | 154.8295 | 186.4575 | 227.606 | 264.6674 | 307.766 | 2.44%
7551 | 23-50 | -50.0371 | 22.5979 | 851.1369 | 123.6245 | 162.3504 | 197.4231 | 225.5139 | 257.6027 | 1.093%
7552 | 23-50.5 | -50.3084 | 22.5979 | 836.8113 | 125.3118 | 164.1747 | 198.838 | 227.1828 | 259.5693 | 1.146%
7553 | 23-50.5 | -50.5797 | 22.5979 | 822.6169 | 126.9341 | 165.8411 | 200.1861 | 228.7781 | 261.455 | 1.2%
7554 | 23-51 | -50.851 | 22.5979 | 808.5604 | 128.5116 | 167.3754 | 201.4959 | 230.3413 | 263.3175 | 1.254%
7555 | 23-51 | -51.1224 | 22.5979 | 794.6494 | 130.0773 | 168.8078 | 202.8064 | 231.9254 | 265.2269 | 1.309%
7556 | 23-51.5 | -51.3937 | 22.5979 | 780.8914 | 131.5673 | 170.0856 | 204.0441 | 233.4263 | 267.0414 | 1.363%
7557 | 23-51.5 | -51.665 | 22.5979 | 767.295 | 133.0309 | 171.2688 | 205.2692 | 234.9264 | 268.8706 | 1.419%
7558 | 23-52 | -51.9363 | 22.5979 | 753.8687 | 134.5112 | 172.3995 | 206.5314 | 236.4915 | 270.8002 | 1.476%
7559 | 23-52 | -52.2077 | 22.5979 | 740.622 | 135.9433 | 173.4261 | 207.7434 | 237.9939 | 272.6523 | 1.533%
7560 | 23-52.5 | -52.479 | 22.5979 | 727.5646 | 137.3857 | 174.4161 | 208.9771 | 239.5326 | 274.5588 | 1.592%
7561 | 23-53 | -52.7503 | 22.5979 | 714.707 | 138.8758 | 175.4091 | 210.2778 | 241.169 | 276.6018 | 1.655%
7562 | 23-53 | -53.0216 | 22.5979 | 702.0601 | 140.3241 | 176.3395 | 211.5287 | 242.7388 | 278.5573 | 1.718%
7563 | 23-53.5 | -53.2929 | 22.5979 | 689.6356 | 141.8071 | 177.2807 | 212.8161 | 244.3598 | 280.5824 | 1.785%
7564 | 23-53.5 | -53.5643 | 22.5979 | 677.4458 | 143.3603 | 178.2638 | 214.1791 | 246.0847 | 282.7466 | 1.857%
7565 | 23-54 | -53.8356 | 22.5979 | 665.5036 | 144.8873 | 179.2252 | 215.5072 | 247.7608 | 284.8449 | 1.93%
7566 | 23-54 | -54.1069 | 22.5979 | 653.8225 | 146.4537 | 180.2109 | 216.8658 | 249.4734 | 286.9868 | 2.008%
7567 | 23-54.5 | -54.3782 | 22.5979 | 642.4169 | 148.075 | 181.2318 | 218.2684 | 251.2382 | 289.191 | 2.092%
7568 | 23-54.5 | -54.6495 | 22.5979 | 631.3017 | 149.6116 | 182.193 | 219.5707 | 252.8631 | 291.2059 | 2.174%
7569 | 23-55 | -54.9209 | 22.5979 | 620.4925 | 151.1318 | 183.1415 | 220.8481 | 254.4509 | 293.1689 | 2.258%
7570 | 23-55 | -55.1922 | 22.5979 | 610.0057 | 152.6421 | 184.0813 | 222.1055 | 256.0079 | 295.0873 | 2.345%
7571 | 23-55.5 | -55.4635 | 22.5979 | 599.8582 | 154.0456 | 184.9366 | 223.2146 | 257.3532 | 296.7152 | 2.429%
7572 | 23-55.5 | -55.7348 | 22.5979 | 590.0674 | 155.4058 | 185.7578 | 224.2641 | 258.6138 | 298.2267 | 2.513%
7573 | 23-56 | -56.0061 | 22.5979 | 580.6516 | 156.7153 | 186.5475 | 225.2575 | 259.7943 | 299.628 | 2.597%
7574 | 23-56.5 | -56.2775 | 22.5979 | 571.6291 | 157.9275 | 187.2674 | 226.132 | 260.8073 | 300.8015 | 2.678%
7575 | 23-56.5 | -56.5488 | 22.5979 | 563.019 | 159.1291 | 187.9907 | 227.006 | 261.8159 | 301.9654 | 2.761%
7576 | 23-57 | -56.8201 | 22.5979 | 554.8405 | 160.2985 | 188.7099 | 227.8666 | 262.8015 | 303.0942 | 2.844%
7577 | 23-57 | -57.0914 | 22.5979 | 547.113 | 161.3616 | 189.3626 | 228.6165 | 263.6331 | 304.0147 | 2.924%
7578 | 23-57.5 | -57.3628 | 22.5979 | 539.8558 | 162.4061 | 190.0208 | 229.3695 | 264.4649 | 304.9319 | 3.005%
7579 | 23-57.5 | -57.6341 | 22.5979 | 533.0881 | 163.4042 | 190.6758 | 230.1124 | 265.2798 | 305.8234 | 3.086%
7580 | 23-58 | -57.9054 | 22.5979 | 526.8289 | 164.2974 | 191.2844 | 230.7834 | 265.9978 | 306.5869 | 3.161%
7581 | 23-58 | -58.1767 | 22.5979 | 521.0965 | 165.2071 | 191.9464 | 231.5334 | 266.8196 | 307.4847 | 3.241%
7582 | 23-58.5 | -58.448 | 22.5979 | 515.9084 | 166.1008 | 192.6391 | 232.3281 | 267.6996 | 308.4572 | 3.321%
7583 | 23-58.5 | -58.7194 | 22.5979 | 511.2813 | 166.923 | 193.2984 | 233.0691 | 268.5058 | 309.3311 | 3.398%
7584 | 23-59 | -58.9907 | 22.5979 | 507.2305 | 167.7577 | 194.0058 | 233.892 | 269.4276 | 310.3626 | 3.478%
7585 | 23-59.5 | -59.262 | 22.5979 | 503.7699 | 168.5776 | 194.7379 | 234.7627 | 270.4201 | 311.4938 | 3.557%
7586 | 23-59.5 | -59.5333 | 22.5979 | 500.9118 | 169.3457 | 195.4484 | 235.6136 | 271.3953 | 312.6115 | 3.634%
7587 | 23-60 | -59.8046 | 22.5979 | 498.6665 | 170.0973 | 196.1831 | 236.5165 | 272.4503 | 313.8438 | 3.709%
7588 | 23-60 | -60.076 | 22.5979 | 497.0424 | 170.8031 | 196.9129 | 237.4286 | 273.5293 | 315.1194 | 3.781%
7589 | 23-60.5 | -60.3473 | 22.5979 | 496.0454 | 171.437 | 197.5992 | 238.2934 | 274.5581 | 316.3422 | 3.847%
7590 | 23-60.5 | -60.6186 | 22.5979 | 495.6795 | 172.0595 | 198.3093 | 239.2128 | 275.6725 | 317.6896 | 3.911%
7591 | 23-61 | -60.8899 | 22.5979 | 495.9461 | 172.6416 | 199.0068 | 240.1321 | 276.7999 | 319.0673 | 3.97%
7592 | 23-61 | -61.1613 | 22.5979 | 496.844 | 173.1655 | 199.6596 | 241.0043 | 277.8791 | 320.3965 | 4.024%
7593 | 23-61.5 | -61.4326 | 22.5979 | 498.3699 | 173.6824 | 200.322 | 241.9099 | 279.0157 | 321.8139 | 4.076%
7594 | 23-61.5 | -61.7039 | 22.5979 | 500.5181 | 174.162 | 200.9419 | 242.7653 | 280.0956 | 323.1672 | 4.124%
7595 | 23-62 | -61.9752 | 22.5979 | 503.2806 | 174.5878 | 201.4937 | 243.5287 | 281.061 | 324.3786 | 4.167%
7596 | 23-62 | -62.2465 | 22.5979 | 506.6472 | 175.0131 | 202.0573 | 244.3262 | 282.0831 | 325.6756 | 4.208%
7597 | 23-62.5 | -62.5179 | 22.5979 | 510.6062 | 175.3994 | 202.5748 | 245.0664 | 283.0375 | 326.8929 | 4.246%
7598 | 23-63 | -62.7892 | 22.5979 | 515.1437 | 175.7352 | 203.025 | 245.7106 | 283.8685 | 327.9531 | 4.278%
7599 | 23-63 | -63.0605 | 22.5979 | 520.2447 | 176.0649 | 203.4688 | 246.3482 | 284.6928 | 329.0066 | 4.309%
7600 | 23-63.5 | -63.3318 | 22.5979 | 525.8927 | 176.3587 | 203.8611 | 246.9077 | 285.4132 | 329.9242 | 4.338%
7601 | 23-63.5 | -63.6031 | 22.5979 | 532.0703 | 176.6223 | 204.2087 | 247.3971 | 286.0387 | 330.7163 | 4.364%
7602 | 23-64 | -63.8745 | 22.5979 | 538.7593 | 176.8989 | 204.5733 | 247.9106 | 286.6949 | 331.5473 | 4.392%
7603 | 23-64 | -64.1458 | 22.5979 | 545.9408 | 177.1512 | 204.901 | 248.3651 | 287.2709 | 332.2713 | 4.417%
7604 | 23-64.5 | -64.4171 | 22.5979 | 553.5957 | 177.3865 | 205.2018 | 248.7754 | 287.7853 | 332.9125 | 4.442%
7605 | 23-64.5 | -64.6884 | 22.5979 | 561.7046 | 177.6426 | 205.528 | 249.2189 | 288.3405 | 333.6035 | 4.469%
7606 | 23-65 | -64.9598 | 22.5979 | 570.2482 | 177.8673 | 205.8034 | 249.5778 | 288.7774 | 334.1342 | 4.494%
7607 | 23-65 | -65.2311 | 22.5979 | 579.2071 | 178.0754 | 206.0508 | 249.8885 | 289.1465 | 334.5724 | 4.518%
7608 | 23-65.5 | -65.5024 | 22.5979 | 588.5623 | 178.3071 | 206.3295 | 250.2434 | 289.5721 | 335.0822 | 4.545%
7609 | 23-66 | -65.7737 | 22.5979 | 598.2954 | 178.4984 | 206.5481 | 250.5045 | 289.8706 | 335.4237 | 4.569%
7610 | 23-66 | -66.045 | 22.5979 | 608.388 | 178.6669 | 206.7365 | 250.7222 | 290.1135 | 335.6942 | 4.59%
7611 | 23-66.5 | -66.3164 | 22.5979 | 618.8227 | 178.8472 | 206.9475 | 250.9824 | 290.4184 | 336.0518 | 4.612%
7612 | 23-66.5 | -66.5877 | 22.5979 | 629.5822 | 179.0045 | 207.1337 | 251.215 | 290.6938 | 336.3777 | 4.63%
7613 | 23-67 | -66.859 | 22.5979 | 640.6504 | 179.1601 | 207.3282 | 251.4743 | 291.0144 | 336.7729 | 4.648%
7614 | 23-67 | -67.1303 | 22.5979 | 652.0114 | 179.3336 | 207.56 | 251.8056 | 291.4422 | 337.3195 | 4.665%
7615 | 23-67.5 | -67.4016 | 22.5979 | 663.6501 | 179.4567 | 207.7315 | 252.0606 | 291.7787 | 337.7571 | 4.676%
7616 | 23-67.5 | -67.673 | 22.5979 | 675.5522 | 179.5557 | 207.8834 | 252.305 | 292.1145 | 338.2074 | 4.683%
7617 | 23-68 | -67.9443 | 22.5979 | 687.704 | 179.6527 | 208.0489 | 252.5918 | 292.5219 | 338.7669 | 4.688%
7618 | 23-68 | -68.2156 | 22.5979 | 700.0925 | 179.6872 | 208.1356 | 252.7722 | 292.7971 | 339.1626 | 4.687%
7619 | 23-68.5 | -68.4869 | 22.5979 | 712.7052 | 179.7046 | 208.2093 | 252.9478 | 293.0763 | 339.5738 | 4.682%
7620 | 23-69 | -68.7583 | 22.5979 | 725.5304 | 179.7265 | 208.3021 | 253.1694 | 293.4284 | 340.0927 | 4.676%
7621 | 23-69 | -69.0296 | 22.5979 | 738.5571 | 179.6909 | 208.3208 | 253.2886 | 293.6514 | 340.4496 | 4.663%
7622 | 23-69.5 | -69.3009 | 22.5979 | 751.7748 | 179.657 | 208.3493 | 253.4324 | 293.9139 | 340.865 | 4.651%
7623 | 23-69.5 | -69.5722 | 22.5979 | 765.1734 | 179.6454 | 208.4179 | 253.6477 | 294.2794 | 341.4232 | 4.639%
7624 | 23-70 | -69.8435 | 22.5979 | 778.7437 | 179.5823 | 208.4205 | 253.7727 | 294.5312 | 341.8393 | 4.622%
7625 | 23-70 | -70.1149 | 22.5979 | 792.4768 | 179.5014 | 208.4044 | 253.8782 | 294.7633 | 342.2357 | 4.603%
7626 | 23-70.5 | -70.3862 | 22.5979 | 806.3644 | 179.4081 | 208.3773 | 253.9757 | 294.9912 | 342.6332 | 4.582%
7627 | 23-70.5 | -70.6575 | 22.5979 | 820.3985 | 179.2365 | 208.2338 | 253.8906 | 294.9709 | 342.7008 | 4.555%
7628 | 23-71 | -70.9288 | 22.5979 | 834.5717 | 179.0545 | 208.0717 | 253.7723 | 294.9028 | 342.702 | 4.527%
7629 | 23-71 | -71.2001 | 22.5979 | 848.8771 | 178.8691 | 207.9002 | 253.6334 | 294.8029 | 342.6571 | 4.501%
7630 | 23-71.5 | -71.4715 | 22.5979 | 863.308 | 178.6295 | 207.638 | 253.3396 | 294.4842 | 342.3128 | 4.471%
7631 | 23-71.5 | -71.7428 | 22.5979 | 877.8582 | 178.3953 | 207.3784 | 253.043 | 294.157 | 341.9527 | 4.443%
7632 | 23-72 | -72.0141 | 22.5979 | 892.5219 | 178.1712 | 207.1269 | 252.7506 | 293.8295 | 341.5863 | 4.416%
7633 | 23-72.5 | -72.2854 | 22.5979 | 907.2934 | 177.9484 | 206.8547 | 252.3969 | 293.3994 | 341.0643 | 4.392%
7634 | 23-72.5 | -72.5568 | 22.5979 | 922.1677 | 177.787 | 206.6549 | 252.1334 | 293.0757 | 340.6677 | 4.375%
7635 | 23-73 | -72.8281 | 22.5979 | 937.1397 | 177.6644 | 206.4971 | 251.9162 | 292.8014 | 340.3234 | 4.363%
7636 | 23-73 | -73.0994 | 22.5979 | 952.2048 | 177.4764 | 206.237 | 251.5317 | 292.2954 | 339.6664 | 4.347%
7637 | 23-73.5 | -73.3707 | 22.5979 | 967.3586 | 177.2974 | 205.9835 | 251.1492 | 291.7865 | 339.0003 | 4.331%
7638 | 23-73.5 | -73.642 | 22.5979 | 982.5971 | 177.1053 | 205.7069 | 250.7259 | 291.2191 | 338.2531 | 4.315%
7639 | 23-74 | -73.9134 | 22.5979 | 997.9162 | 176.8186 | 205.323 | 250.1353 | 290.4253 | 337.206 | 4.292%
7640 | 23-74 | -74.1847 | 22.5979 | 1013.3123 | 176.4825 | 204.9413 | 249.5612 | 289.663 | 336.2101 | 4.263%
7641 | 23-74.5 | -74.456 | 22.5979 | 1028.7818 | 176.1105 | 204.5546 | 248.9883 | 288.9088 | 335.2312 | 4.23%
7642 | 23-74.5 | -74.7273 | 22.5979 | 1044.3216 | 175.7296 | 204.1541 | 248.3928 | 288.1231 | 334.2098 | 4.196%
7643 | 23-75 | -74.9986 | 22.5979 | 1059.9284 | 175.3927 | 203.8209 | 247.9095 | 287.4944 | 333.4017 | 4.166%
7644 | 23-75.5 | -75.27 | 22.5979 | 1075.5993 | 175.0779 | 203.4885 | 247.4337 | 286.8799 | 332.6162 | 4.137%
7645 | 23-75.5 | -75.5413 | 22.5979 | 1091.3315 | 174.7404 | 203.0502 | 246.8004 | 286.0577 | 331.5612 | 4.106%
7646 | 23-76 | -75.8126 | 22.5979 | 1107.1223 | 174.3078 | 202.5419 | 246.0879 | 285.1495 | 330.4137 | 4.066%
7647 | 23-76 | -76.0839 | 22.5979 | 1122.9693 | 173.7458 | 201.916 | 245.2169 | 284.0441 | 329.0225 | 4.013%
7648 | 23-76.5 | -76.3553 | 22.5979 | 1138.8701 | 173.0483 | 201.1396 | 244.1252 | 282.6499 | 327.2577 | 3.949%
7649 | 23-76.5 | -76.6266 | 22.5979 | 1154.8223 | 172.2984 | 200.3641 | 243.0383 | 281.2645 | 325.5072 | 3.88%
7650 | 23-77 | -76.8979 | 22.5979 | 1170.8239 | 171.5987 | 199.6548 | 242.0365 | 279.9816 | 323.88 | 3.818%
7651 | 23-77 | -77.1692 | 22.5979 | 1186.8729 | 171.0991 | 199.1178 | 241.2592 | 278.9721 | 322.5848 | 3.775%
7652 | 23-77.5 | -77.4405 | 22.5979 | 1202.9672 | 170.8612 | 198.8467 | 240.8498 | 278.4279 | 321.8737 | 3.755%
7653 | 23-77.5 | -77.7119 | 22.5979 | 1219.105 | 170.8264 | 198.7175 | 240.6186 | 278.0952 | 321.4133 | 3.754%
7654 | 23-78 | -77.9832 | 22.5979 | 1235.2847 | 170.8893 | 198.6224 | 240.4076 | 277.7674 | 320.9372 | 3.764%
7655 | 23-78.5 | -78.2545 | 22.5979 | 1251.5045 | 170.989 | 198.5811 | 240.2609 | 277.5134 | 320.5459 | 3.777%
7656 | 23-78.5 | -78.5258 | 22.5979 | 1267.7629 | 171.0804 | 198.5429 | 240.0993 | 277.2258 | 320.0973 | 3.791%
7657 | 23-79 | -78.7971 | 22.5979 | 1284.0583 | 171.1818 | 198.5364 | 239.9671 | 276.9646 | 319.6703 | 3.808%
7658 | 23-79 | -79.0685 | 22.5979 | 1300.3893 | 171.3463 | 198.6774 | 240.0455 | 276.9748 | 319.5891 | 3.831%
7659 | 23-79.5 | -79.3398 | 22.5979 | 1316.7547 | 171.6102 | 198.8927 | 240.2135 | 277.0876 | 319.6255 | 3.864%
7660 | 23-79.5 | -79.6111 | 22.5979 | 1333.1529 | 171.9826 | 199.1889 | 240.4805 | 277.3158 | 319.7961 | 3.908%
7661 | 23-80 | -79.8824 | 22.5979 | 1349.5829 | 172.5046 | 199.6396 | 240.9653 | 277.8231 | 320.3211 | 3.967%
7662 | 23-80 | -80.1537 | 22.5979 | 1366.0434 | 173.2269 | 200.2658 | 241.6839 | 278.6189 | 321.2011 | 4.046%
7663 | 23-80.5 | -80.4251 | 22.5979 | 1382.5333 | 174.054 | 201.018 | 242.5706 | 279.6227 | 322.337 | 4.138%
7664 | 23-80.5 | -80.6964 | 22.5979 | 1399.0515 | 174.8647 | 201.8277 | 243.5387 | 280.731 | 323.6055 | 4.231%
7665 | 23-81 | -80.9677 | 22.5979 | 1415.597 | 175.4969 | 202.4481 | 244.2411 | 281.5002 | 324.4455 | 4.308%
7666 | 23-81 | -81.239 | 22.5979 | 1432.1689 | 175.962 | 202.9109 | 244.7363 | 282.0157 | 324.976 | 4.368%
7667 | 23-81.5 | -81.5104 | 22.5979 | 1448.766 | 176.3572 | 203.3371 | 245.2037 | 282.5137 | 325.5032 | 4.419%
7668 | 23-82 | -81.7817 | 22.5979 | 1465.3876 | 176.7188 | 203.7086 | 245.5995 | 282.9244 | 325.924 | 4.468%
7669 | 23-82 | -82.053 | 22.5979 | 1482.0328 | 177.0898 | 204.072 | 245.9893 | 283.3313 | 326.3441 | 4.517%
7670 | 23-82.5 | -82.3243 | 22.5979 | 1498.7008 | 177.4772 | 204.4666 | 246.4321 | 283.8126 | 326.8655 | 4.568%
7671 | 23-82.5 | -82.5956 | 22.5979 | 1515.3907 | 177.9002 | 204.9163 | 246.9527 | 284.3934 | 327.5126 | 4.623%
7672 | 23-83 | -82.867 | 22.5979 | 1532.1019 | 178.4111 | 205.4966 | 247.6717 | 285.2384 | 328.5052 | 4.686%
7673 | 23-83 | -83.1383 | 22.5979 | 1548.8335 | 179.0372 | 206.2507 | 248.661 | 286.4477 | 329.9785 | 4.76%
7674 | 23-83.5 | -83.4096 | 22.5979 | 1565.5849 | 179.5936 | 206.9417 | 249.5894 | 287.6004 | 331.4022 | 4.824%
7675 | 23-83.5 | -83.6809 | 22.5979 | 1582.3554 | 180.0294 | 207.5124 | 250.3872 | 288.6153 | 332.6819 | 4.871%
7676 | 23-84 | -83.9522 | 22.5979 | 1599.1444 | 180.3391 | 207.9476 | 251.0377 | 289.4748 | 333.7995 | 4.901%
7677 | 23-84 | -84.2236 | 22.5979 | 1615.9512 | 180.4365 | 208.1308 | 251.3722 | 289.9598 | 334.4738 | 4.903%
7678 | 23-84.5 | -84.4949 | 22.5979 | 1632.7753 | 180.5029 | 208.2981 | 251.7198 | 290.4884 | 335.2313 | 4.898%
7679 | 23-85 | -84.7662 | 22.5979 | 1649.616 | 180.6072 | 208.5404 | 252.2082 | 291.2234 | 336.2779 | 4.894%
7680 | 23-85 | -85.0375 | 22.5979 | 1666.4729 | 180.6088 | 208.6608 | 252.5436 | 291.7767 | 337.1088 | 4.877%
7681 | 23-85.5 | -85.3089 | 22.5979 | 1683.3454 | 180.5075 | 208.6698 | 252.7563 | 292.1988 | 337.8003 | 4.846%
7682 | 23-85.5 | -85.5802 | 22.5979 | 1700.2331 | 180.2729 | 208.5704 | 252.8575 | 292.5095 | 338.3835 | 4.797%
7683 | 23-86 | -85.8515 | 22.5979 | 1717.1353 | 179.8906 | 208.3144 | 252.7637 | 292.5902 | 338.6953 | 4.732%
7684 | 23-86 | -86.1228 | 22.5979 | 1734.0516 | 179.3363 | 207.8727 | 252.4438 | 292.4089 | 338.7041 | 4.647%
7685 | 23-86.5 | -86.3941 | 22.5979 | 1750.9817 | 178.5973 | 207.2269 | 251.8735 | 291.9359 | 338.3735 | 4.543%
7686 | 23-86.5 | -86.6655 | 22.5979 | 1767.9249 | 177.5999 | 206.2792 | 250.8997 | 290.9635 | 337.4278 | 4.414%
7687 | 23-87 | -86.9368 | 22.5979 | 1784.8811 | 176.5161 | 205.2613 | 249.8479 | 289.9077 | 336.3937 | 4.28%
7688 | 23-87 | -87.2081 | 22.5979 | 1801.8496 | 175.3591 | 204.1855 | 248.7322 | 288.7835 | 335.2877 | 4.142%
7689 | 23-87.5 | -87.4794 | 22.5979 | 1818.8302 | 174.0599 | 202.9455 | 247.3719 | 287.3365 | 333.7614 | 3.997%
7690 | 23-88 | -87.7507 | 22.5979 | 1835.8224 | 172.6882 | 201.6498 | 245.9281 | 285.7786 | 332.0904 | 3.851%
7691 | 23-88 | -88.0221 | 22.5979 | 1852.8259 | 171.2481 | 200.3012 | 244.4028 | 284.1113 | 330.2752 | 3.705%
7692 | 23-88.5 | -88.2934 | 22.5979 | 1869.8404 | 169.7469 | 198.8834 | 242.7548 | 282.2677 | 328.216 | 3.561%
7693 | 23-88.5 | -88.5647 | 22.5979 | 1886.8654 | 168.3194 | 197.5832 | 241.2665 | 280.6239 | 326.4055 | 3.429%
7694 | 23-89 | -88.836 | 22.5979 | 1903.9007 | 166.9432 | 196.3709 | 239.8885 | 279.1108 | 324.7496 | 3.307%
7695 | 23-89 | -89.1074 | 22.5979 | 1920.9459 | 165.5524 | 195.1465 | 238.4508 | 277.4888 | 322.9212 | 3.19%
7696 | 23-89.5 | -89.3787 | 22.5979 | 1938.0008 | 164.1667 | 193.952 | 237.0322 | 275.8738 | 321.0831 | 3.079%
7697 | 23-89.5 | -89.65 | 22.5979 | 1955.0651 | 162.7788 | 192.7695 | 235.6023 | 274.2227 | 319.1765 | 2.972%
7698 | 23-90 | -89.9213 | 22.5979 | 1972.1384 | 161.3624 | 191.5661 | 234.0984 | 272.4432 | 317.0713 | 2.868%
7699 | 23-90 | -90.1926 | 22.5979 | 1989.2204 | 159.9978 | 190.4306 | 232.6619 | 270.7282 | 315.0252 | 2.772%
7700 | 23-90.5 | -90.464 | 22.5979 | 2006.311 | 158.6759 | 189.3414 | 231.2657 | 269.0458 | 313.0001 | 2.682%
7701 | 23-90.5 | -90.7353 | 22.5979 | 2023.4098 | 157.3603 | 188.2716 | 229.8818 | 267.3675 | 310.9679 | 2.596%
7702 | 23-50 | -50.0371 | 22.8692 | 861.6932 | 121.9986 | 160.6084 | 196.008 | 223.8211 | 255.5817 | 1.044%
7703 | 23-50.5 | -50.3084 | 22.8692 | 847.5716 | 123.6915 | 162.5388 | 197.4295 | 225.4879 | 257.5348 | 1.095%
7704 | 23-50.5 | -50.5797 | 22.8692 | 833.5857 | 125.318 | 164.3043 | 198.7802 | 227.0765 | 259.4017 | 1.147%
7705 | 23-51 | -50.851 | 22.8692 | 819.7424 | 126.8972 | 165.9273 | 200.0879 | 228.6279 | 261.2398 | 1.199%
7706 | 23-51 | -51.1224 | 22.8692 | 806.049 | 128.461 | 167.4369 | 201.3911 | 230.1946 | 263.1189 | 1.252%
7707 | 23-51.5 | -51.3937 | 22.8692 | 792.5135 | 129.9496 | 168.7822 | 202.6221 | 231.6809 | 264.9085 | 1.305%
7708 | 23-51.5 | -51.665 | 22.8692 | 779.1441 | 131.4097 | 170.0218 | 203.8404 | 233.1691 | 266.7194 | 1.358%
7709 | 23-52 | -51.9363 | 22.8692 | 765.9494 | 132.8823 | 171.1954 | 205.0946 | 234.7248 | 268.6378 | 1.413%
7710 | 23-52 | -52.2077 | 22.8692 | 752.9387 | 134.3041 | 172.2516 | 206.2987 | 236.2201 | 270.4839 | 1.468%
7711 | 23-52.5 | -52.479 | 22.8692 | 740.1218 | 135.7362 | 173.2641 | 207.5281 | 237.7581 | 272.3944 | 1.524%
7712 | 23-53 | -52.7503 | 22.8692 | 727.5089 | 137.2175 | 174.2751 | 208.83 | 239.4021 | 274.4531 | 1.585%
7713 | 23-53 | -53.0216 | 22.8692 | 715.1108 | 138.6568 | 175.2165 | 210.0868 | 240.987 | 276.4355 | 1.645%
7714 | 23-53.5 | -53.2929 | 22.8692 | 702.939 | 140.1329 | 176.1678 | 211.3886 | 242.6361 | 278.506 | 1.709%
7715 | 23-53.5 | -53.5643 | 22.8692 | 691.0054 | 141.6833 | 177.1626 | 212.7769 | 244.4048 | 280.7375 | 1.778%
7716 | 23-54 | -53.8356 | 22.8692 | 679.3227 | 143.2127 | 178.1365 | 214.1398 | 246.1382 | 282.9213 | 1.849%
7717 | 23-54 | -54.1069 | 22.8692 | 667.9039 | 144.7904 | 179.1426 | 215.5446 | 247.9227 | 285.1674 | 1.924%
7718 | 23-54.5 | -54.3782 | 22.8692 | 656.763 | 146.4336 | 180.1929 | 217.0057 | 249.7748 | 287.4951 | 2.005%
7719 | 23-54.5 | -54.6495 | 22.8692 | 645.9143 | 148.0046 | 181.1922 | 218.3764 | 251.498 | 289.6459 | 2.086%
7720 | 23-55 | -54.9209 | 22.8692 | 635.3728 | 149.5683 | 182.1843 | 219.7267 | 253.1876 | 291.7464 | 2.17%
7721 | 23-55 | -55.1922 | 22.8692 | 625.154 | 151.1307 | 183.1723 | 221.0595 | 254.8463 | 293.7993 | 2.256%
7722 | 23-55.5 | -55.4635 | 22.8692 | 615.2742 | 152.591 | 184.0761 | 222.2394 | 256.2841 | 295.5459 | 2.34%
7723 | 23-55.5 | -55.7348 | 22.8692 | 605.7498 | 154.0124 | 184.9444 | 223.3551 | 257.6292 | 297.1645 | 2.424%
7724 | 23-56 | -56.0061 | 22.8692 | 596.598 | 155.3874 | 185.7789 | 224.4098 | 258.8865 | 298.6616 | 2.509%
7725 | 23-56.5 | -56.2775 | 22.8692 | 587.8361 | 156.6654 | 186.5399 | 225.3384 | 259.9659 | 299.9162 | 2.591%
7726 | 23-56.5 | -56.5488 | 22.8692 | 579.4819 | 157.9367 | 187.3015 | 226.26 | 261.0305 | 301.1458 | 2.676%
7727 | 23-57 | -56.8201 | 22.8692 | 571.5533 | 159.1792 | 188.0556 | 227.1604 | 262.06 | 302.323 | 2.762%
7728 | 23-57 | -57.0914 | 22.8692 | 564.0682 | 160.3155 | 188.7383 | 227.9393 | 262.9188 | 303.2678 | 2.845%
7729 | 23-57.5 | -57.3628 | 22.8692 | 557.0445 | 161.4338 | 189.4222 | 228.7125 | 263.7645 | 304.1902 | 2.929%
7730 | 23-57.5 | -57.6341 | 22.8692 | 550.5 | 162.5071 | 190.0988 | 229.4676 | 264.5815 | 305.0701 | 3.013%
7731 | 23-58 | -57.9054 | 22.8692 | 544.4519 | 163.4768 | 190.7276 | 230.1474 | 265.296 | 305.814 | 3.093%
7732 | 23-58 | -58.1767 | 22.8692 | 538.9169 | 164.4593 | 191.4093 | 230.9058 | 266.1141 | 306.6921 | 3.176%
7733 | 23-58.5 | -58.448 | 22.8692 | 533.911 | 165.4215 | 192.1207 | 231.708 | 266.9896 | 307.6445 | 3.261%
7734 | 23-58.5 | -58.7194 | 22.8692 | 529.4492 | 166.3075 | 192.798 | 232.4555 | 267.7902 | 308.4967 | 3.343%
7735 | 23-59 | -58.9907 | 22.8692 | 525.5455 | 167.2052 | 193.5263 | 233.2901 | 268.7136 | 309.5164 | 3.427%
7736 | 23-59.5 | -59.262 | 22.8692 | 522.2122 | 168.0853 | 194.282 | 234.1769 | 269.7139 | 310.6443 | 3.511%
7737 | 23-59.5 | -59.5333 | 22.8692 | 519.4605 | 168.9101 | 195.0185 | 235.048 | 270.7026 | 311.7661 | 3.593%
7738 | 23-60 | -59.8046 | 22.8692 | 517.2996 | 169.7183 | 195.7835 | 235.9776 | 271.7799 | 313.0144 | 3.673%
7739 | 23-60 | -60.076 | 22.8692 | 515.7369 | 170.4794 | 196.548 | 236.9235 | 272.8906 | 314.3182 | 3.751%
7740 | 23-60.5 | -60.3473 | 22.8692 | 514.7779 | 171.1667 | 197.2735 | 237.829 | 273.9605 | 315.5817 | 3.822%
7741 | 23-60.5 | -60.6186 | 22.8692 | 514.426 | 171.8436 | 198.0282 | 238.798 | 275.1283 | 316.9864 | 3.891%
7742 | 23-61 | -60.8899 | 22.8692 | 514.6823 | 172.4789 | 198.7753 | 239.7752 | 276.3209 | 318.4373 | 3.957%
7743 | 23-61 | -61.1613 | 22.8692 | 515.5461 | 173.0525 | 199.4812 | 240.7122 | 277.4753 | 319.8538 | 4.016%
7744 | 23-61.5 | -61.4326 | 22.8692 | 517.0142 | 173.6152 | 200.1975 | 241.6847 | 278.6908 | 321.3639 | 4.073%
7745 | 23-61.5 | -61.7039 | 22.8692 | 519.0816 | 174.1389 | 200.8699 | 242.606 | 279.8487 | 322.8095 | 4.126%
7746 | 23-62 | -61.9752 | 22.8692 | 521.741 | 174.6057 | 201.4706 | 243.431 | 280.8872 | 324.1077 | 4.174%
7747 | 23-62 | -62.2465 | 22.8692 | 524.9835 | 175.069 | 202.0799 | 244.2866 | 281.9788 | 325.4877 | 4.219%
7748 | 23-62.5 | -62.5179 | 22.8692 | 528.7984 | 175.4908 | 202.6402 | 245.0813 | 282.9987 | 326.7833 | 4.261%
7749 | 23-63 | -62.7892 | 22.8692 | 533.1734 | 175.86 | 203.1306 | 245.7768 | 283.8912 | 327.9171 | 4.297%
7750 | 23-63 | -63.0605 | 22.8692 | 538.0947 | 176.2214 | 203.6126 | 246.4631 | 284.7739 | 329.0405 | 4.332%
7751 | 23-63.5 | -63.3318 | 22.8692 | 543.5476 | 176.5438 | 204.0397 | 247.0672 | 285.5479 | 330.0224 | 4.364%
7752 | 23-63.5 | -63.6031 | 22.8692 | 549.5162 | 176.8325 | 204.4179 | 247.5964 | 286.2217 | 330.873 | 4.393%
7753 | 23-64 | -63.8745 | 22.8692 | 555.9838 | 177.1311 | 204.8101 | 248.1465 | 286.9232 | 331.7596 | 4.423%
7754 | 23-64 | -64.1458 | 22.8692 | 562.9333 | 177.4013 | 205.1606 | 248.632 | 287.5378 | 332.5317 | 4.451%
7755 | 23-64.5 | -64.4171 | 22.8692 | 570.3471 | 177.6509 | 205.4795 | 249.0669 | 288.0829 | 333.2109 | 4.477%
7756 | 23-64.5 | -64.6884 | 22.8692 | 578.2072 | 177.9191 | 205.8204 | 249.5294 | 288.6609 | 333.9294 | 4.506%
7757 | 23-65 | -64.9598 | 22.8692 | 586.4957 | 178.1532 | 206.1065 | 249.9007 | 289.112 | 334.4761 | 4.532%
7758 | 23-65 | -65.2311 | 22.8692 | 595.1947 | 178.3695 | 206.3626 | 250.2208 | 289.4908 | 334.924 | 4.558%
7759 | 23-65.5 | -65.5024 | 22.8692 | 604.2864 | 178.6102 | 206.6508 | 250.5857 | 289.9265 | 335.444 | 4.586%
7760 | 23-66 | -65.7737 | 22.8692 | 613.7533 | 178.8087 | 206.875 | 250.8491 | 290.2238 | 335.7795 | 4.611%
7761 | 23-66 | -66.045 | 22.8692 | 623.5784 | 178.9816 | 207.0635 | 251.0591 | 290.4508 | 336.0237 | 4.633%
7762 | 23-66.5 | -66.3164 | 22.8692 | 633.745 | 179.1633 | 207.2695 | 251.3025 | 290.7268 | 336.3367 | 4.656%
7763 | 23-66.5 | -66.5877 | 22.8692 | 644.2368 | 179.3199 | 207.4475 | 251.5134 | 290.9666 | 336.6094 | 4.676%
7764 | 23-67 | -66.859 | 22.8692 | 655.0383 | 179.4741 | 207.6324 | 251.7481 | 291.2477 | 336.9457 | 4.694%
7765 | 23-67 | -67.1303 | 22.8692 | 666.1343 | 179.6464 | 207.854 | 252.053 | 291.6323 | 337.4277 | 4.713%
7766 | 23-67.5 | -67.4016 | 22.8692 | 677.5103 | 179.7679 | 208.0146 | 252.2798 | 291.9231 | 337.7974 | 4.725%
7767 | 23-67.5 | -67.673 | 22.8692 | 689.1524 | 179.8663 | 208.1569 | 252.4985 | 292.2167 | 338.1845 | 4.734%
7768 | 23-68 | -67.9443 | 22.8692 | 701.0475 | 179.9641 | 208.3156 | 252.7643 | 292.5888 | 338.6901 | 4.74%
7769 | 23-68 | -68.2156 | 22.8692 | 713.1826 | 180.0009 | 208.3977 | 252.9277 | 292.8343 | 339.0395 | 4.739%
7770 | 23-68.5 | -68.4869 | 22.8692 | 725.5459 | 180.0231 | 208.4705 | 253.0917 | 293.0906 | 339.4136 | 4.735%
7771 | 23-69 | -68.7583 | 22.8692 | 738.1258 | 180.0531 | 208.5666 | 253.3075 | 293.4276 | 339.9049 | 4.731%
7772 | 23-69 | -69.0296 | 22.8692 | 750.9113 | 180.0282 | 208.5925 | 253.4269 | 293.6433 | 340.2449 | 4.72%
7773 | 23-69.5 | -69.3009 | 22.8692 | 763.8922 | 180.0103 | 208.6366 | 253.5851 | 293.9185 | 340.6702 | 4.71%
7774 | 23-69.5 | -69.5722 | 22.8692 | 777.0586 | 180.0211 | 208.731 | 253.8316 | 294.3198 | 341.2696 | 4.7%
7775 | 23-70 | -69.8435 | 22.8692 | 790.4012 | 179.9866 | 208.7706 | 254.0076 | 294.6361 | 341.7667 | 4.686%
7776 | 23-70 | -70.1149 | 22.8692 | 803.9112 | 179.94 | 208.8006 | 254.1793 | 294.954 | 342.2729 | 4.669%
7777 | 23-70.5 | -70.3862 | 22.8692 | 817.5802 | 179.8866 | 208.8279 | 254.3564 | 295.2856 | 342.8043 | 4.651%
7778 | 23-70.5 | -70.6575 | 22.8692 | 831.4005 | 179.7564 | 208.7418 | 254.3558 | 295.3764 | 343.0157 | 4.628%
7779 | 23-71 | -70.9288 | 22.8692 | 845.3645 | 179.6186 | 208.6403 | 254.3261 | 295.4242 | 343.1664 | 4.604%
7780 | 23-71 | -71.2001 | 22.8692 | 859.4651 | 179.4798 | 208.5317 | 254.2782 | 295.4424 | 343.2731 | 4.581%
7781 | 23-71.5 | -71.4715 | 22.8692 | 873.6959 | 179.2874 | 208.3326 | 254.0746 | 295.2401 | 343.0776 | 4.556%
7782 | 23-71.5 | -71.7428 | 22.8692 | 888.0504 | 179.1005 | 208.1358 | 253.8672 | 295.0275 | 342.8633 | 4.532%
7783 | 23-72 | -72.0141 | 22.8692 | 902.5227 | 178.9244 | 207.9474 | 253.6632 | 294.813 | 342.6401 | 4.509%
7784 | 23-72.5 | -72.2854 | 22.8692 | 917.1073 | 178.7533 | 207.7432 | 253.4055 | 294.5058 | 342.2739 | 4.49%
7785 | 23-72.5 | -72.5568 | 22.8692 | 931.7987 | 178.6479 | 207.6168 | 253.2448 | 294.313 | 342.0428 | 4.478%
7786 | 23-73 | -72.8281 | 22.8692 | 946.592 | 178.5819 | 207.5326 | 253.1299 | 294.1686 | 341.8622 | 4.472%
7787 | 23-73 | -73.0994 | 22.8692 | 961.4825 | 178.4364 | 207.3274 | 252.8212 | 293.7585 | 341.3257 | 4.459%
7788 | 23-73.5 | -73.3707 | 22.8692 | 976.4657 | 178.2863 | 207.109 | 252.4842 | 293.3048 | 340.7264 | 4.447%
7789 | 23-73.5 | -73.642 | 22.8692 | 991.5373 | 178.119 | 206.8607 | 252.0943 | 292.7753 | 340.0224 | 4.434%
7790 | 23-74 | -73.9134 | 22.8692 | 1006.6933 | 177.9006 | 206.5349 | 251.5771 | 292.0691 | 339.0795 | 4.417%
7791 | 23-74 | -74.1847 | 22.8692 | 1021.93 | 177.686 | 206.2458 | 251.1232 | 291.4528 | 338.2604 | 4.4%
7792 | 23-74.5 | -74.456 | 22.8692 | 1037.2437 | 177.468 | 205.9725 | 250.6986 | 290.8795 | 337.5018 | 4.382%
7793 | 23-74.5 | -74.7273 | 22.8692 | 1052.6311 | 177.2351 | 205.678 | 250.2413 | 290.2622 | 336.6848 | 4.363%
7794 | 23-75 | -74.9986 | 22.8692 | 1068.0888 | 177.0406 | 205.4452 | 249.8886 | 289.7921 | 336.069 | 4.346%
7795 | 23-75.5 | -75.27 | 22.8692 | 1083.614 | 176.823 | 205.1768 | 249.4933 | 289.2733 | 335.3973 | 4.326%
7796 | 23-75.5 | -75.5413 | 22.8692 | 1099.2036 | 176.4663 | 204.7079 | 248.8097 | 288.3814 | 334.2484 | 4.293%
7797 | 23-76 | -75.8126 | 22.8692 | 1114.855 | 175.9363 | 204.0667 | 247.9035 | 287.2206 | 332.7754 | 4.243%
7798 | 23-76 | -76.0839 | 22.8692 | 1130.5655 | 175.2444 | 203.2658 | 246.7801 | 285.7881 | 330.9647 | 4.176%
7799 | 23-76.5 | -76.3553 | 22.8692 | 1146.3326 | 174.4547 | 202.3644 | 245.5076 | 284.159 | 328.8986 | 4.102%
7800 | 23-76.5 | -76.6266 | 22.8692 | 1162.1541 | 173.6638 | 201.5318 | 244.3362 | 282.6623 | 327.004 | 4.028%
7801 | 23-77 | -76.8979 | 22.8692 | 1178.0277 | 172.9518 | 200.8049 | 243.3076 | 281.3439 | 325.3304 | 3.962%
7802 | 23-77 | -77.1692 | 22.8692 | 1193.9512 | 172.4335 | 200.2448 | 242.5003 | 280.2979 | 323.9908 | 3.916%
7803 | 23-77.5 | -77.4405 | 22.8692 | 1209.9227 | 172.1231 | 199.9089 | 242.0064 | 279.6508 | 323.1548 | 3.889%
7804 | 23-77.5 | -77.7119 | 22.8692 | 1225.9403 | 171.9543 | 199.6712 | 241.6332 | 279.1449 | 322.4837 | 3.876%
7805 | 23-78 | -77.9832 | 22.8692 | 1242.0021 | 171.8407 | 199.4349 | 241.2376 | 278.5918 | 321.7336 | 3.869%
7806 | 23-78.5 | -78.2545 | 22.8692 | 1258.1064 | 171.7597 | 199.2483 | 240.9026 | 278.1094 | 321.066 | 3.866%
7807 | 23-78.5 | -78.5258 | 22.8692 | 1274.2515 | 171.6683 | 199.0618 | 240.5507 | 277.5926 | 320.3416 | 3.863%
7808 | 23-79 | -78.7971 | 22.8692 | 1290.4359 | 171.6249 | 198.9358 | 240.27 | 277.1563 | 319.7084 | 3.865%
7809 | 23-79 | -79.0685 | 22.8692 | 1306.658 | 171.7528 | 199.0429 | 240.3208 | 277.1462 | 319.6175 | 3.884%
7810 | 23-79.5 | -79.3398 | 22.8692 | 1322.9165 | 172.0456 | 199.3107 | 240.5832 | 277.3953 | 319.8428 | 3.919%
7811 | 23-79.5 | -79.6111 | 22.8692 | 1339.21 | 172.466 | 199.6846 | 240.9801 | 277.8054 | 320.2604 | 3.967%
7812 | 23-80 | -79.8824 | 22.8692 | 1355.5372 | 172.9882 | 200.1502 | 241.5065 | 278.3813 | 320.8888 | 4.025%
7813 | 23-80 | -80.1537 | 22.8692 | 1371.8967 | 173.6641 | 200.7297 | 242.1795 | 279.1342 | 321.7303 | 4.1%
7814 | 23-80.5 | -80.4251 | 22.8692 | 1388.2876 | 174.4202 | 201.4016 | 242.9719 | 280.0315 | 322.746 | 4.185%
7815 | 23-80.5 | -80.6964 | 22.8692 | 1404.7085 | 175.1602 | 202.1292 | 243.8401 | 281.0237 | 323.88 | 4.27%
7816 | 23-81 | -80.9677 | 22.8692 | 1421.1584 | 175.7243 | 202.6689 | 244.4417 | 281.6737 | 324.5791 | 4.34%
7817 | 23-81 | -81.239 | 22.8692 | 1437.6364 | 176.1263 | 203.0564 | 244.8417 | 282.076 | 324.9749 | 4.393%
7818 | 23-81.5 | -81.5104 | 22.8692 | 1454.1413 | 176.4648 | 203.415 | 245.2244 | 282.4736 | 325.3831 | 4.438%
7819 | 23-82 | -81.7817 | 22.8692 | 1470.6723 | 176.776 | 203.727 | 245.5459 | 282.7963 | 325.6999 | 4.481%
7820 | 23-82 | -82.053 | 22.8692 | 1487.2284 | 177.1026 | 204.0377 | 245.8699 | 283.1254 | 326.0282 | 4.525%
7821 | 23-82.5 | -82.3243 | 22.8692 | 1503.8087 | 177.451 | 204.3863 | 246.2552 | 283.5389 | 326.4695 | 4.571%
7822 | 23-82.5 | -82.5956 | 22.8692 | 1520.4125 | 177.8397 | 204.7953 | 246.725 | 284.0596 | 327.0456 | 4.622%
7823 | 23-83 | -82.867 | 22.8692 | 1537.0389 | 178.3214 | 205.3414 | 247.4019 | 284.8553 | 327.9803 | 4.682%
7824 | 23-83 | -83.1383 | 22.8692 | 1553.6872 | 178.9245 | 206.0692 | 248.3597 | 286.0287 | 329.4127 | 4.753%
7825 | 23-83.5 | -83.4096 | 22.8692 | 1570.3566 | 179.463 | 206.7399 | 249.2641 | 287.1539 | 330.8052 | 4.814%
7826 | 23-83.5 | -83.6809 | 22.8692 | 1587.0463 | 179.8862 | 207.2963 | 250.0452 | 288.1499 | 332.0636 | 4.86%
7827 | 23-84 | -83.9522 | 22.8692 | 1603.7558 | 180.1886 | 207.7236 | 250.6865 | 288.9993 | 333.17 | 4.888%
7828 | 23-84 | -84.2236 | 22.8692 | 1620.4844 | 180.2901 | 207.9139 | 251.0337 | 289.5025 | 333.8691 | 4.891%
7829 | 23-84.5 | -84.4949 | 22.8692 | 1637.2315 | 180.3698 | 208.1011 | 251.4123 | 290.0728 | 334.6817 | 4.887%
7830 | 23-85 | -84.7662 | 22.8692 | 1653.9963 | 180.4962 | 208.3744 | 251.947 | 290.869 | 335.8078 | 4.885%
7831 | 23-85 | -85.0375 | 22.8692 | 1670.7785 | 180.5528 | 208.567 | 252.3837 | 291.5514 | 336.8018 | 4.874%
7832 | 23-85.5 | -85.3089 | 22.8692 | 1687.5773 | 180.5398 | 208.6897 | 252.7524 | 292.17 | 337.739 | 4.852%
7833 | 23-85.5 | -85.5802 | 22.8692 | 1704.3923 | 180.4542 | 208.7433 | 253.0613 | 292.7403 | 338.6447 | 4.82%
7834 | 23-86 | -85.8515 | 22.8692 | 1721.223 | 180.2311 | 208.642 | 253.1742 | 293.0768 | 339.2718 | 4.772%
7835 | 23-86 | -86.1228 | 22.8692 | 1738.0688 | 179.8464 | 208.3586 | 253.0627 | 293.1507 | 339.5921 | 4.705%
7836 | 23-86.5 | -86.3941 | 22.8692 | 1754.9293 | 179.2869 | 207.8756 | 252.7033 | 292.9337 | 339.5714 | 4.619%
7837 | 23-86.5 | -86.6655 | 22.8692 | 1771.804 | 178.4813 | 207.0951 | 251.9465 | 292.225 | 338.9456 | 4.509%
7838 | 23-87 | -86.9368 | 22.8692 | 1788.6924 | 177.6012 | 206.2511 | 251.1228 | 291.448 | 338.2514 | 4.392%
7839 | 23-87 | -87.2081 | 22.8692 | 1805.5942 | 176.6589 | 205.3561 | 250.246 | 290.6176 | 337.5052 | 4.272%
7840 | 23-87.5 | -87.4794 | 22.8692 | 1822.5089 | 175.5827 | 204.2993 | 249.1291 | 289.4706 | 336.3475 | 4.145%
7841 | 23-88 | -87.7507 | 22.8692 | 1839.4361 | 174.436 | 203.182 | 247.9211 | 288.2027 | 335.0319 | 4.015%
7842 | 23-88 | -88.0221 | 22.8692 | 1856.3754 | 173.2153 | 202.0014 | 246.617 | 286.8066 | 333.5484 | 3.883%
7843 | 23-88.5 | -88.2934 | 22.8692 | 1873.3265 | 171.8961 | 200.7162 | 245.1412 | 285.1724 | 331.7432 | 3.749%
7844 | 23-88.5 | -88.5647 | 22.8692 | 1890.289 | 170.5879 | 199.4829 | 243.7353 | 283.6252 | 330.0457 | 3.621%
7845 | 23-89 | -88.836 | 22.8692 | 1907.2625 | 169.2769 | 198.2789 | 242.3592 | 282.1073 | 328.3764 | 3.498%
7846 | 23-89 | -89.1074 | 22.8692 | 1924.2467 | 167.9003 | 197.0274 | 240.8763 | 280.4223 | 326.4628 | 3.376%
7847 | 23-89.5 | -89.3787 | 22.8692 | 1941.2413 | 166.5273 | 195.8081 | 239.4171 | 278.751 | 324.549 | 3.259%
7848 | 23-89.5 | -89.65 | 22.8692 | 1958.246 | 165.149 | 194.6007 | 237.9476 | 277.0461 | 322.5706 | 3.147%
7849 | 23-90 | -89.9213 | 22.8692 | 1975.2604 | 163.7352 | 193.3661 | 236.397 | 275.2046 | 320.3847 | 3.038%
7850 | 23-90 | -90.1926 | 22.8692 | 1992.2843 | 162.3629 | 192.1936 | 234.9034 | 273.4128 | 318.2371 | 2.936%
7851 | 23-90.5 | -90.464 | 22.8692 | 2009.3174 | 161.0207 | 191.0608 | 233.4389 | 271.6378 | 316.0894 | 2.84%
7852 | 23-90.5 | -90.7353 | 22.8692 | 2026.3593 | 159.6695 | 189.9397 | 231.9757 | 269.8529 | 313.9163 | 2.748%
7853 | 23-50 | -50.0371 | 23.1405 | 872.5203 | 120.5385 | 158.9526 | 194.7403 | 222.3168 | 253.7995 | 1.001%
7854 | 23-50.5 | -50.3084 | 23.1405 | 858.6023 | 122.2389 | 160.981 | 196.1756 | 223.9936 | 255.7572 | 1.051%
7855 | 23-50.5 | -50.5797 | 23.1405 | 844.8241 | 123.8725 | 162.846 | 197.5356 | 225.5854 | 257.6194 | 1.101%
7856 | 23-51 | -50.851 | 23.1405 | 831.1929 | 125.4566 | 164.5635 | 198.8469 | 227.1331 | 259.4441 | 1.152%
7857 | 23-51 | -51.1224 | 23.1405 | 817.7159 | 127.0223 | 166.1568 | 200.1482 | 228.6899 | 261.3028 | 1.204%
7858 | 23-51.5 | -51.3937 | 23.1405 | 804.4011 | 128.5119 | 167.5753 | 201.3759 | 230.166 | 263.0734 | 1.255%
7859 | 23-51.5 | -51.665 | 23.1405 | 791.2565 | 129.9692 | 168.8747 | 202.5881 | 231.6439 | 264.8687 | 1.306%
7860 | 23-52 | -51.9363 | 23.1405 | 778.2908 | 131.4325 | 170.0923 | 203.8327 | 233.1892 | 266.7758 | 1.359%
7861 | 23-52 | -52.2077 | 23.1405 | 765.5132 | 132.8399 | 171.1761 | 205.0235 | 234.6715 | 268.6094 | 1.411%
7862 | 23-52.5 | -52.479 | 23.1405 | 752.9333 | 134.2557 | 172.2075 | 206.2404 | 236.1988 | 270.5117 | 1.466%
7863 | 23-53 | -52.7503 | 23.1405 | 740.5612 | 135.7208 | 173.2316 | 207.5327 | 237.8368 | 272.5692 | 1.523%
7864 | 23-53 | -53.0216 | 23.1405 | 728.4075 | 137.143 | 174.1786 | 208.7833 | 239.4208 | 274.5577 | 1.581%
7865 | 23-53.5 | -53.2929 | 23.1405 | 716.4834 | 138.6034 | 175.1339 | 210.0855 | 241.0787 | 276.6476 | 1.642%
7866 | 23-53.5 | -53.5643 | 23.1405 | 704.8005 | 140.1414 | 176.1332 | 211.483 | 242.8683 | 278.915 | 1.708%
7867 | 23-54 | -53.8356 | 23.1405 | 693.371 | 141.6609 | 177.109 | 212.8613 | 244.631 | 281.1459 | 1.776%
7868 | 23-54 | -54.1069 | 23.1405 | 682.2078 | 143.2348 | 178.1234 | 214.2921 | 246.4594 | 283.4584 | 1.848%
7869 | 23-54.5 | -54.3782 | 23.1405 | 671.3241 | 144.8828 | 179.1901 | 215.7918 | 248.3723 | 285.8748 | 1.927%
7870 | 23-54.5 | -54.6495 | 23.1405 | 660.7338 | 146.4713 | 180.2153 | 217.2127 | 250.1698 | 288.1299 | 2.005%
7871 | 23-55 | -54.9209 | 23.1405 | 650.4512 | 148.0642 | 181.2415 | 218.6217 | 251.9421 | 290.3433 | 2.087%
7872 | 23-55 | -55.1922 | 23.1405 | 640.4912 | 149.6667 | 182.271 | 220.0198 | 253.6895 | 292.5136 | 2.173%
7873 | 23-55.5 | -55.4635 | 23.1405 | 630.8691 | 151.1722 | 183.2186 | 221.2634 | 255.2101 | 294.3667 | 2.256%
7874 | 23-55.5 | -55.7348 | 23.1405 | 621.6006 | 152.645 | 184.1316 | 222.4425 | 256.6365 | 296.0885 | 2.341%
7875 | 23-56 | -56.0061 | 23.1405 | 612.7018 | 154.0788 | 185.0113 | 223.5602 | 257.974 | 297.6866 | 2.426%
7876 | 23-56.5 | -56.2775 | 23.1405 | 604.189 | 155.4186 | 185.8157 | 224.5479 | 259.1272 | 299.033 | 2.509%
7877 | 23-56.5 | -56.5488 | 23.1405 | 596.0787 | 156.757 | 186.6194 | 225.5245 | 260.2591 | 300.3446 | 2.595%
7878 | 23-57 | -56.8201 | 23.1405 | 588.3878 | 158.0716 | 187.4133 | 226.4747 | 261.3474 | 301.5913 | 2.684%
7879 | 23-57 | -57.0914 | 23.1405 | 581.1327 | 159.2807 | 188.1316 | 227.2941 | 262.2508 | 302.585 | 2.768%
7880 | 23-57.5 | -57.3628 | 23.1405 | 574.3302 | 160.4758 | 188.849 | 228.1021 | 263.1318 | 303.5426 | 2.856%
7881 | 23-57.5 | -57.6341 | 23.1405 | 567.9963 | 161.6296 | 189.5568 | 228.8863 | 263.9749 | 304.444 | 2.943%
7882 | 23-58 | -57.9054 | 23.1405 | 562.1471 | 162.6815 | 190.2151 | 229.5907 | 264.7081 | 305.1984 | 3.028%
7883 | 23-58 | -58.1767 | 23.1405 | 556.7977 | 163.7408 | 190.9241 | 230.371 | 265.5418 | 306.0836 | 3.115%
7884 | 23-58.5 | -58.448 | 23.1405 | 551.9628 | 164.7736 | 191.6597 | 231.1911 | 266.4281 | 307.0369 | 3.204%
7885 | 23-58.5 | -58.7194 | 23.1405 | 547.6559 | 165.7236 | 192.3574 | 231.9505 | 267.2314 | 307.8795 | 3.29%
7886 | 23-59 | -58.9907 | 23.1405 | 543.8896 | 166.6845 | 193.107 | 232.7991 | 268.1606 | 308.894 | 3.378%
7887 | 23-59.5 | -59.262 | 23.1405 | 540.6753 | 167.6243 | 193.8848 | 233.7011 | 269.1685 | 310.0191 | 3.467%
7888 | 23-59.5 | -59.5333 | 23.1405 | 538.0228 | 168.5034 | 194.644 | 234.588 | 270.1653 | 311.1388 | 3.553%
7889 | 23-60 | -59.8046 | 23.1405 | 535.9405 | 169.3649 | 195.4347 | 235.538 | 271.257 | 312.393 | 3.639%
7890 | 23-60 | -60.076 | 23.1405 | 534.4351 | 170.1768 | 196.2282 | 236.5097 | 272.3893 | 313.7124 | 3.721%
7891 | 23-60.5 | -60.3473 | 23.1405 | 533.5113 | 170.9123 | 196.9866 | 237.4474 | 273.4898 | 315.0036 | 3.796%
7892 | 23-60.5 | -60.6186 | 23.1405 | 533.1724 | 171.6379 | 197.7799 | 238.4583 | 274.702 | 316.4549 | 3.871%
7893 | 23-61 | -60.8899 | 23.1405 | 533.4193 | 172.3204 | 198.5702 | 239.4857 | 275.9505 | 317.9682 | 3.942%
7894 | 23-61 | -61.1613 | 23.1405 | 534.2513 | 172.9383 | 199.323 | 240.479 | 277.1697 | 319.459 | 4.006%
7895 | 23-61.5 | -61.4326 | 23.1405 | 535.6656 | 173.5434 | 200.0889 | 241.5123 | 278.456 | 321.0518 | 4.068%
7896 | 23-61.5 | -61.7039 | 23.1405 | 537.6576 | 174.1096 | 200.8112 | 242.4955 | 279.6868 | 322.583 | 4.126%
7897 | 23-62 | -61.9752 | 23.1405 | 540.221 | 174.6174 | 201.4605 | 243.3811 | 280.7969 | 323.9658 | 4.178%
7898 | 23-62 | -62.2465 | 23.1405 | 543.3477 | 175.1208 | 202.1181 | 244.2985 | 281.9628 | 325.4349 | 4.228%
7899 | 23-62.5 | -62.5179 | 23.1405 | 547.0279 | 175.5816 | 202.7258 | 245.1541 | 283.0561 | 326.8189 | 4.273%
7900 | 23-63 | -62.7892 | 23.1405 | 551.2506 | 175.9886 | 203.2621 | 245.9085 | 284.0195 | 328.0379 | 4.314%
7901 | 23-63 | -63.0605 | 23.1405 | 556.0034 | 176.3868 | 203.7889 | 246.6528 | 284.9724 | 329.2461 | 4.353%
7902 | 23-63.5 | -63.3318 | 23.1405 | 561.2729 | 176.7434 | 204.2579 | 247.3115 | 285.8129 | 330.3088 | 4.389%
7903 | 23-63.5 | -63.6031 | 23.1405 | 567.0446 | 177.0627 | 204.674 | 247.8904 | 286.5475 | 331.2334 | 4.422%
7904 | 23-64 | -63.8745 | 23.1405 | 573.3033 | 177.3889 | 205.1003 | 248.4854 | 287.304 | 332.1872 | 4.455%
7905 | 23-64 | -64.1458 | 23.1405 | 580.0333 | 177.6827 | 205.48 | 249.0094 | 287.9658 | 333.0168 | 4.485%
7906 | 23-64.5 | -64.4171 | 23.1405 | 587.2183 | 177.9524 | 205.8237 | 249.477 | 288.5509 | 333.745 | 4.514%
7907 | 23-64.5 | -64.6884 | 23.1405 | 594.8418 | 178.2383 | 206.1867 | 249.9686 | 289.1648 | 334.5073 | 4.545%
7908 | 23-65 | -64.9598 | 23.1405 | 602.8873 | 178.487 | 206.4904 | 250.3626 | 289.6432 | 335.087 | 4.573%
7909 | 23-65 | -65.2311 | 23.1405 | 611.3379 | 178.716 | 206.7615 | 250.7013 | 290.0439 | 335.5607 | 4.6%
7910 | 23-65.5 | -65.5024 | 23.1405 | 620.1772 | 178.9697 | 207.0648 | 251.0847 | 290.5013 | 336.106 | 4.63%
7911 | 23-66 | -65.7737 | 23.1405 | 629.3887 | 179.179 | 207.2997 | 251.358 | 290.8073 | 336.4484 | 4.657%
7912 | 23-66 | -66.045 | 23.1405 | 638.9563 | 179.3599 | 207.4935 | 251.5684 | 291.0293 | 336.6805 | 4.681%
7913 | 23-66.5 | -66.3164 | 23.1405 | 648.8642 | 179.5473 | 207.701 | 251.805 | 291.2901 | 336.9673 | 4.706%
7914 | 23-66.5 | -66.5877 | 23.1405 | 659.0971 | 179.7064 | 207.8756 | 252.0018 | 291.5047 | 337.2007 | 4.727%
7915 | 23-67 | -66.859 | 23.1405 | 669.64 | 179.861 | 208.0538 | 252.2171 | 291.7532 | 337.4877 | 4.746%
7916 | 23-67 | -67.1303 | 23.1405 | 680.4785 | 180.0327 | 208.2668 | 252.4985 | 292.0993 | 337.912 | 4.766%
7917 | 23-67.5 | -67.4016 | 23.1405 | 691.5987 | 180.1528 | 208.4172 | 252.6994 | 292.3482 | 338.2192 | 4.779%
7918 | 23-67.5 | -67.673 | 23.1405 | 702.9871 | 180.2501 | 208.5499 | 252.8929 | 292.6009 | 338.545 | 4.789%
7919 | 23-68 | -67.9443 | 23.1405 | 714.631 | 180.3478 | 208.7004 | 253.1357 | 292.9349 | 338.9933 | 4.796%
7920 | 23-68 | -68.2156 | 23.1405 | 726.5181 | 180.3843 | 208.7738 | 253.275 | 293.1404 | 339.2827 | 4.796%
7921 | 23-68.5 | -68.4869 | 23.1405 | 738.6364 | 180.4076 | 208.8395 | 253.417 | 293.3596 | 339.6001 | 4.794%
7922 | 23-69 | -68.7583 | 23.1405 | 750.9749 | 180.4409 | 208.9315 | 253.6151 | 293.6647 | 340.0414 | 4.79%
7923 | 23-69 | -69.0296 | 23.1405 | 763.5228 | 180.4198 | 208.9537 | 253.717 | 293.8488 | 340.3313 | 4.781%
7924 | 23-69.5 | -69.3009 | 23.1405 | 776.27 | 180.4091 | 208.9996 | 253.8666 | 294.1046 | 340.7233 | 4.772%
7925 | 23-69.5 | -69.5722 | 23.1405 | 789.2067 | 180.4316 | 209.1027 | 254.116 | 294.5026 | 341.3112 | 4.764%
7926 | 23-70 | -69.8435 | 23.1405 | 802.3238 | 180.4138 | 209.1604 | 254.3121 | 294.8404 | 341.831 | 4.752%
7927 | 23-70 | -70.1149 | 23.1405 | 815.6124 | 180.3906 | 209.219 | 254.5208 | 295.2032 | 342.3916 | 4.738%
7928 | 23-70.5 | -70.3862 | 23.1405 | 829.0644 | 180.3673 | 209.2852 | 254.7513 | 295.6022 | 343.0074 | 4.723%
7929 | 23-70.5 | -70.6575 | 23.1405 | 842.6719 | 180.271 | 209.2435 | 254.8133 | 295.7729 | 343.3199 | 4.702%
7930 | 23-71 | -70.9288 | 23.1405 | 856.4275 | 180.1709 | 209.1916 | 254.8532 | 295.9096 | 343.5833 | 4.681%
7931 | 23-71 | -71.2001 | 23.1405 | 870.324 | 180.0735 | 209.1369 | 254.8803 | 296.0232 | 343.8102 | 4.662%
7932 | 23-71.5 | -71.4715 | 23.1405 | 884.3548 | 179.923 | 208.992 | 254.7516 | 295.9154 | 343.7333 | 4.641%
7933 | 23-71.5 | -71.7428 | 23.1405 | 898.5135 | 179.7797 | 208.8512 | 254.621 | 295.7996 | 343.6403 | 4.621%
7934 | 23-72 | -72.0141 | 23.1405 | 912.7943 | 179.6481 | 208.7199 | 254.4954 | 295.6837 | 343.5404 | 4.602%
7935 | 23-72.5 | -72.2854 | 23.1405 | 927.1914 | 179.5214 | 208.5736 | 254.3185 | 295.4793 | 343.304 | 4.587%
7936 | 23-72.5 | -72.5568 | 23.1405 | 941.6994 | 179.4619 | 208.508 | 254.244 | 295.3975 | 343.2142 | 4.58%
7937 | 23-73 | -72.8281 | 23.1405 | 956.3133 | 179.4413 | 208.4848 | 254.2167 | 295.3663 | 343.1785 | 4.577%
7938 | 23-73 | -73.0994 | 23.1405 | 971.0282 | 179.3336 | 208.3304 | 253.9811 | 295.0509 | 342.7634 | 4.568%
7939 | 23-73.5 | -73.3707 | 23.1405 | 985.8397 | 179.2129 | 208.1503 | 253.697 | 294.6642 | 342.2482 | 4.559%
7940 | 23-73.5 | -73.642 | 23.1405 | 1000.7432 | 179.0724 | 207.9348 | 253.3501 | 294.1874 | 341.6086 | 4.549%
7941 | 23-74 | -73.9134 | 23.1405 | 1015.7349 | 178.8957 | 207.6577 | 252.8966 | 293.5587 | 340.7603 | 4.536%
7942 | 23-74 | -74.1847 | 23.1405 | 1030.8107 | 178.7571 | 207.4378 | 252.5338 | 293.0543 | 340.0779 | 4.527%
7943 | 23-74.5 | -74.456 | 23.1405 | 1045.9671 | 178.6353 | 207.2445 | 252.2147 | 292.6105 | 339.4776 | 4.519%
7944 | 23-74.5 | -74.7273 | 23.1405 | 1061.2004 | 178.4927 | 207.021 | 251.8494 | 292.1049 | 338.796 | 4.509%
7945 | 23-75 | -74.9986 | 23.1405 | 1076.5075 | 178.3835 | 206.8535 | 251.5802 | 291.735 | 338.3004 | 4.501%
7946 | 23-75.5 | -75.27 | 23.1405 | 1091.8852 | 178.2297 | 206.6328 | 251.2436 | 291.285 | 337.7093 | 4.488%
7947 | 23-75.5 | -75.5413 | 23.1405 | 1107.3305 | 177.8855 | 206.1716 | 250.5633 | 290.3917 | 336.5527 | 4.456%
7948 | 23-76 | -75.8126 | 23.1405 | 1122.8405 | 177.3348 | 205.4973 | 249.6019 | 289.154 | 334.9758 | 4.403%
7949 | 23-76 | -76.0839 | 23.1405 | 1138.4127 | 176.6106 | 204.6472 | 248.4004 | 287.6147 | 333.0227 | 4.332%
7950 | 23-76.5 | -76.3553 | 23.1405 | 1154.0443 | 175.8065 | 203.72 | 247.0818 | 285.9195 | 330.8653 | 4.255%
7951 | 23-76.5 | -76.6266 | 23.1405 | 1169.7331 | 175.032 | 202.8944 | 245.9116 | 284.4178 | 328.9574 | 4.182%
7952 | 23-77 | -76.8979 | 23.1405 | 1185.4767 | 174.3546 | 202.1914 | 244.91 | 283.1291 | 327.3164 | 4.118%
7953 | 23-77 | -77.1692 | 23.1405 | 1201.2729 | 173.8593 | 201.6465 | 244.1212 | 282.1045 | 326.0017 | 4.073%
7954 | 23-77.5 | -77.4405 | 23.1405 | 1217.1196 | 173.5402 | 201.296 | 243.6075 | 281.4327 | 325.1351 | 4.044%
7955 | 23-77.5 | -77.7119 | 23.1405 | 1233.0148 | 173.3091 | 201.0059 | 243.1654 | 280.8423 | 324.3608 | 4.025%
7956 | 23-78 | -77.9832 | 23.1405 | 1248.9567 | 173.0921 | 200.6816 | 242.6548 | 280.149 | 323.4403 | 4.008%
7957 | 23-78.5 | -78.2545 | 23.1405 | 1264.9434 | 172.893 | 200.3914 | 242.1878 | 279.5083 | 322.5831 | 3.993%
7958 | 23-78.5 | -78.5258 | 23.1405 | 1280.9732 | 172.6769 | 200.0942 | 241.6979 | 278.8287 | 321.6667 | 3.978%
7959 | 23-79 | -78.7971 | 23.1405 | 1297.0446 | 172.5238 | 199.8688 | 241.298 | 278.2556 | 320.8765 | 3.969%
7960 | 23-79 | -79.0685 | 23.1405 | 1313.1558 | 172.5864 | 199.9096 | 241.2783 | 278.1727 | 320.7114 | 3.98%
7961 | 23-79.5 | -79.3398 | 23.1405 | 1329.3054 | 172.8398 | 200.1427 | 241.5159 | 278.4081 | 320.9383 | 4.011%
7962 | 23-79.5 | -79.6111 | 23.1405 | 1345.4921 | 173.2242 | 200.4865 | 241.895 | 278.814 | 321.3698 | 4.055%
7963 | 23-80 | -79.8824 | 23.1405 | 1361.7144 | 173.6854 | 200.8899 | 242.3594 | 279.3299 | 321.9423 | 4.106%
7964 | 23-80 | -80.1537 | 23.1405 | 1377.971 | 174.2684 | 201.3737 | 242.9236 | 279.9631 | 322.6525 | 4.172%
7965 | 23-80.5 | -80.4251 | 23.1405 | 1394.2607 | 174.9117 | 201.9315 | 243.58 | 280.7052 | 323.4912 | 4.245%
7966 | 23-80.5 | -80.6964 | 23.1405 | 1410.5824 | 175.5426 | 202.5443 | 244.3091 | 281.5366 | 324.4391 | 4.318%
7967 | 23-81 | -80.9677 | 23.1405 | 1426.9348 | 176.0056 | 202.9713 | 244.7718 | 282.024 | 324.9478 | 4.377%
7968 | 23-81 | -81.239 | 23.1405 | 1443.3168 | 176.3214 | 203.2574 | 245.0461 | 282.2783 | 325.1697 | 4.42%
7969 | 23-81.5 | -81.5104 | 23.1405 | 1459.7276 | 176.5896 | 203.5336 | 245.3271 | 282.5568 | 325.4385 | 4.457%
7970 | 23-82 | -81.7817 | 23.1405 | 1476.1659 | 176.8462 | 203.7816 | 245.5698 | 282.7873 | 325.6475 | 4.493%
7971 | 23-82 | -82.053 | 23.1405 | 1492.631 | 177.1271 | 204.0385 | 245.8271 | 283.0379 | 325.8835 | 4.532%
7972 | 23-82.5 | -82.3243 | 23.1405 | 1509.1218 | 177.4341 | 204.3379 | 246.1508 | 283.3784 | 326.2384 | 4.573%
7973 | 23-82.5 | -82.5956 | 23.1405 | 1525.6375 | 177.7846 | 204.7011 | 246.5622 | 283.8293 | 326.731 | 4.619%
7974 | 23-83 | -82.867 | 23.1405 | 1542.1773 | 178.2327 | 205.2069 | 247.1882 | 284.5641 | 327.5932 | 4.675%
7975 | 23-83 | -83.1383 | 23.1405 | 1558.7403 | 178.8076 | 205.9019 | 248.1058 | 285.6907 | 328.9709 | 4.742%
7976 | 23-83.5 | -83.4096 | 23.1405 | 1575.3258 | 179.3232 | 206.5455 | 248.9767 | 286.7766 | 330.3171 | 4.801%
7977 | 23-83.5 | -83.6809 | 23.1405 | 1591.933 | 179.7298 | 207.0827 | 249.7342 | 287.7452 | 331.5437 | 4.844%
7978 | 23-84 | -83.9522 | 23.1405 | 1608.5613 | 180.0228 | 207.4997 | 250.364 | 288.5819 | 332.6363 | 4.871%
7979 | 23-84 | -84.2236 | 23.1405 | 1625.2098 | 180.1267 | 207.6943 | 250.719 | 289.0963 | 333.3508 | 4.874%
7980 | 23-84.5 | -84.4949 | 23.1405 | 1641.878 | 180.2186 | 207.8983 | 251.1222 | 289.6988 | 334.2048 | 4.871%
7981 | 23-85 | -84.7662 | 23.1405 | 1658.5652 | 180.3661 | 208.1997 | 251.6965 | 290.5456 | 335.395 | 4.871%
7982 | 23-85 | -85.0375 | 23.1405 | 1675.2708 | 180.4675 | 208.4495 | 252.2112 | 291.3258 | 336.5108 | 4.865%
7983 | 23-85.5 | -85.3089 | 23.1405 | 1691.9943 | 180.5234 | 208.6591 | 252.6971 | 292.0901 | 337.6282 | 4.852%
7984 | 23-85.5 | -85.5802 | 23.1405 | 1708.7349 | 180.5301 | 208.8281 | 253.1597 | 292.8504 | 338.7677 | 4.83%
7985 | 23-86 | -85.8515 | 23.1405 | 1725.4923 | 180.4112 | 208.8451 | 253.4275 | 293.376 | 339.6251 | 4.794%
7986 | 23-86 | -86.1228 | 23.1405 | 1742.2659 | 180.143 | 208.6849 | 253.4738 | 293.64 | 340.1739 | 4.74%
7987 | 23-86.5 | -86.3941 | 23.1405 | 1759.0552 | 179.7115 | 208.3299 | 253.2752 | 293.6139 | 340.3799 | 4.668%
7988 | 23-86.5 | -86.6655 | 23.1405 | 1775.8596 | 179.0459 | 207.6806 | 252.6827 | 293.0997 | 339.9843 | 4.572%
7989 | 23-87 | -86.9368 | 23.1405 | 1792.6787 | 178.3174 | 206.9736 | 252.032 | 292.5291 | 339.5359 | 4.471%
7990 | 23-87 | -87.2081 | 23.1405 | 1809.5121 | 177.537 | 206.221 | 251.3368 | 291.9166 | 339.051 | 4.366%
7991 | 23-87.5 | -87.4794 | 23.1405 | 1826.3593 | 176.6323 | 205.3089 | 250.4052 | 290.9926 | 338.1615 | 4.252%
7992 | 23-88 | -87.7507 | 23.1405 | 1843.2199 | 175.6615 | 204.3339 | 249.3811 | 289.9476 | 337.1154 | 4.137%
7993 | 23-88 | -88.0221 | 23.1405 | 1860.0935 | 174.615 | 203.29 | 248.2549 | 288.768 | 335.8947 | 4.018%
7994 | 23-88.5 | -88.2934 | 23.1405 | 1876.9797 | 173.4473 | 202.118 | 246.9252 | 287.3106 | 334.3033 | 3.893%
7995 | 23-88.5 | -88.5647 | 23.1405 | 1893.8781 | 172.2523 | 200.9563 | 245.609 | 285.8697 | 332.7318 | 3.771%
7996 | 23-89 | -88.836 | 23.1405 | 1910.7883 | 171.0216 | 199.7865 | 244.272 | 284.395 | 331.1101 | 3.65%
7997 | 23-89 | -89.1074 | 23.1405 | 1927.71 | 169.7119 | 198.5464 | 242.7987 | 282.7173 | 329.2006 | 3.528%
7998 | 23-89.5 | -89.3787 | 23.1405 | 1944.6429 | 168.4026 | 197.3401 | 241.3529 | 281.0597 | 327.3004 | 3.411%
7999 | 23-89.5 | -89.65 | 23.1405 | 1961.5865 | 167.0833 | 196.1449 | 239.8978 | 279.371 | 325.3405 | 3.299%
8000 | 23-90 | -89.9213 | 23.1405 | 1978.5406 | 165.7202 | 194.9164 | 238.3555 | 277.5399 | 323.1675 | 3.188%
8001 | 23-90 | -90.1926 | 23.1405 | 1995.5049 | 164.3881 | 193.7453 | 236.8631 | 275.7492 | 321.0209 | 3.085%
8002 | 23-90.5 | -90.464 | 23.1405 | 2012.479 | 163.0758 | 192.6077 | 235.3904 | 273.9626 | 318.857 | 2.987%
8003 | 23-90.5 | -90.7353 | 23.1405 | 2029.4627 | 161.7437 | 191.4737 | 233.9061 | 272.1483 | 316.6445 | 2.891%
8004 | 23-50 | -50.0371 | 23.4119 | 883.6083 | 119.1815 | 157.3293 | 193.5376 | 220.8811 | 252.0893 | 0.9625%
8005 | 23-50.5 | -50.3084 | 23.4119 | 869.8929 | 120.8911 | 159.4491 | 194.9932 | 222.5799 | 254.0709 | 1.011%
8006 | 23-50.5 | -50.5797 | 23.4119 | 856.3215 | 122.5341 | 161.4097 | 196.3686 | 224.1855 | 255.9442 | 1.06%
8007 | 23-51 | -50.851 | 23.4119 | 842.901 | 124.1262 | 163.2225 | 197.6893 | 225.7381 | 257.7679 | 1.11%
8008 | 23-51 | -51.1224 | 23.4119 | 829.6387 | 125.6971 | 164.9061 | 198.9936 | 227.2919 | 259.6157 | 1.16%
8009 | 23-51.5 | -51.3937 | 23.4119 | 816.5425 | 127.1903 | 166.4035 | 200.2203 | 228.7607 | 261.3709 | 1.21%
8010 | 23-51.5 | -51.665 | 23.4119 | 803.6203 | 128.6464 | 167.7679 | 201.4262 | 230.2271 | 263.1477 | 1.26%
8011 | 23-52 | -51.9363 | 23.4119 | 790.8809 | 130.101 | 169.0336 | 202.6583 | 231.7565 | 265.0349 | 1.311%
8012 | 23-52 | -52.2077 | 23.4119 | 778.3331 | 131.4935 | 170.1483 | 203.8303 | 233.2163 | 266.8413 | 1.361%
8013 | 23-52.5 | -52.479 | 23.4119 | 765.9866 | 132.8902 | 171.1994 | 205.0255 | 234.7183 | 268.7142 | 1.413%
8014 | 23-53 | -52.7503 | 23.4119 | 753.8511 | 134.3339 | 172.2347 | 206.2955 | 236.331 | 270.7426 | 1.468%
8015 | 23-53 | -53.0216 | 23.4119 | 741.9371 | 135.7324 | 173.1844 | 207.5257 | 237.8931 | 272.7077 | 1.523%
8016 | 23-53.5 | -53.2929 | 23.4119 | 730.2554 | 137.1689 | 174.1388 | 208.8123 | 239.5361 | 274.7839 | 1.581%
8017 | 23-53.5 | -53.5643 | 23.4119 | 718.8174 | 138.6841 | 175.1354 | 210.2007 | 241.3202 | 277.0505 | 1.644%
8018 | 23-54 | -53.8356 | 23.4119 | 707.635 | 140.181 | 176.1037 | 211.5741 | 243.0834 | 279.2888 | 1.708%
8019 | 23-54 | -54.1069 | 23.4119 | 696.7204 | 141.7361 | 177.1135 | 213.01 | 244.9265 | 281.6285 | 1.778%
8020 | 23-54.5 | -54.3782 | 23.4119 | 686.0865 | 143.3716 | 178.1831 | 214.5273 | 246.8719 | 284.0963 | 1.853%
8021 | 23-54.5 | -54.6495 | 23.4119 | 675.7467 | 144.9601 | 179.2212 | 215.9793 | 248.7188 | 286.4237 | 1.929%
8022 | 23-55 | -54.9209 | 23.4119 | 665.7145 | 146.5657 | 180.27 | 217.4315 | 250.5547 | 288.7263 | 2.009%
8023 | 23-55 | -55.1922 | 23.4119 | 656.0041 | 148.1936 | 181.3314 | 218.8837 | 252.3779 | 290.9995 | 2.092%
8024 | 23-55.5 | -55.4635 | 23.4119 | 646.6301 | 149.7302 | 182.3145 | 220.1823 | 253.9726 | 292.9503 | 2.175%
8025 | 23-55.5 | -55.7348 | 23.4119 | 637.6073 | 151.2413 | 183.2655 | 221.4188 | 255.4754 | 294.7718 | 2.258%
8026 | 23-56 | -56.0061 | 23.4119 | 628.9509 | 152.7231 | 184.1856 | 222.5966 | 256.8919 | 296.4724 | 2.344%
8027 | 23-56.5 | -56.2775 | 23.4119 | 620.6762 | 154.117 | 185.0316 | 223.6452 | 258.1247 | 297.9211 | 2.427%
8028 | 23-56.5 | -56.5488 | 23.4119 | 612.7987 | 155.5168 | 185.8772 | 224.6814 | 259.3329 | 299.3298 | 2.514%
8029 | 23-57 | -56.8201 | 23.4119 | 605.3339 | 156.9001 | 186.7127 | 225.6885 | 260.4929 | 300.6658 | 2.604%
8030 | 23-57 | -57.0914 | 23.4119 | 598.2973 | 158.1817 | 187.4706 | 226.5593 | 261.4584 | 301.7347 | 2.69%
8031 | 23-57.5 | -57.3628 | 23.4119 | 591.7041 | 159.4564 | 188.2282 | 227.4168 | 262.3975 | 302.7602 | 2.78%
8032 | 23-57.5 | -57.6341 | 23.4119 | 585.5695 | 160.6968 | 188.9759 | 228.2474 | 263.2925 | 303.7198 | 2.872%
8033 | 23-58 | -57.9054 | 23.4119 | 579.9079 | 161.838 | 189.6726 | 228.9931 | 264.069 | 304.5191 | 2.96%
8034 | 23-58 | -58.1767 | 23.4119 | 574.7333 | 162.9805 | 190.4161 | 229.8089 | 264.9384 | 305.4392 | 3.052%
8035 | 23-58.5 | -58.448 | 23.4119 | 570.0591 | 164.0891 | 191.1814 | 230.6571 | 265.8502 | 306.4141 | 3.145%
8036 | 23-58.5 | -58.7194 | 23.4119 | 565.8976 | 165.1066 | 191.9025 | 231.4345 | 266.6653 | 307.26 | 3.235%
8037 | 23-59 | -58.9907 | 23.4119 | 562.2602 | 166.1336 | 192.675 | 232.3008 | 267.6063 | 308.2784 | 3.328%
8038 | 23-59.5 | -59.262 | 23.4119 | 559.1572 | 167.1355 | 193.475 | 233.2199 | 268.6255 | 309.4067 | 3.421%
8039 | 23-59.5 | -59.5333 | 23.4119 | 556.5974 | 168.0702 | 194.2559 | 234.1229 | 269.6322 | 310.5276 | 3.511%
8040 | 23-60 | -59.8046 | 23.4119 | 554.5885 | 168.9845 | 195.069 | 235.0901 | 270.7349 | 311.7846 | 3.601%
8041 | 23-60 | -60.076 | 23.4119 | 553.1365 | 169.8454 | 195.8868 | 236.0817 | 271.8819 | 313.1115 | 3.687%
8042 | 23-60.5 | -60.3473 | 23.4119 | 552.2457 | 170.6263 | 196.6727 | 237.0448 | 273.005 | 314.4209 | 3.767%
8043 | 23-60.5 | -60.6186 | 23.4119 | 551.9188 | 171.3964 | 197.4979 | 238.0892 | 274.2515 | 315.9068 | 3.847%
8044 | 23-61 | -60.8899 | 23.4119 | 552.1569 | 172.1204 | 198.3235 | 239.1562 | 275.543 | 317.4665 | 3.921%
8045 | 23-61 | -61.1613 | 23.4119 | 552.9592 | 172.7757 | 199.1142 | 240.1931 | 276.8105 | 319.0109 | 3.99%
8046 | 23-61.5 | -61.4326 | 23.4119 | 554.3233 | 173.417 | 199.9212 | 241.2749 | 278.1519 | 320.666 | 4.056%
8047 | 23-61.5 | -61.7039 | 23.4119 | 556.2451 | 174.0207 | 200.6866 | 242.3099 | 279.4422 | 322.2657 | 4.118%
8048 | 23-62 | -61.9752 | 23.4119 | 558.7187 | 174.5664 | 201.3803 | 243.2501 | 280.6162 | 323.7232 | 4.174%
8049 | 23-62 | -62.2465 | 23.4119 | 561.7369 | 175.1093 | 202.0854 | 244.228 | 281.8545 | 325.279 | 4.229%
8050 | 23-62.5 | -62.5179 | 23.4119 | 565.291 | 175.6103 | 202.7418 | 245.1462 | 283.0233 | 326.7538 | 4.279%
8051 | 23-63 | -62.7892 | 23.4119 | 569.3708 | 176.0574 | 203.3266 | 245.9629 | 284.0618 | 328.063 | 4.324%
8052 | 23-63 | -63.0605 | 23.4119 | 573.9653 | 176.4952 | 203.9017 | 246.7696 | 285.0903 | 329.3626 | 4.368%
8053 | 23-63.5 | -63.3318 | 23.4119 | 579.0621 | 176.8897 | 204.4175 | 247.4896 | 286.0056 | 330.5164 | 4.408%
8054 | 23-63.5 | -63.6031 | 23.4119 | 584.648 | 177.2442 | 204.8772 | 248.1261 | 286.8108 | 331.5273 | 4.444%
8055 | 23-64 | -63.8745 | 23.4119 | 590.7093 | 177.6024 | 205.3429 | 248.7728 | 287.6305 | 332.558 | 4.481%
8056 | 23-64 | -64.1458 | 23.4119 | 597.2313 | 177.9243 | 205.757 | 249.3414 | 288.3463 | 333.4532 | 4.515%
8057 | 23-64.5 | -64.4171 | 23.4119 | 604.1992 | 178.2185 | 206.1308 | 249.8479 | 288.9789 | 334.2388 | 4.546%
8058 | 23-64.5 | -64.6884 | 23.4119 | 611.5978 | 178.5267 | 206.5214 | 250.3762 | 289.6379 | 335.0564 | 4.58%
8059 | 23-65 | -64.9598 | 23.4119 | 619.4115 | 178.7944 | 206.8488 | 250.8016 | 290.155 | 335.6835 | 4.61%
8060 | 23-65 | -65.2311 | 23.4119 | 627.6248 | 179.0402 | 207.1405 | 251.167 | 290.5882 | 336.1968 | 4.639%
8061 | 23-65.5 | -65.5024 | 23.4119 | 636.2222 | 179.3098 | 207.4629 | 251.5748 | 291.0747 | 336.7769 | 4.671%
8062 | 23-66 | -65.7737 | 23.4119 | 645.1884 | 179.5324 | 207.7119 | 251.8632 | 291.3966 | 337.1357 | 4.7%
8063 | 23-66 | -66.045 | 23.4119 | 654.5082 | 179.7245 | 207.9158 | 252.0811 | 291.623 | 337.3681 | 4.726%
8064 | 23-66.5 | -66.3164 | 23.4119 | 664.1667 | 179.9218 | 208.1306 | 252.3201 | 291.8809 | 337.6449 | 4.753%
8065 | 23-66.5 | -66.5877 | 23.4119 | 674.1493 | 180.087 | 208.3072 | 252.5108 | 292.0812 | 337.8531 | 4.776%
8066 | 23-67 | -66.859 | 23.4119 | 684.4417 | 180.2446 | 208.4823 | 252.7118 | 292.3039 | 338.0995 | 4.797%
8067 | 23-67 | -67.1303 | 23.4119 | 695.0303 | 180.4171 | 208.6882 | 252.9719 | 292.6141 | 338.4693 | 4.818%
8068 | 23-67.5 | -67.4016 | 23.4119 | 705.9016 | 180.5365 | 208.8296 | 253.1488 | 292.8236 | 338.7175 | 4.832%
8069 | 23-67.5 | -67.673 | 23.4119 | 717.0427 | 180.6333 | 208.9536 | 253.3184 | 293.0369 | 338.9843 | 4.843%
8070 | 23-68 | -67.9443 | 23.4119 | 728.4414 | 180.7311 | 209.0959 | 253.538 | 293.3324 | 339.3744 | 4.851%
8071 | 23-68 | -68.2156 | 23.4119 | 740.0855 | 180.7668 | 209.1595 | 253.6512 | 293.4952 | 339.5997 | 4.853%
8072 | 23-68.5 | -68.4869 | 23.4119 | 751.9637 | 180.79 | 209.2162 | 253.768 | 293.6726 | 339.8541 | 4.851%
8073 | 23-69 | -68.7583 | 23.4119 | 764.0651 | 180.8246 | 209.3012 | 253.9436 | 293.9396 | 340.2372 | 4.849%
8074 | 23-69 | -69.0296 | 23.4119 | 776.3792 | 180.8044 | 209.3152 | 254.0209 | 294.0821 | 340.4637 | 4.841%
8075 | 23-69.5 | -69.3009 | 23.4119 | 788.8959 | 180.796 | 209.3554 | 254.1499 | 294.3021 | 340.8004 | 4.833%
8076 | 23-69.5 | -69.5722 | 23.4119 | 801.6059 | 180.8231 | 209.4565 | 254.3851 | 294.6731 | 341.3446 | 4.827%
8077 | 23-70 | -69.8435 | 23.4119 | 814.4999 | 180.8135 | 209.5192 | 254.5799 | 295.0031 | 341.8479 | 4.816%
8078 | 23-70 | -70.1149 | 23.4119 | 827.5693 | 180.8051 | 209.5931 | 254.8043 | 295.3812 | 342.4232 | 4.803%
8079 | 23-70.5 | -70.3862 | 23.4119 | 840.8061 | 180.804 | 209.6857 | 255.0678 | 295.8193 | 343.0851 | 4.79%
8080 | 23-70.5 | -70.6575 | 23.4119 | 854.2022 | 180.7348 | 209.678 | 255.1752 | 296.0462 | 343.467 | 4.772%
8081 | 23-71 | -70.9288 | 23.4119 | 867.7504 | 180.6662 | 209.6658 | 255.2686 | 296.2494 | 343.8125 | 4.755%
8082 | 23-71 | -71.2001 | 23.4119 | 881.4435 | 180.6044 | 209.6557 | 255.3551 | 296.4365 | 344.13 | 4.739%
8083 | 23-71.5 | -71.4715 | 23.4119 | 895.2749 | 180.4907 | 209.5564 | 255.2866 | 296.4028 | 344.144 | 4.721%
8084 | 23-71.5 | -71.7428 | 23.4119 | 909.2383 | 180.3863 | 209.4636 | 255.2194 | 296.3647 | 344.146 | 4.705%
8085 | 23-72 | -72.0141 | 23.4119 | 923.3276 | 180.295 | 209.3822 | 255.1594 | 296.3294 | 344.1446 | 4.691%
8086 | 23-72.5 | -72.2854 | 23.4119 | 937.5371 | 180.2074 | 209.2858 | 255.0506 | 296.2104 | 344.0149 | 4.679%
8087 | 23-72.5 | -72.5568 | 23.4119 | 951.8614 | 180.1876 | 209.273 | 255.0511 | 296.2251 | 344.048 | 4.676%
8088 | 23-73 | -72.8281 | 23.4119 | 966.2954 | 180.2064 | 209.3038 | 255.1027 | 296.2971 | 344.1457 | 4.677%
8089 | 23-73 | -73.0994 | 23.4119 | 980.8341 | 180.1339 | 209.198 | 254.939 | 296.0762 | 343.8532 | 4.671%
8090 | 23-73.5 | -73.3707 | 23.4119 | 995.473 | 180.0431 | 209.058 | 254.7125 | 295.7641 | 343.4338 | 4.665%
8091 | 23-73.5 | -73.642 | 23.4119 | 1010.2076 | 179.9291 | 208.8768 | 254.4131 | 295.3474 | 342.8697 | 4.657%
8092 | 23-74 | -73.9134 | 23.4119 | 1025.0338 | 179.782 | 208.6367 | 254.0093 | 294.7806 | 342.0979 | 4.648%
8093 | 23-74 | -74.1847 | 23.4119 | 1039.9477 | 179.678 | 208.4599 | 253.7035 | 294.3464 | 341.5017 | 4.643%
8094 | 23-74.5 | -74.456 | 23.4119 | 1054.9454 | 179.5923 | 208.3107 | 253.4418 | 293.9724 | 340.9862 | 4.639%
8095 | 23-74.5 | -74.7273 | 23.4119 | 1070.0234 | 179.4798 | 208.1224 | 253.1199 | 293.5176 | 340.3643 | 4.632%
8096 | 23-75 | -74.9986 | 23.4119 | 1085.1784 | 179.3973 | 207.9845 | 252.8843 | 293.1851 | 339.9099 | 4.628%
8097 | 23-75.5 | -75.27 | 23.4119 | 1100.4071 | 179.2694 | 207.792 | 252.5793 | 292.7692 | 339.3557 | 4.618%
8098 | 23-75.5 | -75.5413 | 23.4119 | 1115.7065 | 178.9637 | 207.3663 | 251.9411 | 291.9239 | 338.254 | 4.59%
8099 | 23-76 | -75.8126 | 23.4119 | 1131.0736 | 178.4669 | 206.7353 | 251.0308 | 290.744 | 336.7424 | 4.542%
8100 | 23-76 | -76.0839 | 23.4119 | 1146.5057 | 177.8085 | 205.9337 | 249.8852 | 289.2671 | 334.8589 | 4.478%
8101 | 23-76.5 | -76.3553 | 23.4119 | 1162.0002 | 177.0795 | 205.0576 | 248.6248 | 287.6358 | 332.7717 | 4.407%
8102 | 23-76.5 | -76.6266 | 23.4119 | 1177.5545 | 176.3907 | 204.2921 | 247.526 | 286.2156 | 330.9566 | 4.341%
8103 | 23-77 | -76.8979 | 23.4119 | 1193.1663 | 175.8006 | 203.6512 | 246.601 | 285.0165 | 329.4206 | 4.285%
8104 | 23-77 | -77.1692 | 23.4119 | 1208.8333 | 175.3815 | 203.1602 | 245.8803 | 284.0733 | 328.2032 | 4.247%
8105 | 23-77.5 | -77.4405 | 23.4119 | 1224.5534 | 175.1195 | 202.8464 | 245.4139 | 283.4588 | 327.4056 | 4.223%
8106 | 23-77.5 | -77.7119 | 23.4119 | 1240.3245 | 174.9056 | 202.5627 | 244.9807 | 282.8796 | 326.6454 | 4.205%
8107 | 23-78 | -77.9832 | 23.4119 | 1256.1446 | 174.6615 | 202.2063 | 244.4304 | 282.1396 | 325.67 | 4.185%
8108 | 23-78.5 | -78.2545 | 23.4119 | 1272.0118 | 174.4101 | 201.8558 | 243.8904 | 281.4146 | 324.7156 | 4.164%
8109 | 23-78.5 | -78.5258 | 23.4119 | 1287.9245 | 174.1264 | 201.4822 | 243.3107 | 280.6335 | 323.6845 | 4.14%
8110 | 23-79 | -78.7971 | 23.4119 | 1303.8808 | 173.8944 | 201.1684 | 242.8083 | 279.9461 | 322.7668 | 4.122%
8111 | 23-79 | -79.0685 | 23.4119 | 1319.8792 | 173.8534 | 201.1004 | 242.6608 | 279.7187 | 322.4385 | 4.122%
8112 | 23-79.5 | -79.3398 | 23.4119 | 1335.9181 | 173.9843 | 201.2116 | 242.7536 | 279.7895 | 322.4782 | 4.14%
8113 | 23-79.5 | -79.6111 | 23.4119 | 1351.996 | 174.2339 | 201.4274 | 242.9804 | 280.0215 | 322.7116 | 4.17%
8114 | 23-80 | -79.8824 | 23.4119 | 1368.1115 | 174.5513 | 201.6999 | 243.2898 | 280.3613 | 323.084 | 4.207%
8115 | 23-80 | -80.1537 | 23.4119 | 1384.2633 | 174.9779 | 202.0426 | 243.6852 | 280.8013 | 323.573 | 4.256%
8116 | 23-80.5 | -80.4251 | 23.4119 | 1400.45 | 175.4588 | 202.452 | 244.1619 | 281.3356 | 324.1713 | 4.311%
8117 | 23-80.5 | -80.6964 | 23.4119 | 1416.6704 | 175.931 | 202.9165 | 244.7095 | 281.9556 | 324.8731 | 4.368%
8118 | 23-81 | -80.9677 | 23.4119 | 1432.9234 | 176.2431 | 203.1978 | 244.9923 | 282.232 | 325.1346 | 4.409%
8119 | 23-81 | -81.239 | 23.4119 | 1449.2077 | 176.4375 | 203.3556 | 245.1078 | 282.3 | 325.1376 | 4.438%
8120 | 23-81.5 | -81.5104 | 23.4119 | 1465.5224 | 176.6217 | 203.5338 | 245.2687 | 282.4384 | 325.243 | 4.465%
8121 | 23-82 | -81.7817 | 23.4119 | 1481.8663 | 176.8194 | 203.7137 | 245.4289 | 282.5735 | 325.3419 | 4.494%
8122 | 23-82 | -82.053 | 23.4119 | 1498.2384 | 177.057 | 203.9207 | 245.626 | 282.7549 | 325.4982 | 4.528%
8123 | 23-82.5 | -82.3243 | 23.4119 | 1514.6379 | 177.3296 | 204.1803 | 245.9016 | 283.0399 | 325.789 | 4.564%
8124 | 23-82.5 | -82.5956 | 23.4119 | 1531.0637 | 177.6543 | 204.5138 | 246.2772 | 283.4493 | 326.2338 | 4.607%
8125 | 23-83 | -82.867 | 23.4119 | 1547.5151 | 178.0792 | 204.9931 | 246.8714 | 284.1479 | 327.0545 | 4.66%
8126 | 23-83 | -83.1383 | 23.4119 | 1563.991 | 178.6302 | 205.6611 | 247.7575 | 285.2389 | 328.3923 | 4.724%
8127 | 23-83.5 | -83.4096 | 23.4119 | 1580.4909 | 179.1215 | 206.2766 | 248.5942 | 286.2851 | 329.6924 | 4.78%
8128 | 23-83.5 | -83.6809 | 23.4119 | 1597.0137 | 179.5093 | 206.7923 | 249.3259 | 287.2242 | 330.8852 | 4.82%
8129 | 23-84 | -83.9522 | 23.4119 | 1613.5589 | 179.7918 | 207.1982 | 249.9442 | 288.0493 | 331.9661 | 4.846%
8130 | 23-84 | -84.2236 | 23.4119 | 1630.1256 | 179.897 | 207.396 | 250.3054 | 288.5728 | 332.6935 | 4.848%
8131 | 23-84.5 | -84.4949 | 23.4119 | 1646.7132 | 180.0004 | 207.615 | 250.7297 | 289.2021 | 333.5812 | 4.847%
8132 | 23-85 | -84.7662 | 23.4119 | 1663.3211 | 180.1683 | 207.942 | 251.3382 | 290.0912 | 334.8234 | 4.85%
8133 | 23-85 | -85.0375 | 23.4119 | 1679.9485 | 180.3045 | 208.2347 | 251.9089 | 290.9396 | 336.022 | 4.848%
8134 | 23-85.5 | -85.3089 | 23.4119 | 1696.5948 | 180.4097 | 208.5044 | 252.4725 | 291.798 | 337.2531 | 4.841%
8135 | 23-85.5 | -85.5802 | 23.4119 | 1713.2595 | 180.4799 | 208.75 | 253.0331 | 292.6759 | 338.5336 | 4.826%
8136 | 23-86 | -85.8515 | 23.4119 | 1729.942 | 180.4298 | 208.8486 | 253.4026 | 293.3218 | 339.533 | 4.799%
8137 | 23-86 | -86.1228 | 23.4119 | 1746.6417 | 180.2365 | 208.7749 | 253.5538 | 293.7071 | 340.222 | 4.754%
8138 | 23-86.5 | -86.3941 | 23.4119 | 1763.3581 | 179.8857 | 208.5112 | 253.4624 | 293.8016 | 340.5636 | 4.692%
8139 | 23-86.5 | -86.6655 | 23.4119 | 1780.0907 | 179.3041 | 207.9561 | 252.979 | 293.4094 | 340.304 | 4.606%
8140 | 23-87 | -86.9368 | 23.4119 | 1796.8389 | 178.6696 | 207.3476 | 252.4439 | 292.9688 | 340.002 | 4.515%
8141 | 23-87 | -87.2081 | 23.4119 | 1813.6023 | 177.9932 | 206.6977 | 251.8702 | 292.4943 | 339.6735 | 4.421%
8142 | 23-87.5 | -87.4794 | 23.4119 | 1830.3805 | 177.2034 | 205.8908 | 251.0647 | 291.7149 | 338.9495 | 4.319%
8143 | 23-88 | -87.7507 | 23.4119 | 1847.173 | 176.354 | 205.0212 | 250.17 | 290.8208 | 338.0797 | 4.214%
8144 | 23-88 | -88.0221 | 23.4119 | 1863.9793 | 175.432 | 204.081 | 249.174 | 289.7959 | 337.0426 | 4.105%
8145 | 23-88.5 | -88.2934 | 23.4119 | 1880.7991 | 174.3823 | 203.0022 | 247.9623 | 288.4793 | 335.6191 | 3.989%
8146 | 23-88.5 | -88.5647 | 23.4119 | 1897.6318 | 173.2927 | 201.9172 | 246.7429 | 287.1538 | 334.1851 | 3.873%
8147 | 23-89 | -88.836 | 23.4119 | 1914.4773 | 172.1563 | 200.8091 | 245.484 | 285.7723 | 332.6746 | 3.757%
8148 | 23-89 | -89.1074 | 23.4119 | 1931.335 | 170.9368 | 199.6203 | 244.0776 | 284.1763 | 330.8644 | 3.64%
8149 | 23-89.5 | -89.3787 | 23.4119 | 1948.2046 | 169.7209 | 198.4659 | 242.702 | 282.6062 | 329.0728 | 3.527%
8150 | 23-89.5 | -89.65 | 23.4119 | 1965.0858 | 168.496 | 197.3215 | 241.3179 | 281.0081 | 327.2276 | 3.418%
8151 | 23-90 | -89.9213 | 23.4119 | 1981.9781 | 167.2246 | 196.1378 | 239.8418 | 279.2641 | 325.1677 | 3.31%
8152 | 23-90 | -90.1926 | 23.4119 | 1998.8814 | 165.9832 | 195.0074 | 238.4103 | 277.5541 | 323.1264 | 3.209%
8153 | 23-90.5 | -90.464 | 23.4119 | 2015.7952 | 164.7522 | 193.9048 | 236.99 | 275.837 | 321.0533 | 3.113%
8154 | 23-90.5 | -90.7353 | 23.4119 | 2032.7192 | 163.4908 | 192.7974 | 235.5446 | 274.0736 | 318.9065 | 3.018%
8155 | 24-50 | -50.0371 | 23.6832 | 894.9474 | 117.9011 | 155.7156 | 192.3584 | 219.4499 | 250.3591 | 0.9269%
8156 | 24-50.5 | -50.3084 | 23.6832 | 881.4337 | 119.6215 | 157.9209 | 193.8397 | 221.1816 | 252.382 | 0.9745%
8157 | 24-50.5 | -50.5797 | 23.6832 | 868.0677 | 121.2765 | 159.9728 | 195.2368 | 222.8121 | 254.2838 | 1.022%
8158 | 24-51 | -50.851 | 23.6832 | 854.8562 | 122.8798 | 161.8788 | 196.5732 | 224.3802 | 256.1223 | 1.071%
8159 | 24-51 | -51.1224 | 23.6832 | 841.8066 | 124.46 | 163.6538 | 197.8865 | 225.9402 | 257.9727 | 1.12%
8160 | 24-51.5 | -51.3937 | 23.6832 | 828.9266 | 125.9605 | 165.237 | 199.1164 | 227.4075 | 259.7199 | 1.169%
8161 | 24-51.5 | -51.665 | 23.6832 | 816.2242 | 127.4189 | 166.6736 | 200.3179 | 228.8635 | 261.4788 | 1.217%
8162 | 24-52 | -51.9363 | 23.6832 | 803.7078 | 128.8687 | 167.9957 | 201.5376 | 230.3743 | 263.3391 | 1.267%
8163 | 24-52 | -52.2077 | 23.6832 | 791.3864 | 130.2495 | 169.15 | 202.6893 | 231.8058 | 265.1075 | 1.316%
8164 | 24-52.5 | -52.479 | 23.6832 | 779.2693 | 131.6287 | 170.2275 | 203.8579 | 233.2722 | 266.9335 | 1.365%
8165 | 24-53 | -52.7503 | 23.6832 | 767.366 | 133.0497 | 171.2777 | 205.0963 | 234.8433 | 268.9078 | 1.418%
8166 | 24-53 | -53.0216 | 23.6832 | 755.6868 | 134.421 | 172.2306 | 206.2944 | 236.3645 | 270.821 | 1.47%
8167 | 24-53.5 | -53.2929 | 23.6832 | 744.2423 | 135.8268 | 173.1815 | 207.5505 | 237.9699 | 272.8511 | 1.526%
8168 | 24-53.5 | -53.5643 | 23.6832 | 733.0434 | 137.3094 | 174.1691 | 208.9117 | 239.7219 | 275.0796 | 1.586%
8169 | 24-54 | -53.8356 | 23.6832 | 722.1017 | 138.7716 | 175.1211 | 210.261 | 241.4581 | 277.2877 | 1.647%
8170 | 24-54 | -54.1069 | 23.6832 | 711.429 | 140.2946 | 176.116 | 211.682 | 243.2882 | 279.6172 | 1.712%
8171 | 24-54.5 | -54.3782 | 23.6832 | 701.0376 | 141.9027 | 177.1758 | 213.1968 | 245.2388 | 282.0998 | 1.784%
8172 | 24-54.5 | -54.6495 | 23.6832 | 690.9402 | 143.4748 | 178.2135 | 214.6604 | 247.1092 | 284.4662 | 1.857%
8173 | 24-55 | -54.9209 | 23.6832 | 681.15 | 145.0761 | 179.272 | 216.1385 | 248.9874 | 286.8315 | 1.934%
8174 | 24-55 | -55.1922 | 23.6832 | 671.6804 | 146.7124 | 180.3533 | 217.6307 | 250.8705 | 289.1898 | 2.015%
8175 | 24-55.5 | -55.4635 | 23.6832 | 662.5452 | 148.264 | 181.361 | 218.9733 | 252.5284 | 291.2277 | 2.095%
8176 | 24-55.5 | -55.7348 | 23.6832 | 653.7584 | 149.7976 | 182.3408 | 220.2589 | 254.1001 | 293.1427 | 2.177%
8177 | 24-56 | -56.0061 | 23.6832 | 645.3343 | 151.3135 | 183.294 | 221.4911 | 255.5919 | 294.9445 | 2.262%
8178 | 24-56.5 | -56.2775 | 23.6832 | 637.2873 | 152.75 | 184.1771 | 222.5994 | 256.9067 | 296.5029 | 2.345%
8179 | 24-56.5 | -56.5488 | 23.6832 | 629.6319 | 154.2023 | 185.0621 | 223.6972 | 258.198 | 298.0211 | 2.432%
8180 | 24-57 | -56.8201 | 23.6832 | 622.3824 | 155.6481 | 185.9388 | 224.7665 | 259.4404 | 299.4646 | 2.522%
8181 | 24-57 | -57.0914 | 23.6832 | 615.5534 | 157.0005 | 186.7398 | 225.6995 | 260.4867 | 300.6368 | 2.61%
8182 | 24-57.5 | -57.3628 | 23.6832 | 609.1589 | 158.3566 | 187.5432 | 226.6207 | 261.5064 | 301.7636 | 2.702%
8183 | 24-57.5 | -57.6341 | 23.6832 | 603.2128 | 159.6878 | 188.3383 | 227.5141 | 262.4787 | 302.8181 | 2.797%
8184 | 24-58 | -57.9054 | 23.6832 | 597.7285 | 160.9233 | 189.0804 | 228.3161 | 263.3216 | 303.6954 | 2.89%
8185 | 24-58 | -58.1767 | 23.6832 | 592.7188 | 162.1545 | 189.8648 | 229.1802 | 264.2456 | 304.6774 | 2.986%
8186 | 24-58.5 | -58.448 | 23.6832 | 588.1959 | 163.3448 | 190.6652 | 230.0664 | 265.1973 | 305.6939 | 3.083%
8187 | 24-58.5 | -58.7194 | 23.6832 | 584.171 | 164.4351 | 191.4136 | 230.8687 | 266.0342 | 306.5569 | 3.177%
8188 | 24-59 | -58.9907 | 23.6832 | 580.6546 | 165.5321 | 192.2109 | 231.7569 | 266.9936 | 307.5884 | 3.274%
8189 | 24-59.5 | -59.262 | 23.6832 | 577.656 | 166.6004 | 193.0332 | 232.6951 | 268.0277 | 308.726 | 3.371%
8190 | 24-59.5 | -59.5333 | 23.6832 | 575.1831 | 167.5938 | 193.8348 | 233.6149 | 269.0466 | 309.8528 | 3.465%
8191 | 24-60 | -59.8046 | 23.6832 | 573.2429 | 168.5622 | 194.6672 | 234.5962 | 270.1576 | 311.1101 | 3.559%
8192 | 24-60 | -60.076 | 23.6832 | 571.8408 | 169.4723 | 195.5044 | 235.6018 | 271.3127 | 312.437 | 3.65%
8193 | 24-60.5 | -60.3473 | 23.6832 | 570.9808 | 170.2978 | 196.3124 | 236.5833 | 272.4499 | 313.7543 | 3.734%
8194 | 24-60.5 | -60.6186 | 23.6832 | 570.6652 | 171.1093 | 197.1623 | 237.6513 | 273.718 | 315.2589 | 3.817%
8195 | 24-61 | -60.8899 | 23.6832 | 570.8951 | 171.8691 | 198.0141 | 238.7448 | 275.0357 | 316.8436 | 3.896%
8196 | 24-61 | -61.1613 | 23.6832 | 571.6697 | 172.554 | 198.8318 | 239.8094 | 276.3309 | 318.4152 | 3.967%
8197 | 24-61.5 | -61.4326 | 23.6832 | 572.9868 | 173.2236 | 199.6689 | 240.924 | 277.7068 | 320.1062 | 4.037%
8198 | 24-61.5 | -61.7039 | 23.6832 | 574.8428 | 173.8574 | 200.4678 | 241.997 | 279.0389 | 321.7519 | 4.102%
8199 | 24-62 | -61.9752 | 23.6832 | 577.2323 | 174.4358 | 201.199 | 242.9823 | 280.2648 | 323.269 | 4.162%
8200 | 24-62 | -62.2465 | 23.6832 | 580.1488 | 175.0151 | 201.9476 | 244.0151 | 281.5685 | 324.9026 | 4.221%
8201 | 24-62.5 | -62.5179 | 23.6832 | 583.5845 | 175.5551 | 202.6511 | 244.9937 | 282.81 | 326.4648 | 4.275%
8202 | 24-63 | -62.7892 | 23.6832 | 587.5301 | 176.0422 | 203.2844 | 245.8727 | 283.9235 | 327.8641 | 4.325%
8203 | 24-63 | -63.0605 | 23.6832 | 591.9755 | 176.5205 | 203.9088 | 246.7428 | 285.0285 | 329.2558 | 4.373%
8204 | 24-63.5 | -63.3318 | 23.6832 | 596.9095 | 176.9551 | 204.4738 | 247.527 | 286.0221 | 330.5046 | 4.418%
8205 | 24-63.5 | -63.6031 | 23.6832 | 602.32 | 177.3476 | 204.9806 | 248.2255 | 286.9034 | 331.6084 | 4.458%
8206 | 24-64 | -63.8745 | 23.6832 | 608.1944 | 177.7407 | 205.4892 | 248.928 | 287.7908 | 332.7213 | 4.499%
8207 | 24-64 | -64.1458 | 23.6832 | 614.5193 | 178.0936 | 205.9408 | 249.5451 | 288.5653 | 333.6871 | 4.537%
8208 | 24-64.5 | -64.4171 | 23.6832 | 621.281 | 178.4155 | 206.3483 | 250.0952 | 289.2507 | 334.5366 | 4.572%
8209 | 24-64.5 | -64.6884 | 23.6832 | 628.4653 | 178.7492 | 206.7708 | 250.6658 | 289.9618 | 335.4182 | 4.608%
8210 | 24-65 | -64.9598 | 23.6832 | 636.0579 | 179.0399 | 207.1272 | 251.1301 | 290.5272 | 336.1051 | 4.641%
8211 | 24-65 | -65.2311 | 23.6832 | 644.0443 | 179.3061 | 207.4445 | 251.53 | 291.0031 | 336.6711 | 4.673%
8212 | 24-65.5 | -65.5024 | 23.6832 | 652.4101 | 179.5944 | 207.7899 | 251.9679 | 291.5265 | 337.2962 | 4.707%
8213 | 24-66 | -65.7737 | 23.6832 | 661.1409 | 179.8329 | 208.0571 | 252.2778 | 291.8728 | 337.6826 | 4.738%
8214 | 24-66 | -66.045 | 23.6832 | 670.2222 | 180.0393 | 208.2757 | 252.5108 | 292.1143 | 337.9297 | 4.766%
8215 | 24-66.5 | -66.3164 | 23.6832 | 679.6402 | 180.2506 | 208.5042 | 252.7621 | 292.3826 | 338.2141 | 4.795%
8216 | 24-66.5 | -66.5877 | 23.6832 | 689.3809 | 180.426 | 208.6884 | 252.9557 | 292.5807 | 338.4133 | 4.82%
8217 | 24-67 | -66.859 | 23.6832 | 699.4309 | 180.5897 | 208.865 | 253.1493 | 292.7867 | 338.6312 | 4.843%
8218 | 24-67 | -67.1303 | 23.6832 | 709.7769 | 180.765 | 209.0667 | 253.3923 | 293.0665 | 338.9535 | 4.865%
8219 | 24-67.5 | -67.4016 | 23.6832 | 720.4062 | 180.8858 | 209.2022 | 253.5498 | 293.2431 | 339.1512 | 4.881%
8220 | 24-67.5 | -67.673 | 23.6832 | 731.3065 | 180.9839 | 209.3201 | 253.6999 | 293.4231 | 339.3671 | 4.893%
8221 | 24-68 | -67.9443 | 23.6832 | 742.4657 | 181.0833 | 209.4564 | 253.8997 | 293.6846 | 339.7049 | 4.903%
8222 | 24-68 | -68.2156 | 23.6832 | 753.8724 | 181.1199 | 209.5128 | 253.9908 | 293.8101 | 339.8734 | 4.906%
8223 | 24-68.5 | -68.4869 | 23.6832 | 765.5154 | 181.1442 | 209.5626 | 254.086 | 293.9508 | 340.0718 | 4.906%
8224 | 24-69 | -68.7583 | 23.6832 | 777.3841 | 181.181 | 209.6422 | 254.2422 | 294.1841 | 340.4026 | 4.905%
8225 | 24-69 | -69.0296 | 23.6832 | 789.4683 | 181.1617 | 209.6487 | 254.2964 | 294.2875 | 340.5696 | 4.898%
8226 | 24-69.5 | -69.3009 | 23.6832 | 801.7583 | 181.1542 | 209.6814 | 254.4028 | 294.4692 | 340.8479 | 4.892%
8227 | 24-69.5 | -69.5722 | 23.6832 | 814.2446 | 181.1829 | 209.7764 | 254.6175 | 294.805 | 341.338 | 4.886%
8228 | 24-70 | -69.8435 | 23.6832 | 826.9183 | 181.1764 | 209.8369 | 254.8002 | 295.1127 | 341.8057 | 4.876%
8229 | 24-70 | -70.1149 | 23.6832 | 839.7709 | 181.1765 | 209.9173 | 255.0269 | 295.4886 | 342.3726 | 4.865%
8230 | 24-70.5 | -70.3862 | 23.6832 | 852.7944 | 181.1909 | 210.0266 | 255.309 | 295.9464 | 343.0552 | 4.853%
8231 | 24-70.5 | -70.6575 | 23.6832 | 865.9809 | 181.1426 | 210.0442 | 255.4486 | 296.2121 | 343.4835 | 4.837%
8232 | 24-71 | -70.9288 | 23.6832 | 879.3231 | 181.0991 | 210.0624 | 255.5811 | 296.4623 | 343.8857 | 4.822%
8233 | 24-71 | -71.2001 | 23.6832 | 892.8141 | 181.0661 | 210.0869 | 255.7118 | 296.7023 | 344.2663 | 4.81%
8234 | 24-71.5 | -71.4715 | 23.6832 | 906.447 | 180.983 | 210.0242 | 255.6896 | 296.724 | 344.3464 | 4.795%
8235 | 24-71.5 | -71.7428 | 23.6832 | 920.2155 | 180.9116 | 209.9708 | 255.6717 | 296.7444 | 344.4178 | 4.782%
8236 | 24-72 | -72.0141 | 23.6832 | 934.1137 | 180.8555 | 209.9309 | 255.6635 | 296.7703 | 344.4889 | 4.772%
8237 | 24-72.5 | -72.2854 | 23.6832 | 948.1358 | 180.8026 | 209.8776 | 255.6115 | 296.7211 | 344.4446 | 4.765%
8238 | 24-72.5 | -72.5568 | 23.6832 | 962.2764 | 180.8196 | 209.9127 | 255.679 | 296.821 | 344.5855 | 4.765%
8239 | 24-73 | -72.8281 | 23.6832 | 976.5302 | 180.876 | 209.9946 | 255.8048 | 296.9898 | 344.8077 | 4.769%
8240 | 24-73 | -73.0994 | 23.6832 | 990.8923 | 180.8378 | 209.9362 | 255.7109 | 296.8607 | 344.6343 | 4.767%
8241 | 24-73.5 | -73.3707 | 23.6832 | 1005.3581 | 180.7775 | 209.8371 | 255.5435 | 296.6254 | 344.3135 | 4.763%
8242 | 24-73.5 | -73.642 | 23.6832 | 1019.9232 | 180.69 | 209.6906 | 255.2925 | 296.2704 | 343.8275 | 4.758%
8243 | 24-74 | -73.9134 | 23.6832 | 1034.5832 | 180.5655 | 209.4793 | 254.9277 | 295.7524 | 343.1167 | 4.752%
8244 | 24-74 | -74.1847 | 23.6832 | 1049.3341 | 180.4818 | 209.3269 | 254.6534 | 295.3563 | 342.5668 | 4.749%
8245 | 24-74.5 | -74.456 | 23.6832 | 1064.1722 | 180.4129 | 209.1966 | 254.4139 | 295.0075 | 342.08 | 4.747%
8246 | 24-74.5 | -74.7273 | 23.6832 | 1079.0939 | 180.3124 | 209.0197 | 254.1018 | 294.5608 | 341.4635 | 4.743%
8247 | 24-75 | -74.9986 | 23.6832 | 1094.0955 | 180.2386 | 208.8872 | 253.8655 | 294.221 | 340.9934 | 4.74%
8248 | 24-75.5 | -75.27 | 23.6832 | 1109.174 | 180.1254 | 208.7074 | 253.5692 | 293.8095 | 340.4379 | 4.732%
8249 | 24-75.5 | -75.5413 | 23.6832 | 1124.3261 | 179.8607 | 208.3252 | 252.9838 | 293.0256 | 339.4074 | 4.709%
8250 | 24-76 | -75.8126 | 23.6832 | 1139.5489 | 179.4554 | 207.768 | 252.1663 | 291.9559 | 338.0269 | 4.671%
8251 | 24-76 | -76.0839 | 23.6832 | 1154.8395 | 178.9162 | 207.0555 | 251.1325 | 290.6115 | 336.3002 | 4.619%
8252 | 24-76.5 | -76.3553 | 23.6832 | 1170.1952 | 178.3065 | 206.2648 | 249.9766 | 289.1019 | 334.3549 | 4.56%
8253 | 24-76.5 | -76.6266 | 23.6832 | 1185.6135 | 177.7389 | 205.587 | 248.9862 | 287.8091 | 332.6894 | 4.506%
8254 | 24-77 | -76.8979 | 23.6832 | 1201.092 | 177.264 | 205.0306 | 248.1673 | 286.7359 | 331.3029 | 4.461%
8255 | 24-77 | -77.1692 | 23.6832 | 1216.6282 | 176.9458 | 204.6141 | 247.5422 | 285.9079 | 330.224 | 4.433%
8256 | 24-77.5 | -77.4405 | 23.6832 | 1232.2199 | 176.7677 | 204.3639 | 247.1593 | 285.3955 | 329.551 | 4.417%
8257 | 24-77.5 | -77.7119 | 23.6832 | 1247.8651 | 176.6032 | 204.1219 | 246.7831 | 284.8879 | 328.8802 | 4.404%
8258 | 24-78 | -77.9832 | 23.6832 | 1263.5617 | 176.3642 | 203.7753 | 246.2507 | 284.1743 | 327.9417 | 4.383%
8259 | 24-78.5 | -78.2545 | 23.6832 | 1279.3078 | 176.0916 | 203.4046 | 245.6933 | 283.4352 | 326.9782 | 4.359%
8260 | 24-78.5 | -78.5258 | 23.6832 | 1295.1015 | 175.7644 | 202.9859 | 245.0677 | 282.6086 | 325.9033 | 4.329%
8261 | 24-79 | -78.7971 | 23.6832 | 1310.9411 | 175.4598 | 202.5926 | 244.4759 | 281.8239 | 324.8803 | 4.302%
8262 | 24-79 | -79.0685 | 23.6832 | 1326.8249 | 175.2965 | 202.3865 | 244.1602 | 281.4015 | 324.3258 | 4.288%
8263 | 24-79.5 | -79.3398 | 23.6832 | 1342.7512 | 175.2528 | 202.3265 | 244.04 | 281.2212 | 324.0695 | 4.287%
8264 | 24-79.5 | -79.6111 | 23.6832 | 1358.7186 | 175.3104 | 202.3675 | 244.0496 | 281.1971 | 324.0014 | 4.296%
8265 | 24-80 | -79.8824 | 23.6832 | 1374.7256 | 175.4462 | 202.4824 | 244.1662 | 281.3126 | 324.1127 | 4.314%
8266 | 24-80 | -80.1537 | 23.6832 | 1390.7707 | 175.6887 | 202.665 | 244.3662 | 281.5254 | 324.3376 | 4.342%
8267 | 24-80.5 | -80.4251 | 23.6832 | 1406.8526 | 175.9831 | 202.9081 | 244.6383 | 281.8205 | 324.6563 | 4.378%
8268 | 24-80.5 | -80.6964 | 23.6832 | 1422.97 | 176.2749 | 203.2064 | 244.9801 | 282.1988 | 325.0742 | 4.414%
8269 | 24-81 | -80.9677 | 23.6832 | 1439.1217 | 176.4211 | 203.3304 | 245.0677 | 282.2455 | 325.0655 | 4.437%
8270 | 24-81 | -81.239 | 23.6832 | 1455.3065 | 176.485 | 203.3547 | 245.0183 | 282.1198 | 324.8415 | 4.451%
8271 | 24-81.5 | -81.5104 | 23.6832 | 1471.5233 | 176.5841 | 203.4342 | 245.059 | 282.1188 | 324.7851 | 4.468%
8272 | 24-82 | -81.7817 | 23.6832 | 1487.771 | 176.7229 | 203.547 | 245.1395 | 282.1632 | 324.7807 | 4.489%
8273 | 24-82 | -82.053 | 23.6832 | 1504.0484 | 176.9235 | 203.7133 | 245.2905 | 282.2941 | 324.882 | 4.518%
8274 | 24-82.5 | -82.3243 | 23.6832 | 1520.3548 | 177.1786 | 203.9558 | 245.5505 | 282.5654 | 325.162 | 4.552%
8275 | 24-82.5 | -82.5956 | 23.6832 | 1536.689 | 177.5024 | 204.2924 | 245.9365 | 282.9926 | 325.6339 | 4.594%
8276 | 24-83 | -82.867 | 23.6832 | 1553.0501 | 177.9226 | 204.77 | 246.5346 | 283.7008 | 326.4716 | 4.646%
8277 | 24-83 | -83.1383 | 23.6832 | 1569.4373 | 178.4534 | 205.4173 | 247.3996 | 284.771 | 327.7893 | 4.707%
8278 | 24-83.5 | -83.4096 | 23.6832 | 1585.8497 | 178.9135 | 205.9973 | 248.194 | 285.769 | 329.0344 | 4.758%
8279 | 24-83.5 | -83.6809 | 23.6832 | 1602.2865 | 179.2747 | 206.4828 | 248.8904 | 286.6682 | 330.1821 | 4.795%
8280 | 24-84 | -83.9522 | 23.6832 | 1618.7469 | 179.5424 | 206.8737 | 249.4935 | 287.4783 | 331.2487 | 4.818%
8281 | 24-84 | -84.2236 | 23.6832 | 1635.2302 | 179.648 | 207.074 | 249.8611 | 288.0121 | 331.9913 | 4.821%
8282 | 24-84.5 | -84.4949 | 23.6832 | 1651.7355 | 179.7599 | 207.3046 | 250.3021 | 288.663 | 332.9065 | 4.821%
8283 | 24-85 | -84.7662 | 23.6832 | 1668.2623 | 179.9418 | 207.6487 | 250.9328 | 289.5788 | 334.1807 | 4.825%
8284 | 24-85 | -85.0375 | 23.6832 | 1684.8099 | 180.0965 | 207.9627 | 251.5291 | 290.4566 | 335.4128 | 4.826%
8285 | 24-85.5 | -85.3089 | 23.6832 | 1701.3775 | 180.227 | 208.2609 | 252.1256 | 291.3514 | 336.6843 | 4.822%
8286 | 24-85.5 | -85.5802 | 23.6832 | 1717.9646 | 180.3297 | 208.542 | 252.7258 | 292.2721 | 338.0104 | 4.812%
8287 | 24-86 | -85.8515 | 23.6832 | 1734.5705 | 180.3181 | 208.6817 | 253.1399 | 292.9648 | 339.0582 | 4.79%
8288 | 24-86 | -86.1228 | 23.6832 | 1751.1948 | 180.1723 | 208.6584 | 253.3443 | 293.4045 | 339.8019 | 4.752%
8289 | 24-86.5 | -86.3941 | 23.6832 | 1767.8367 | 179.8788 | 208.454 | 253.3136 | 293.5593 | 340.2015 | 4.698%
8290 | 24-86.5 | -86.6655 | 23.6832 | 1784.4959 | 179.3614 | 207.9656 | 252.8985 | 293.2349 | 340.0072 | 4.62%
8291 | 24-87 | -86.9368 | 23.6832 | 1801.1717 | 178.7945 | 207.4276 | 252.4363 | 292.8675 | 339.7766 | 4.538%
8292 | 24-87 | -87.2081 | 23.6832 | 1817.8636 | 178.1882 | 206.8513 | 251.9395 | 292.4708 | 339.5251 | 4.452%
8293 | 24-87.5 | -87.4794 | 23.6832 | 1834.5713 | 177.4702 | 206.1209 | 251.2161 | 291.7769 | 338.8889 | 4.358%
8294 | 24-88 | -87.7507 | 23.6832 | 1851.2941 | 176.7 | 205.3289 | 250.4086 | 290.9775 | 338.1213 | 4.261%
8295 | 24-88 | -88.0221 | 23.6832 | 1868.0316 | 175.8636 | 204.4672 | 249.5047 | 290.0564 | 337.201 | 4.16%
8296 | 24-88.5 | -88.2934 | 23.6832 | 1884.7835 | 174.9056 | 203.4667 | 248.3884 | 288.8507 | 335.9062 | 4.051%
8297 | 24-88.5 | -88.5647 | 23.6832 | 1901.5492 | 173.9135 | 202.4614 | 247.2695 | 287.6448 | 334.6144 | 3.943%
8298 | 24-89 | -88.836 | 23.6832 | 1918.3284 | 172.8792 | 201.4344 | 246.1164 | 286.3922 | 333.2605 | 3.833%
8299 | 24-89 | -89.1074 | 23.6832 | 1935.1207 | 171.7639 | 200.3256 | 244.8186 | 284.9319 | 331.6194 | 3.722%
8300 | 24-89.5 | -89.3787 | 23.6832 | 1951.9257 | 170.6544 | 199.2509 | 243.554 | 283.5031 | 330.0064 | 3.616%
8301 | 24-89.5 | -89.65 | 23.6832 | 1968.743 | 169.5361 | 198.1842 | 242.2816 | 282.0497 | 328.3466 | 3.512%
8302 | 24-90 | -89.9213 | 23.6832 | 1985.5722 | 168.3691 | 197.073 | 240.9133 | 280.4482 | 326.4723 | 3.409%
8303 | 24-90 | -90.1926 | 23.6832 | 2002.4131 | 167.231 | 196.0111 | 239.5851 | 278.8755 | 324.6107 | 3.313%
8304 | 24-90.5 | -90.464 | 23.6832 | 2019.2652 | 166.1012 | 194.9719 | 238.2606 | 277.2862 | 322.7052 | 3.221%
8305 | 24-90.5 | -90.7353 | 23.6832 | 2036.1282 | 164.938 | 193.92 | 236.8983 | 275.6329 | 320.7023 | 3.13%
8306 | 24-50 | -50.0371 | 23.9545 | 906.5282 | 116.7568 | 154.1985 | 191.2779 | 218.1334 | 248.762 | 0.8956%
8307 | 24-50.5 | -50.3084 | 23.9545 | 893.2148 | 118.4911 | 156.4812 | 192.7896 | 219.9069 | 250.8408 | 0.9424%
8308 | 24-50.5 | -50.5797 | 23.9545 | 880.0525 | 120.162 | 158.618 | 194.2151 | 221.5737 | 252.7883 | 0.9895%
8309 | 24-51 | -50.851 | 23.9545 | 867.0482 | 121.7814 | 160.6112 | 195.5755 | 223.1708 | 254.6617 | 1.037%
8310 | 24-51 | -51.1224 | 23.9545 | 854.209 | 123.3771 | 162.4732 | 196.9081 | 224.7532 | 256.5378 | 1.086%
8311 | 24-51.5 | -51.3937 | 23.9545 | 841.5427 | 124.8905 | 164.1424 | 198.1503 | 226.2325 | 258.2965 | 1.134%
8312 | 24-51.5 | -51.665 | 23.9545 | 829.0571 | 126.3568 | 165.6586 | 199.3557 | 227.6896 | 260.0526 | 1.181%
8313 | 24-52 | -51.9363 | 23.9545 | 816.7606 | 127.8077 | 167.0462 | 200.5706 | 229.1907 | 261.897 | 1.23%
8314 | 24-52 | -52.2077 | 23.9545 | 804.6618 | 129.183 | 168.2502 | 201.7083 | 230.6006 | 263.6341 | 1.278%
8315 | 24-52.5 | -52.479 | 23.9545 | 792.7699 | 130.5497 | 169.3633 | 202.8545 | 232.0348 | 265.4154 | 1.326%
8316 | 24-53 | -52.7503 | 23.9545 | 781.0944 | 131.951 | 170.4349 | 204.0632 | 233.5647 | 267.3343 | 1.377%
8317 | 24-53 | -53.0216 | 23.9545 | 769.6451 | 133.2953 | 171.3944 | 205.226 | 235.0384 | 269.1848 | 1.427%
8318 | 24-53.5 | -53.2929 | 23.9545 | 758.4323 | 134.6673 | 172.3407 | 206.4433 | 236.5929 | 271.1491 | 1.479%
8319 | 24-53.5 | -53.5643 | 23.9545 | 747.4667 | 136.1101 | 173.3138 | 207.7637 | 238.2925 | 273.3109 | 1.536%
8320 | 24-54 | -53.8356 | 23.9545 | 736.7593 | 137.5289 | 174.2413 | 209.0732 | 239.9788 | 275.4569 | 1.593%
8321 | 24-54 | -54.1069 | 23.9545 | 726.3216 | 139.0102 | 175.2122 | 210.4636 | 241.7734 | 277.745 | 1.656%
8322 | 24-54.5 | -54.3782 | 23.9545 | 716.1654 | 140.5814 | 176.2534 | 211.9607 | 243.7075 | 280.2131 | 1.724%
8323 | 24-54.5 | -54.6495 | 23.9545 | 706.3028 | 142.1242 | 177.2798 | 213.4176 | 245.5762 | 282.5843 | 1.793%
8324 | 24-55 | -54.9209 | 23.9545 | 696.7465 | 143.7074 | 178.3365 | 214.9038 | 247.4726 | 284.9806 | 1.867%
8325 | 24-55 | -55.1922 | 23.9545 | 687.5091 | 145.3376 | 179.426 | 216.4196 | 249.3948 | 287.3975 | 1.945%
8326 | 24-55.5 | -55.4635 | 23.9545 | 678.6037 | 146.8928 | 180.4494 | 217.7946 | 251.1016 | 289.5052 | 2.023%
8327 | 24-55.5 | -55.7348 | 23.9545 | 670.0436 | 148.4401 | 181.4522 | 219.1228 | 252.7354 | 291.5065 | 2.104%
8328 | 24-56 | -56.0061 | 23.9545 | 661.8421 | 149.98 | 182.4356 | 220.4077 | 254.3019 | 293.4105 | 2.187%
8329 | 24-56.5 | -56.2775 | 23.9545 | 654.0129 | 151.4481 | 183.3535 | 221.5748 | 255.6991 | 295.0807 | 2.269%
8330 | 24-56.5 | -56.5488 | 23.9545 | 646.5695 | 152.9436 | 184.2775 | 222.7366 | 257.0789 | 296.7177 | 2.355%
8331 | 24-57 | -56.8201 | 23.9545 | 639.5253 | 154.4453 | 185.1972 | 223.8747 | 258.4154 | 298.2866 | 2.446%
8332 | 24-57 | -57.0914 | 23.9545 | 632.8937 | 155.8657 | 186.0459 | 224.8815 | 259.5608 | 299.5892 | 2.536%
8333 | 24-57.5 | -57.3628 | 23.9545 | 626.6878 | 157.3023 | 186.9009 | 225.8795 | 260.6816 | 300.847 | 2.63%
8334 | 24-57.5 | -57.6341 | 23.9545 | 620.9203 | 158.7247 | 187.7495 | 226.849 | 261.7516 | 302.0255 | 2.728%
8335 | 24-58 | -57.9054 | 23.9545 | 615.6037 | 160.0523 | 188.5413 | 227.7171 | 262.6758 | 303.0026 | 2.824%
8336 | 24-58 | -58.1767 | 23.9545 | 610.7498 | 161.3715 | 189.3715 | 228.6388 | 263.6685 | 304.0663 | 2.924%
8337 | 24-58.5 | -58.448 | 23.9545 | 606.3695 | 162.644 | 190.2117 | 229.5714 | 264.6723 | 305.1411 | 3.026%
8338 | 24-58.5 | -58.7194 | 23.9545 | 602.4734 | 163.808 | 190.991 | 230.4048 | 265.5396 | 306.033 | 3.123%
8339 | 24-59 | -58.9907 | 23.9545 | 599.0707 | 164.9726 | 191.8134 | 231.3161 | 266.5193 | 307.0806 | 3.224%
8340 | 24-59.5 | -59.262 | 23.9545 | 596.1701 | 166.1021 | 192.6552 | 232.2692 | 267.5634 | 308.2213 | 3.325%
8341 | 24-59.5 | -59.5333 | 23.9545 | 593.7788 | 167.1512 | 193.4717 | 233.1974 | 268.5835 | 309.3398 | 3.423%
8342 | 24-60 | -59.8046 | 23.9545 | 591.9031 | 168.172 | 194.3174 | 234.1843 | 269.6917 | 310.5835 | 3.521%
8343 | 24-60 | -60.076 | 23.9545 | 590.5478 | 169.1287 | 195.1676 | 235.1945 | 270.8427 | 311.8945 | 3.615%
8344 | 24-60.5 | -60.3473 | 23.9545 | 589.7166 | 169.9955 | 195.9901 | 236.183 | 271.9785 | 313.1997 | 3.703%
8345 | 24-60.5 | -60.6186 | 23.9545 | 589.4117 | 170.8429 | 196.8557 | 237.2609 | 273.2502 | 314.6991 | 3.79%
8346 | 24-61 | -60.8899 | 23.9545 | 589.6338 | 171.6307 | 197.7236 | 238.3655 | 274.5734 | 316.2821 | 3.871%
8347 | 24-61 | -61.1613 | 23.9545 | 590.3824 | 172.3357 | 198.5571 | 239.4413 | 275.8746 | 317.8524 | 3.945%
8348 | 24-61.5 | -61.4326 | 23.9545 | 591.6555 | 173.0264 | 199.415 | 240.5751 | 277.2676 | 319.5574 | 4.017%
8349 | 24-61.5 | -61.7039 | 23.9545 | 593.4498 | 173.684 | 200.2391 | 241.675 | 278.6277 | 321.2317 | 4.085%
8350 | 24-62 | -61.9752 | 23.9545 | 595.7604 | 174.2892 | 201.0006 | 242.696 | 279.8939 | 322.7945 | 4.148%
8351 | 24-62 | -62.2465 | 23.9545 | 598.5814 | 174.9007 | 201.7878 | 243.7775 | 281.2557 | 324.4973 | 4.21%
8352 | 24-62.5 | -62.5179 | 23.9545 | 601.9057 | 175.4769 | 202.5354 | 244.8133 | 282.5665 | 326.1431 | 4.269%
8353 | 24-63 | -62.7892 | 23.9545 | 605.7249 | 176.0029 | 203.2161 | 245.7537 | 283.7545 | 327.6326 | 4.323%
8354 | 24-63 | -63.0605 | 23.9545 | 610.0297 | 176.5218 | 203.8904 | 246.6889 | 284.9387 | 329.1205 | 4.376%
8355 | 24-63.5 | -63.3318 | 23.9545 | 614.81 | 176.9973 | 204.5058 | 247.539 | 286.0127 | 330.467 | 4.425%
8356 | 24-63.5 | -63.6031 | 23.9545 | 620.0546 | 177.4292 | 205.0609 | 248.3005 | 286.9705 | 331.6637 | 4.47%
8357 | 24-64 | -63.8745 | 23.9545 | 625.752 | 177.8589 | 205.6138 | 249.0598 | 287.9265 | 332.859 | 4.515%
8358 | 24-64 | -64.1458 | 23.9545 | 631.8898 | 178.2448 | 206.1052 | 249.7276 | 288.7618 | 333.8976 | 4.556%
8359 | 24-64.5 | -64.4171 | 23.9545 | 638.4554 | 178.5968 | 206.5495 | 250.3254 | 289.505 | 334.817 | 4.595%
8360 | 24-64.5 | -64.6884 | 23.9545 | 645.4356 | 178.9592 | 207.0082 | 250.9447 | 290.2768 | 335.7737 | 4.634%
8361 | 24-65 | -64.9598 | 23.9545 | 652.8172 | 179.2765 | 207.3985 | 251.4554 | 290.9002 | 336.5329 | 4.671%
8362 | 24-65 | -65.2311 | 23.9545 | 660.5867 | 179.5674 | 207.7476 | 251.8986 | 291.4307 | 337.167 | 4.705%
8363 | 24-65.5 | -65.5024 | 23.9545 | 668.7305 | 179.8793 | 208.1233 | 252.3781 | 292.0064 | 337.8576 | 4.742%
8364 | 24-66 | -65.7737 | 23.9545 | 677.2352 | 180.1387 | 208.4161 | 252.7216 | 292.3937 | 338.2939 | 4.776%
8365 | 24-66 | -66.045 | 23.9545 | 686.0872 | 180.3643 | 208.6573 | 252.9822 | 292.6675 | 338.5787 | 4.807%
8366 | 24-66.5 | -66.3164 | 23.9545 | 695.2733 | 180.5943 | 208.9068 | 253.2583 | 292.9638 | 338.8947 | 4.838%
8367 | 24-66.5 | -66.5877 | 23.9545 | 704.7803 | 180.7834 | 209.1048 | 253.4652 | 293.1741 | 339.1046 | 4.865%
8368 | 24-67 | -66.859 | 23.9545 | 714.5956 | 180.9566 | 209.2884 | 253.661 | 293.3773 | 339.3127 | 4.89%
8369 | 24-67 | -67.1303 | 23.9545 | 724.7065 | 181.1383 | 209.4921 | 253.8977 | 293.6422 | 339.6089 | 4.914%
8370 | 24-67.5 | -67.4016 | 23.9545 | 735.1007 | 181.264 | 209.6281 | 254.0473 | 293.8021 | 339.7788 | 4.932%
8371 | 24-67.5 | -67.673 | 23.9545 | 745.7665 | 181.3669 | 209.746 | 254.1887 | 293.9643 | 339.9651 | 4.946%
8372 | 24-68 | -67.9443 | 23.9545 | 756.6923 | 181.4712 | 209.8819 | 254.3781 | 294.2051 | 340.2687 | 4.957%
8373 | 24-68 | -68.2156 | 23.9545 | 767.867 | 181.5117 | 209.9358 | 254.4549 | 294.304 | 340.395 | 4.961%
8374 | 24-68.5 | -68.4869 | 23.9545 | 779.2798 | 181.5398 | 209.9829 | 254.5356 | 294.4182 | 340.5511 | 4.962%
8375 | 24-69 | -68.7583 | 23.9545 | 790.9205 | 181.581 | 210.0609 | 254.679 | 294.6271 | 340.8427 | 4.963%
8376 | 24-69 | -69.0296 | 23.9545 | 802.779 | 181.5632 | 210.0612 | 254.7129 | 294.6957 | 340.9564 | 4.958%
8377 | 24-69.5 | -69.3009 | 23.9545 | 814.8458 | 181.556 | 210.0864 | 254.7974 | 294.8409 | 341.1792 | 4.952%
8378 | 24-69.5 | -69.5722 | 23.9545 | 827.1118 | 181.5851 | 210.1745 | 254.9917 | 295.1425 | 341.6175 | 4.948%
8379 | 24-70 | -69.8435 | 23.9545 | 839.5683 | 181.5782 | 210.2283 | 255.1564 | 295.4203 | 342.0401 | 4.938%
8380 | 24-70 | -70.1149 | 23.9545 | 852.2067 | 181.5822 | 210.3088 | 255.376 | 295.7817 | 342.5827 | 4.927%
8381 | 24-70.5 | -70.3862 | 23.9545 | 865.0192 | 181.6062 | 210.4268 | 255.6644 | 296.2432 | 343.2651 | 4.918%
8382 | 24-70.5 | -70.6575 | 23.9545 | 877.9981 | 181.5722 | 210.4603 | 255.8224 | 296.5291 | 343.7158 | 4.903%
8383 | 24-71 | -70.9288 | 23.9545 | 891.1361 | 181.5463 | 210.4987 | 255.9789 | 296.8067 | 344.149 | 4.89%
8384 | 24-71 | -71.2001 | 23.9545 | 904.4261 | 181.5343 | 210.5472 | 256.1381 | 297.0791 | 344.5666 | 4.88%
8385 | 24-71.5 | -71.4715 | 23.9545 | 917.8616 | 181.4741 | 210.5107 | 256.1471 | 297.1364 | 344.6872 | 4.868%
8386 | 24-71.5 | -71.7428 | 23.9545 | 931.4363 | 181.4289 | 210.4869 | 256.1641 | 297.1963 | 344.8033 | 4.858%
8387 | 24-72 | -72.0141 | 23.9545 | 945.1441 | 181.4014 | 210.4794 | 256.1942 | 297.2655 | 344.9234 | 4.851%
8388 | 24-72.5 | -72.2854 | 23.9545 | 958.9792 | 181.3776 | 210.4603 | 256.1846 | 297.2664 | 344.9382 | 4.847%
8389 | 24-72.5 | -72.5568 | 23.9545 | 972.9362 | 181.4272 | 210.5366 | 256.3075 | 297.4352 | 345.1643 | 4.851%
8390 | 24-73 | -72.8281 | 23.9545 | 987.0099 | 181.5188 | 210.6645 | 256.498 | 297.6866 | 345.4913 | 4.859%
8391 | 24-73 | -73.0994 | 23.9545 | 1001.1954 | 181.5135 | 210.6493 | 256.4647 | 297.6349 | 345.416 | 4.86%
8392 | 24-73.5 | -73.3707 | 23.9545 | 1015.4879 | 181.4846 | 210.5907 | 256.3529 | 297.4698 | 345.1834 | 4.86%
8393 | 24-73.5 | -73.642 | 23.9545 | 1029.8828 | 181.4263 | 210.4809 | 256.1514 | 297.1765 | 344.7741 | 4.858%
8394 | 24-74 | -73.9134 | 23.9545 | 1044.3761 | 181.3276 | 210.3012 | 255.8282 | 296.7098 | 344.1261 | 4.855%
8395 | 24-74 | -74.1847 | 23.9545 | 1058.9635 | 181.2672 | 210.1765 | 255.5886 | 296.3548 | 343.625 | 4.855%
8396 | 24-74.5 | -74.456 | 23.9545 | 1073.6412 | 181.2186 | 210.0688 | 255.3751 | 296.035 | 343.1705 | 4.856%
8397 | 24-74.5 | -74.7273 | 23.9545 | 1088.4055 | 181.1345 | 209.908 | 255.0781 | 295.6018 | 342.5656 | 4.854%
8398 | 24-75 | -74.9986 | 23.9545 | 1103.2529 | 181.0737 | 209.7858 | 254.8467 | 295.2612 | 342.0871 | 4.853%
8399 | 24-75.5 | -75.27 | 23.9545 | 1118.18 | 180.9753 | 209.6181 | 254.557 | 294.8506 | 341.5247 | 4.848%
8400 | 24-75.5 | -75.5413 | 23.9545 | 1133.1837 | 180.7365 | 209.2632 | 254.0009 | 294.0973 | 340.5261 | 4.829%
8401 | 24-76 | -75.8126 | 23.9545 | 1148.2609 | 180.3705 | 208.7494 | 253.2337 | 293.0837 | 339.2083 | 4.795%
8402 | 24-76 | -76.0839 | 23.9545 | 1163.4088 | 179.8956 | 208.0927 | 252.2659 | 291.8145 | 337.5672 | 4.75%
8403 | 24-76.5 | -76.3553 | 23.9545 | 1178.6245 | 179.3698 | 207.3665 | 251.1877 | 290.3943 | 335.7246 | 4.701%
8404 | 24-76.5 | -76.6266 | 23.9545 | 1193.9054 | 178.9075 | 206.7689 | 250.2987 | 289.2224 | 334.2032 | 4.657%
8405 | 24-77 | -76.8979 | 23.9545 | 1209.249 | 178.5332 | 206.2902 | 249.5804 | 288.2711 | 332.9639 | 4.623%
8406 | 24-77 | -77.1692 | 23.9545 | 1224.6529 | 178.2814 | 205.9283 | 249.0271 | 287.531 | 331.9925 | 4.601%
8407 | 24-77.5 | -77.4405 | 23.9545 | 1240.1148 | 178.1335 | 205.7105 | 248.6884 | 287.0742 | 331.389 | 4.589%
8408 | 24-77.5 | -77.7119 | 23.9545 | 1255.6326 | 177.9819 | 205.4872 | 248.3411 | 286.6057 | 330.7698 | 4.576%
8409 | 24-78 | -77.9832 | 23.9545 | 1271.2042 | 177.7495 | 205.1543 | 247.8349 | 285.9305 | 329.8856 | 4.556%
8410 | 24-78.5 | -78.2545 | 23.9545 | 1286.8275 | 177.4782 | 204.7936 | 247.3033 | 285.2334 | 328.9843 | 4.53%
8411 | 24-78.5 | -78.5258 | 23.9545 | 1302.5006 | 177.1323 | 204.3625 | 246.6773 | 284.4192 | 327.9386 | 4.496%
8412 | 24-79 | -78.7971 | 23.9545 | 1318.2218 | 176.7723 | 203.9119 | 246.0269 | 283.5762 | 326.8593 | 4.461%
8413 | 24-79 | -79.0685 | 23.9545 | 1333.9893 | 176.5072 | 203.59 | 245.5742 | 282.9982 | 326.1283 | 4.434%
8414 | 24-79.5 | -79.3398 | 23.9545 | 1349.8014 | 176.3478 | 203.3968 | 245.2929 | 282.6319 | 325.6576 | 4.418%
8415 | 24-79.5 | -79.6111 | 23.9545 | 1365.6566 | 176.2842 | 203.3161 | 245.1561 | 282.4398 | 325.3962 | 4.414%
8416 | 24-80 | -79.8824 | 23.9545 | 1381.5533 | 176.2991 | 203.3256 | 245.1489 | 282.4153 | 325.3493 | 4.417%
8417 | 24-80 | -80.1537 | 23.9545 | 1397.4901 | 176.3947 | 203.3825 | 245.1965 | 282.4518 | 325.3704 | 4.43%
8418 | 24-80.5 | -80.4251 | 23.9545 | 1413.4655 | 176.5278 | 203.4791 | 245.2869 | 282.5332 | 325.438 | 4.447%
8419 | 24-80.5 | -80.6964 | 23.9545 | 1429.4782 | 176.6736 | 203.6312 | 245.4467 | 282.6968 | 325.6027 | 4.467%
8420 | 24-81 | -80.9677 | 23.9545 | 1445.527 | 176.7141 | 203.6374 | 245.3896 | 282.5746 | 325.3968 | 4.477%
8421 | 24-81 | -81.239 | 23.9545 | 1461.6106 | 176.7023 | 203.5749 | 245.2362 | 282.3297 | 325.0362 | 4.482%
8422 | 24-81.5 | -81.5104 | 23.9545 | 1477.7278 | 176.7447 | 203.5909 | 245.203 | 282.2458 | 324.8871 | 4.491%
8423 | 24-82 | -81.7817 | 23.9545 | 1493.8775 | 176.8351 | 203.6493 | 245.2202 | 282.2194 | 324.8033 | 4.507%
8424 | 24-82 | -82.053 | 23.9545 | 1510.0587 | 177.0074 | 203.7862 | 245.341 | 282.3199 | 324.8747 | 4.531%
8425 | 24-82.5 | -82.3243 | 23.9545 | 1526.2702 | 177.266 | 204.0399 | 245.6258 | 282.6295 | 325.2101 | 4.565%
8426 | 24-82.5 | -82.5956 | 23.9545 | 1542.511 | 177.6107 | 204.4089 | 246.0638 | 283.128 | 325.7769 | 4.609%
8427 | 24-83 | -82.867 | 23.9545 | 1558.7803 | 178.0335 | 204.8956 | 246.6825 | 283.8682 | 326.6609 | 4.66%
8428 | 24-83 | -83.1383 | 23.9545 | 1575.0771 | 178.529 | 205.5045 | 247.505 | 284.8925 | 327.9295 | 4.716%
8429 | 24-83.5 | -83.4096 | 23.9545 | 1591.4004 | 178.9309 | 206.0159 | 248.2143 | 285.7905 | 329.0571 | 4.76%
8430 | 24-83.5 | -83.6809 | 23.9545 | 1607.7495 | 179.242 | 206.4428 | 248.8386 | 286.6053 | 330.106 | 4.791%
8431 | 24-84 | -83.9522 | 23.9545 | 1624.1235 | 179.4823 | 206.8038 | 249.4083 | 287.3793 | 331.1337 | 4.811%
8432 | 24-84 | -84.2236 | 23.9545 | 1640.5217 | 179.5854 | 207.0042 | 249.7806 | 287.9226 | 331.8919 | 4.812%
8433 | 24-84.5 | -84.4949 | 23.9545 | 1656.9432 | 179.6978 | 207.2372 | 250.2272 | 288.5823 | 332.8199 | 4.812%
8434 | 24-85 | -84.7662 | 23.9545 | 1673.3874 | 179.8746 | 207.5748 | 250.8492 | 289.4871 | 334.0803 | 4.816%
8435 | 24-85 | -85.0375 | 23.9545 | 1689.8534 | 180.017 | 207.8715 | 251.4194 | 290.3303 | 335.2672 | 4.815%
8436 | 24-85.5 | -85.3089 | 23.9545 | 1706.3408 | 180.1386 | 208.1548 | 251.9905 | 291.1893 | 336.4896 | 4.811%
8437 | 24-85.5 | -85.5802 | 23.9545 | 1722.8487 | 180.2388 | 208.4268 | 252.5699 | 292.0772 | 337.768 | 4.802%
8438 | 24-86 | -85.8515 | 23.9545 | 1739.3766 | 180.2293 | 208.5611 | 252.9647 | 292.7364 | 338.7641 | 4.781%
8439 | 24-86 | -86.1228 | 23.9545 | 1755.9238 | 180.1054 | 208.5552 | 253.1775 | 293.1748 | 339.4933 | 4.747%
8440 | 24-86.5 | -86.3941 | 23.9545 | 1772.4898 | 179.8558 | 208.3939 | 253.1862 | 293.3639 | 339.9193 | 4.699%
8441 | 24-86.5 | -86.6655 | 23.9545 | 1789.074 | 179.4018 | 207.9706 | 252.837 | 293.104 | 339.786 | 4.631%
8442 | 24-87 | -86.9368 | 23.9545 | 1805.6759 | 178.9029 | 207.503 | 252.4466 | 292.8076 | 339.6234 | 4.557%
8443 | 24-87 | -87.2081 | 23.9545 | 1822.2948 | 178.3672 | 206.9996 | 252.0242 | 292.4845 | 339.4423 | 4.48%
8444 | 24-87.5 | -87.4794 | 23.9545 | 1838.9304 | 177.7206 | 206.3437 | 251.3777 | 291.8676 | 338.8813 | 4.394%
8445 | 24-88 | -87.7507 | 23.9545 | 1855.5821 | 177.0245 | 205.6266 | 250.6506 | 291.152 | 338.1998 | 4.305%
8446 | 24-88 | -88.0221 | 23.9545 | 1872.2495 | 176.2683 | 204.8401 | 249.8309 | 290.322 | 337.3774 | 4.212%
8447 | 24-88.5 | -88.2934 | 23.9545 | 1888.932 | 175.3962 | 203.9153 | 248.8039 | 289.2173 | 336.1969 | 4.111%
8448 | 24-88.5 | -88.5647 | 23.9545 | 1905.6292 | 174.496 | 202.9882 | 247.7824 | 288.1263 | 335.0406 | 4.009%
8449 | 24-89 | -88.836 | 23.9545 | 1922.3408 | 173.5582 | 202.0417 | 246.7344 | 287.002 | 333.843 | 3.907%
8450 | 24-89 | -89.1074 | 23.9545 | 1939.0663 | 172.5413 | 201.0119 | 245.5442 | 285.6769 | 332.3704 | 3.802%
8451 | 24-89.5 | -89.3787 | 23.9545 | 1955.8052 | 171.532 | 200.0157 | 244.3903 | 284.3897 | 330.9371 | 3.702%
8452 | 24-89.5 | -89.65 | 23.9545 | 1972.5572 | 170.5143 | 199.0256 | 243.2289 | 283.0807 | 329.4632 | 3.604%
8453 | 24-90 | -89.9213 | 23.9545 | 1989.322 | 169.4458 | 197.9852 | 241.9662 | 281.619 | 327.7711 | 3.506%
8454 | 24-90 | -90.1926 | 23.9545 | 2006.0991 | 168.4056 | 196.9914 | 240.7415 | 280.1845 | 326.0912 | 3.414%
8455 | 24-90.5 | -90.464 | 23.9545 | 2022.8882 | 167.3721 | 196.016 | 239.5149 | 278.7267 | 324.3593 | 3.326%
8456 | 24-90.5 | -90.7353 | 23.9545 | 2039.6889 | 166.3028 | 195.0206 | 238.2385 | 277.1884 | 322.5076 | 3.239%
8457 | 24-50 | -50.0371 | 24.2258 | 918.3415 | 115.7013 | 152.7373 | 190.2239 | 216.8165 | 247.1297 | 0.8669%
8458 | 24-50.5 | -50.3084 | 24.2258 | 905.2269 | 117.4491 | 155.0862 | 191.7651 | 218.6329 | 249.2679 | 0.9129%
8459 | 24-50.5 | -50.5797 | 24.2258 | 892.2665 | 119.1366 | 157.2987 | 193.2204 | 220.3401 | 251.2689 | 0.9593%
8460 | 24-51 | -50.851 | 24.2258 | 879.4671 | 120.7742 | 159.3733 | 194.6084 | 221.973 | 253.1879 | 1.006%
8461 | 24-51 | -51.1224 | 24.2258 | 866.8359 | 122.3893 | 161.3189 | 195.9662 | 223.5872 | 255.1037 | 1.055%
8462 | 24-51.5 | -51.3937 | 24.2258 | 854.3805 | 123.92 | 163.0717 | 197.2275 | 225.0892 | 256.8892 | 1.102%
8463 | 24-51.5 | -51.665 | 24.2258 | 842.1086 | 125.3985 | 164.6677 | 198.4438 | 226.5578 | 258.657 | 1.149%
8464 | 24-52 | -51.9363 | 24.2258 | 830.0284 | 126.8549 | 166.1286 | 199.6606 | 228.0586 | 260.4983 | 1.197%
8465 | 24-52 | -52.2077 | 24.2258 | 818.1485 | 128.2297 | 167.3918 | 200.7914 | 229.456 | 262.2155 | 1.244%
8466 | 24-52.5 | -52.479 | 24.2258 | 806.4776 | 129.5882 | 168.5495 | 201.9209 | 230.8647 | 263.9605 | 1.291%
8467 | 24-53 | -52.7503 | 24.2258 | 795.0252 | 130.9732 | 169.6502 | 203.1032 | 232.3571 | 265.8279 | 1.34%
8468 | 24-53 | -53.0216 | 24.2258 | 783.8007 | 132.2924 | 170.6221 | 204.2306 | 233.7819 | 267.6126 | 1.388%
8469 | 24-53.5 | -53.2929 | 24.2258 | 772.8142 | 133.6296 | 171.5662 | 205.4044 | 235.2775 | 269.499 | 1.438%
8470 | 24-53.5 | -53.5643 | 24.2258 | 762.0759 | 135.0285 | 172.5231 | 206.6738 | 236.9091 | 271.5716 | 1.492%
8471 | 24-54 | -53.8356 | 24.2258 | 751.5966 | 136.3976 | 173.4219 | 207.9302 | 238.5258 | 273.6276 | 1.546%
8472 | 24-54 | -54.1069 | 24.2258 | 741.3871 | 137.8295 | 174.3622 | 209.2746 | 240.2621 | 275.8423 | 1.605%
8473 | 24-54.5 | -54.3782 | 24.2258 | 731.459 | 139.3542 | 175.3752 | 210.7364 | 242.1543 | 278.2607 | 1.669%
8474 | 24-54.5 | -54.6495 | 24.2258 | 721.8237 | 140.8559 | 176.3788 | 212.1669 | 243.9934 | 280.5984 | 1.735%
8475 | 24-55 | -54.9209 | 24.2258 | 712.4932 | 142.4079 | 177.4214 | 213.6405 | 245.879 | 282.9865 | 1.805%
8476 | 24-55 | -55.1922 | 24.2258 | 703.4797 | 144.0183 | 178.5068 | 215.1596 | 247.812 | 285.4237 | 1.881%
8477 | 24-55.5 | -55.4635 | 24.2258 | 694.7955 | 145.5666 | 179.5364 | 216.5523 | 249.548 | 287.5751 | 1.956%
8478 | 24-55.5 | -55.7348 | 24.2258 | 686.4531 | 147.1198 | 180.5555 | 217.9134 | 251.2311 | 289.6462 | 2.035%
8479 | 24-56 | -56.0061 | 24.2258 | 678.4652 | 148.6783 | 181.5647 | 219.2453 | 252.8654 | 291.644 | 2.116%
8480 | 24-56.5 | -56.2775 | 24.2258 | 670.8445 | 150.1712 | 182.5131 | 220.4657 | 254.3382 | 293.4174 | 2.197%
8481 | 24-56.5 | -56.5488 | 24.2258 | 663.6035 | 151.7004 | 183.4723 | 221.6872 | 255.8018 | 295.1684 | 2.283%
8482 | 24-57 | -56.8201 | 24.2258 | 656.755 | 153.2495 | 184.4322 | 222.8924 | 257.2316 | 296.863 | 2.374%
8483 | 24-57 | -57.0914 | 24.2258 | 650.3113 | 154.7319 | 185.3282 | 223.9757 | 258.4821 | 298.3061 | 2.464%
8484 | 24-57.5 | -57.3628 | 24.2258 | 644.2846 | 156.2446 | 186.2353 | 225.0549 | 259.7125 | 299.7086 | 2.561%
8485 | 24-57.5 | -57.6341 | 24.2258 | 638.6867 | 157.755 | 187.1381 | 226.1058 | 260.89 | 301.0269 | 2.662%
8486 | 24-58 | -57.9054 | 24.2258 | 633.5289 | 159.1727 | 187.9806 | 227.0453 | 261.9058 | 302.12 | 2.761%
8487 | 24-58 | -58.1767 | 24.2258 | 628.8222 | 160.5792 | 188.8576 | 228.0305 | 262.9775 | 303.2816 | 2.865%
8488 | 24-58.5 | -58.448 | 24.2258 | 624.5767 | 161.9343 | 189.7394 | 229.0155 | 264.0438 | 304.4309 | 2.97%
8489 | 24-58.5 | -58.7194 | 24.2258 | 620.802 | 163.1732 | 190.5514 | 229.8862 | 264.9521 | 305.3676 | 3.071%
8490 | 24-59 | -58.9907 | 24.2258 | 617.5066 | 164.4039 | 191.3977 | 230.8213 | 265.9549 | 306.4368 | 3.176%
8491 | 24-59.5 | -59.262 | 24.2258 | 614.6982 | 165.5904 | 192.255 | 231.7855 | 267.0049 | 307.5766 | 3.28%
8492 | 24-59.5 | -59.5333 | 24.2258 | 612.3837 | 166.6885 | 193.0805 | 232.7144 | 268.0172 | 308.676 | 3.381%
8493 | 24-60 | -59.8046 | 24.2258 | 610.5685 | 167.7567 | 193.9335 | 233.6997 | 269.1146 | 309.8969 | 3.482%
8494 | 24-60 | -60.076 | 24.2258 | 609.2573 | 168.7582 | 194.7904 | 234.7075 | 270.2534 | 311.1834 | 3.58%
8495 | 24-60.5 | -60.3473 | 24.2258 | 608.4531 | 169.6634 | 195.6203 | 235.6943 | 271.3782 | 312.4652 | 3.671%
8496 | 24-60.5 | -60.6186 | 24.2258 | 608.1581 | 170.5421 | 196.4927 | 236.7703 | 272.6389 | 313.9419 | 3.76%
8497 | 24-61 | -60.8899 | 24.2258 | 608.373 | 171.3519 | 197.3667 | 237.8728 | 273.9515 | 315.5031 | 3.844%
8498 | 24-61 | -61.1613 | 24.2258 | 609.0972 | 172.0702 | 198.2067 | 238.9479 | 275.2444 | 317.0552 | 3.92%
8499 | 24-61.5 | -61.4326 | 24.2258 | 610.329 | 172.7747 | 199.0771 | 240.0913 | 276.6436 | 318.7617 | 3.993%
8500 | 24-61.5 | -61.7039 | 24.2258 | 612.0652 | 173.4493 | 199.9192 | 241.2104 | 278.0237 | 320.4565 | 4.063%
8501 | 24-62 | -61.9752 | 24.2258 | 614.3016 | 174.0752 | 200.7048 | 242.261 | 279.3244 | 322.0596 | 4.128%
8502 | 24-62 | -62.2465 | 24.2258 | 617.0328 | 174.7133 | 201.525 | 243.386 | 280.7394 | 323.8273 | 4.193%
8503 | 24-62.5 | -62.5179 | 24.2258 | 620.2521 | 175.3215 | 202.3128 | 244.4754 | 282.1166 | 325.555 | 4.255%
8504 | 24-63 | -62.7892 | 24.2258 | 623.9521 | 175.8838 | 203.039 | 245.4764 | 283.3795 | 327.1366 | 4.313%
8505 | 24-63 | -63.0605 | 24.2258 | 628.1242 | 176.4423 | 203.7628 | 246.4778 | 284.6454 | 328.7249 | 4.37%
8506 | 24-63.5 | -63.3318 | 24.2258 | 632.7591 | 176.9587 | 204.4293 | 247.3957 | 285.8029 | 330.1738 | 4.424%
8507 | 24-63.5 | -63.6031 | 24.2258 | 637.8466 | 177.4308 | 205.0342 | 248.2227 | 286.8411 | 331.4684 | 4.474%
8508 | 24-64 | -63.8745 | 24.2258 | 643.3761 | 177.8988 | 205.6341 | 249.0432 | 287.8714 | 332.7538 | 4.523%
8509 | 24-64 | -64.1458 | 24.2258 | 649.3362 | 178.3207 | 206.1699 | 249.7689 | 288.7772 | 333.8782 | 4.569%
8510 | 24-64.5 | -64.4171 | 24.2258 | 655.7152 | 178.7067 | 206.6566 | 250.4234 | 289.5906 | 334.8839 | 4.611%
8511 | 24-64.5 | -64.6884 | 24.2258 | 662.5009 | 179.1017 | 207.1572 | 251.1002 | 290.4346 | 335.9309 | 4.654%
8512 | 24-65 | -64.9598 | 24.2258 | 669.681 | 179.4496 | 207.5872 | 251.6656 | 291.1273 | 336.777 | 4.694%
8513 | 24-65 | -65.2311 | 24.2258 | 677.2429 | 179.7695 | 207.9738 | 252.1609 | 291.7235 | 337.4936 | 4.731%
8514 | 24-65.5 | -65.5024 | 24.2258 | 685.1739 | 180.1095 | 208.386 | 252.6909 | 292.3633 | 338.2646 | 4.771%
8515 | 24-66 | -65.7737 | 24.2258 | 693.4614 | 180.3948 | 208.7115 | 253.0783 | 292.8051 | 338.7685 | 4.808%
8516 | 24-66 | -66.045 | 24.2258 | 702.0928 | 180.6442 | 208.9819 | 253.3771 | 293.1254 | 339.1097 | 4.842%
8517 | 24-66.5 | -66.3164 | 24.2258 | 711.0553 | 180.8967 | 209.2585 | 253.6877 | 293.4631 | 339.4755 | 4.877%
8518 | 24-66.5 | -66.5877 | 24.2258 | 720.3368 | 181.1029 | 209.4757 | 253.917 | 293.6986 | 339.7136 | 4.906%
8519 | 24-67 | -66.859 | 24.2258 | 729.925 | 181.2888 | 209.6719 | 254.1246 | 293.9125 | 339.9305 | 4.933%
8520 | 24-67 | -67.1303 | 24.2258 | 739.8079 | 181.4806 | 209.8837 | 254.3653 | 294.177 | 340.2204 | 4.959%
8521 | 24-67.5 | -67.4016 | 24.2258 | 749.9739 | 181.6149 | 210.026 | 254.5169 | 294.334 | 340.3811 | 4.979%
8522 | 24-67.5 | -67.673 | 24.2258 | 760.4116 | 181.7255 | 210.1486 | 254.6571 | 294.4889 | 340.5516 | 4.994%
8523 | 24-68 | -67.9443 | 24.2258 | 771.1099 | 181.8371 | 210.2874 | 254.8409 | 294.7151 | 340.8292 | 5.007%
8524 | 24-68 | -68.2156 | 24.2258 | 782.0581 | 181.8837 | 210.3417 | 254.9077 | 294.7933 | 340.9207 | 5.013%
8525 | 24-68.5 | -68.4869 | 24.2258 | 793.2458 | 181.9173 | 210.3885 | 254.9772 | 294.885 | 341.0399 | 5.017%
8526 | 24-69 | -68.7583 | 24.2258 | 804.6631 | 181.9638 | 210.466 | 255.1092 | 295.0711 | 341.2941 | 5.019%
8527 | 24-69 | -69.0296 | 24.2258 | 816.3002 | 181.9476 | 210.4603 | 255.1232 | 295.1057 | 341.3554 | 5.015%
8528 | 24-69.5 | -69.3009 | 24.2258 | 828.1479 | 181.9402 | 210.4774 | 255.1851 | 295.2134 | 341.522 | 5.01%
8529 | 24-69.5 | -69.5722 | 24.2258 | 840.1971 | 181.968 | 210.5567 | 255.3569 | 295.4786 | 341.9057 | 5.007%
8530 | 24-70 | -69.8435 | 24.2258 | 852.4395 | 181.9578 | 210.5993 | 255.4961 | 295.7164 | 342.2699 | 4.997%
8531 | 24-70 | -70.1149 | 24.2258 | 864.8666 | 181.9608 | 210.6721 | 255.6959 | 296.0453 | 342.7639 | 4.987%
8532 | 24-70.5 | -70.3862 | 24.2258 | 877.4707 | 181.9877 | 210.7878 | 255.9722 | 296.4846 | 343.4108 | 4.978%
8533 | 24-70.5 | -70.6575 | 24.2258 | 890.2441 | 181.9605 | 210.8257 | 256.1298 | 296.7649 | 343.8488 | 4.965%
8534 | 24-71 | -70.9288 | 24.2258 | 903.1797 | 181.9447 | 210.873 | 256.2924 | 297.0455 | 344.2806 | 4.953%
8535 | 24-71 | -71.2001 | 24.2258 | 916.2705 | 181.946 | 210.9344 | 256.4634 | 297.328 | 344.706 | 4.945%
8536 | 24-71.5 | -71.4715 | 24.2258 | 929.51 | 181.902 | 210.9147 | 256.4897 | 297.4026 | 344.8434 | 4.935%
8537 | 24-71.5 | -71.7428 | 24.2258 | 942.8919 | 181.8763 | 210.9114 | 256.5283 | 297.4846 | 344.9817 | 4.928%
8538 | 24-72 | -72.0141 | 24.2258 | 956.4101 | 181.8715 | 210.928 | 256.584 | 297.5805 | 345.1291 | 4.924%
8539 | 24-72.5 | -72.2854 | 24.2258 | 970.059 | 181.8712 | 210.9353 | 256.6051 | 297.6155 | 345.182 | 4.923%
8540 | 24-72.5 | -72.5568 | 24.2258 | 983.833 | 181.949 | 211.0453 | 256.7709 | 297.8358 | 345.4697 | 4.93%
8541 | 24-73 | -72.8281 | 24.2258 | 997.7269 | 182.0719 | 211.2124 | 257.0134 | 298.1515 | 345.8759 | 4.942%
8542 | 24-73 | -73.0994 | 24.2258 | 1011.7358 | 182.097 | 211.2347 | 257.0296 | 298.1606 | 345.8752 | 4.946%
8543 | 24-73.5 | -73.3707 | 24.2258 | 1025.8549 | 182.0988 | 211.214 | 256.9678 | 298.0569 | 345.7177 | 4.949%
8544 | 24-73.5 | -73.642 | 24.2258 | 1040.0796 | 182.0706 | 211.1414 | 256.8154 | 297.8239 | 345.3825 | 4.952%
8545 | 24-74 | -73.9134 | 24.2258 | 1054.4058 | 181.9996 | 210.9963 | 256.5383 | 297.4144 | 344.8054 | 4.952%
8546 | 24-74 | -74.1847 | 24.2258 | 1068.8292 | 181.9645 | 210.9019 | 256.3372 | 297.1057 | 344.3601 | 4.955%
8547 | 24-74.5 | -74.456 | 24.2258 | 1083.3459 | 181.9385 | 210.8198 | 256.154 | 296.8205 | 343.9452 | 4.959%
8548 | 24-74.5 | -74.7273 | 24.2258 | 1097.9522 | 181.8734 | 210.679 | 255.8784 | 296.4097 | 343.3634 | 4.96%
8549 | 24-75 | -74.9986 | 24.2258 | 1112.6445 | 181.8284 | 210.5713 | 255.6587 | 296.0777 | 342.8892 | 4.962%
8550 | 24-75.5 | -75.27 | 24.2258 | 1127.4195 | 181.7436 | 210.415 | 255.3759 | 295.6689 | 342.3223 | 4.96%
8551 | 24-75.5 | -75.5413 | 24.2258 | 1142.2739 | 181.519 | 210.0728 | 254.8294 | 294.9219 | 341.3253 | 4.943%
8552 | 24-76 | -75.8126 | 24.2258 | 1157.2045 | 181.1693 | 209.5739 | 254.0738 | 293.9164 | 340.0106 | 4.911%
8553 | 24-76 | -76.0839 | 24.2258 | 1172.2084 | 180.7188 | 208.9422 | 253.1315 | 292.6723 | 338.3938 | 4.869%
8554 | 24-76.5 | -76.3553 | 24.2258 | 1187.2829 | 180.2392 | 208.2636 | 252.1107 | 291.3184 | 336.6278 | 4.825%
8555 | 24-76.5 | -76.6266 | 24.2258 | 1202.4252 | 179.8649 | 207.7416 | 251.3206 | 290.2673 | 335.2536 | 4.791%
8556 | 24-77 | -76.8979 | 24.2258 | 1217.6327 | 179.5755 | 207.3366 | 250.7016 | 289.4395 | 334.1672 | 4.765%
8557 | 24-77 | -77.1692 | 24.2258 | 1232.903 | 179.3538 | 207.0126 | 250.2012 | 288.7668 | 333.2808 | 4.746%
8558 | 24-77.5 | -77.4405 | 24.2258 | 1248.2338 | 179.2066 | 206.7979 | 249.8699 | 288.3217 | 332.6946 | 4.734%
8559 | 24-77.5 | -77.7119 | 24.2258 | 1263.6228 | 179.0493 | 206.5716 | 249.5249 | 287.861 | 332.0906 | 4.72%
8560 | 24-78 | -77.9832 | 24.2258 | 1279.0678 | 178.8259 | 206.2573 | 249.0544 | 287.2387 | 331.2808 | 4.699%
8561 | 24-78.5 | -78.2545 | 24.2258 | 1294.5669 | 178.5837 | 205.9371 | 248.5922 | 286.6394 | 330.513 | 4.675%
8562 | 24-78.5 | -78.5258 | 24.2258 | 1310.118 | 178.2601 | 205.5311 | 248.0175 | 285.9027 | 329.5779 | 4.641%
8563 | 24-79 | -78.7971 | 24.2258 | 1325.7193 | 177.8833 | 205.0587 | 247.3565 | 285.0614 | 328.5165 | 4.601%
8564 | 24-79 | -79.0685 | 24.2258 | 1341.369 | 177.5485 | 204.664 | 246.8246 | 284.4 | 327.6985 | 4.564%
8565 | 24-79.5 | -79.3398 | 24.2258 | 1357.0654 | 177.3126 | 204.3902 | 246.4535 | 283.9368 | 327.1239 | 4.539%
8566 | 24-79.5 | -79.6111 | 24.2258 | 1372.8068 | 177.1888 | 204.2398 | 246.2404 | 283.6635 | 326.7769 | 4.526%
8567 | 24-80 | -79.8824 | 24.2258 | 1388.5917 | 177.1362 | 204.1795 | 246.1552 | 283.5544 | 326.6388 | 4.52%
8568 | 24-80 | -80.1537 | 24.2258 | 1404.4185 | 177.1122 | 204.1285 | 246.0713 | 283.4383 | 326.4825 | 4.519%
8569 | 24-80.5 | -80.4251 | 24.2258 | 1420.2858 | 177.1053 | 204.0899 | 245.9915 | 283.3175 | 326.3101 | 4.521%
8570 | 24-80.5 | -80.6964 | 24.2258 | 1436.1923 | 177.1422 | 204.1135 | 245.9899 | 283.2894 | 326.2476 | 4.528%
8571 | 24-81 | -80.9677 | 24.2258 | 1452.1365 | 177.1143 | 204.0415 | 245.8395 | 283.0606 | 325.9198 | 4.529%
8572 | 24-81 | -81.239 | 24.2258 | 1468.1173 | 177.0647 | 203.9391 | 245.6438 | 282.772 | 325.5146 | 4.529%
8573 | 24-81.5 | -81.5104 | 24.2258 | 1484.1333 | 177.079 | 203.9263 | 245.5815 | 282.6596 | 325.3383 | 4.535%
8574 | 24-82 | -81.7817 | 24.2258 | 1500.1835 | 177.1271 | 203.9433 | 245.5513 | 282.5805 | 325.1962 | 4.545%
8575 | 24-82 | -82.053 | 24.2258 | 1516.2667 | 177.2646 | 204.0576 | 245.6505 | 282.6611 | 325.2502 | 4.565%
8576 | 24-82.5 | -82.3243 | 24.2258 | 1532.3818 | 177.5273 | 204.3374 | 245.981 | 283.0358 | 325.6747 | 4.599%
8577 | 24-82.5 | -82.5956 | 24.2258 | 1548.5277 | 177.9004 | 204.7468 | 246.4835 | 283.6221 | 326.3582 | 4.645%
8578 | 24-83 | -82.867 | 24.2258 | 1564.7035 | 178.3245 | 205.2385 | 247.1188 | 284.3904 | 327.2849 | 4.696%
8579 | 24-83 | -83.1383 | 24.2258 | 1580.9083 | 178.7655 | 205.7913 | 247.8756 | 285.3408 | 328.4702 | 4.745%
8580 | 24-83.5 | -83.4096 | 24.2258 | 1597.141 | 179.094 | 206.217 | 248.4774 | 286.1114 | 329.4469 | 4.78%
8581 | 24-83.5 | -83.6809 | 24.2258 | 1613.4008 | 179.3446 | 206.5723 | 249.0122 | 286.8204 | 330.371 | 4.803%
8582 | 24-84 | -83.9522 | 24.2258 | 1629.6869 | 179.5513 | 206.8954 | 249.5379 | 287.545 | 331.3432 | 4.818%
8583 | 24-84 | -84.2236 | 24.2258 | 1645.9984 | 179.65 | 207.0939 | 249.9127 | 288.0953 | 332.1141 | 4.819%
8584 | 24-84.5 | -84.4949 | 24.2258 | 1662.3345 | 179.7541 | 207.3183 | 250.3505 | 288.7461 | 333.0332 | 4.817%
8585 | 24-85 | -84.7662 | 24.2258 | 1678.6945 | 179.9053 | 207.6237 | 250.9291 | 289.597 | 334.2268 | 4.818%
8586 | 24-85 | -85.0375 | 24.2258 | 1695.0775 | 180.0042 | 207.8638 | 251.4208 | 290.3405 | 335.2885 | 4.813%
8587 | 24-85.5 | -85.3089 | 24.2258 | 1711.483 | 180.0828 | 208.0893 | 251.9091 | 291.0927 | 336.3746 | 4.804%
8588 | 24-85.5 | -85.5802 | 24.2258 | 1727.9103 | 180.1452 | 208.3081 | 252.4085 | 291.8748 | 337.5151 | 4.792%
8589 | 24-86 | -85.8515 | 24.2258 | 1744.3586 | 180.1019 | 208.3911 | 252.722 | 292.4231 | 338.3637 | 4.768%
8590 | 24-86 | -86.1228 | 24.2258 | 1760.8273 | 179.974 | 208.3697 | 252.8986 | 292.8045 | 339.0095 | 4.735%
8591 | 24-86.5 | -86.3941 | 24.2258 | 1777.3159 | 179.7551 | 208.2346 | 252.9242 | 292.9999 | 339.4275 | 4.692%
8592 | 24-86.5 | -86.6655 | 24.2258 | 1793.8237 | 179.3636 | 207.8758 | 252.6403 | 292.8043 | 339.3551 | 4.632%
8593 | 24-87 | -86.9368 | 24.2258 | 1810.3501 | 178.9336 | 207.4798 | 252.3234 | 292.5811 | 339.2635 | 4.568%
8594 | 24-87 | -87.2081 | 24.2258 | 1826.8947 | 178.4693 | 207.0504 | 251.9767 | 292.333 | 339.1543 | 4.5%
8595 | 24-87.5 | -87.4794 | 24.2258 | 1843.4568 | 177.8951 | 206.4701 | 251.4084 | 291.7947 | 338.6703 | 4.423%
8596 | 24-88 | -87.7507 | 24.2258 | 1860.0359 | 177.2702 | 205.8283 | 250.7612 | 291.1613 | 338.0717 | 4.342%
8597 | 24-88 | -88.0221 | 24.2258 | 1876.6316 | 176.5887 | 205.1169 | 250.0234 | 290.4178 | 337.3398 | 4.256%
8598 | 24-88.5 | -88.2934 | 24.2258 | 1893.2434 | 175.7967 | 204.2675 | 249.0834 | 289.4099 | 336.2666 | 4.163%
8599 | 24-88.5 | -88.5647 | 24.2258 | 1909.8708 | 174.9817 | 203.4174 | 248.156 | 288.4282 | 335.2373 | 4.069%
8600 | 24-89 | -88.836 | 24.2258 | 1926.5134 | 174.1328 | 202.5495 | 247.2088 | 287.4256 | 334.1862 | 3.973%
8601 | 24-89 | -89.1074 | 24.2258 | 1943.1706 | 173.2068 | 201.5962 | 246.1209 | 286.227 | 332.8697 | 3.875%
8602 | 24-89.5 | -89.3787 | 24.2258 | 1959.8422 | 172.2899 | 200.6756 | 245.0717 | 285.0726 | 331.6035 | 3.78%
8603 | 24-89.5 | -89.65 | 24.2258 | 1976.5276 | 171.3647 | 199.7592 | 244.0156 | 283.8995 | 330.3035 | 3.687%
8604 | 24-90 | -89.9213 | 24.2258 | 1993.2265 | 170.387 | 198.7871 | 242.8539 | 282.5705 | 328.7836 | 3.594%
8605 | 24-90 | -90.1926 | 24.2258 | 2009.9385 | 169.4374 | 197.8598 | 241.7295 | 281.2697 | 327.2788 | 3.507%
8606 | 24-90.5 | -90.464 | 24.2258 | 2026.6633 | 168.4933 | 196.9473 | 240.5992 | 279.9412 | 325.7173 | 3.423%
8607 | 24-90.5 | -90.7353 | 24.2258 | 2043.4004 | 167.5111 | 196.0081 | 239.4088 | 278.5182 | 324.0178 | 3.34%
8608 | 24-50 | -50.0371 | 24.4972 | 930.3786 | 114.7287 | 151.3402 | 189.1911 | 215.4883 | 245.4445 | 0.8405%
8609 | 24-50.5 | -50.3084 | 24.4972 | 917.4609 | 116.4861 | 153.74 | 190.7543 | 217.338 | 247.6299 | 0.8856%
8610 | 24-50.5 | -50.5797 | 24.4972 | 904.7003 | 118.1883 | 156.0161 | 192.2353 | 219.0808 | 249.6786 | 0.9313%
8611 | 24-51 | -50.851 | 24.4972 | 892.1035 | 119.8442 | 158.1644 | 193.65 | 220.7493 | 251.6439 | 0.9778%
8612 | 24-51 | -51.1224 | 24.4972 | 879.6777 | 121.481 | 160.1886 | 195.0354 | 222.3995 | 253.6058 | 1.026%
8613 | 24-51.5 | -51.3937 | 24.4972 | 867.4302 | 123.0322 | 162.0219 | 196.3208 | 223.9321 | 255.4298 | 1.073%
8614 | 24-51.5 | -51.665 | 24.4972 | 855.3687 | 124.5267 | 163.6961 | 197.5545 | 225.4223 | 257.2243 | 1.12%
8615 | 24-52 | -51.9363 | 24.4972 | 843.5012 | 125.9931 | 165.2307 | 198.7807 | 226.9342 | 259.0785 | 1.167%
8616 | 24-52 | -52.2077 | 24.4972 | 831.8361 | 127.3726 | 166.562 | 199.9129 | 228.3312 | 260.7927 | 1.213%
8617 | 24-52.5 | -52.479 | 24.4972 | 820.382 | 128.7278 | 167.7732 | 201.0334 | 229.7257 | 262.5166 | 1.26%
8618 | 24-53 | -52.7503 | 24.4972 | 809.1479 | 130.1003 | 168.9111 | 202.1958 | 231.19 | 264.3456 | 1.308%
8619 | 24-53 | -53.0216 | 24.4972 | 798.1432 | 131.3979 | 169.9028 | 203.2929 | 232.573 | 266.0742 | 1.354%
8620 | 24-53.5 | -53.2929 | 24.4972 | 787.3774 | 132.703 | 170.8507 | 204.4252 | 234.0122 | 267.8856 | 1.402%
8621 | 24-53.5 | -53.5643 | 24.4972 | 776.8606 | 134.059 | 171.7949 | 205.642 | 235.5728 | 269.8643 | 1.453%
8622 | 24-54 | -53.8356 | 24.4972 | 766.6031 | 135.3772 | 172.6654 | 206.8396 | 237.111 | 271.8172 | 1.504%
8623 | 24-54 | -54.1069 | 24.4972 | 756.6153 | 136.7561 | 173.5723 | 208.1276 | 238.7733 | 273.9362 | 1.559%
8624 | 24-54.5 | -54.3782 | 24.4972 | 746.9082 | 138.2279 | 174.5495 | 209.5392 | 240.6013 | 276.2731 | 1.62%
8625 | 24-54.5 | -54.6495 | 24.4972 | 737.4928 | 139.6795 | 175.5205 | 210.9252 | 242.3844 | 278.5408 | 1.682%
8626 | 24-55 | -54.9209 | 24.4972 | 728.3805 | 141.1897 | 176.5382 | 212.3666 | 244.2308 | 280.8811 | 1.749%
8627 | 24-55 | -55.1922 | 24.4972 | 719.5829 | 142.7692 | 177.6082 | 213.8682 | 246.1445 | 283.2969 | 1.821%
8628 | 24-55.5 | -55.4635 | 24.4972 | 711.1116 | 144.3006 | 178.6343 | 215.2614 | 247.8849 | 285.4577 | 1.894%
8629 | 24-55.5 | -55.7348 | 24.4972 | 702.9784 | 145.8515 | 179.6618 | 216.6416 | 249.5976 | 287.5717 | 1.97%
8630 | 24-56 | -56.0061 | 24.4972 | 695.1953 | 147.4219 | 180.6905 | 218.0097 | 251.2847 | 289.6427 | 2.05%
8631 | 24-56.5 | -56.2775 | 24.4972 | 687.7741 | 148.9334 | 181.6634 | 219.2729 | 252.8182 | 291.4992 | 2.13%
8632 | 24-56.5 | -56.5488 | 24.4972 | 680.7268 | 150.488 | 182.6519 | 220.5446 | 254.3525 | 293.3461 | 2.215%
8633 | 24-57 | -56.8201 | 24.4972 | 674.065 | 152.0737 | 183.6465 | 221.8084 | 255.8644 | 295.152 | 2.305%
8634 | 24-57 | -57.0914 | 24.4972 | 667.8003 | 153.6081 | 184.5851 | 222.9626 | 257.2133 | 296.7278 | 2.397%
8635 | 24-57.5 | -57.3628 | 24.4972 | 661.944 | 155.1879 | 185.5405 | 224.1201 | 258.5514 | 298.2742 | 2.494%
8636 | 24-57.5 | -57.6341 | 24.4972 | 656.5071 | 156.7789 | 186.4951 | 225.2526 | 259.8395 | 299.7389 | 2.598%
8637 | 24-58 | -57.9054 | 24.4972 | 651.5 | 158.282 | 187.3875 | 226.2675 | 260.9552 | 300.9622 | 2.7%
8638 | 24-58 | -58.1767 | 24.4972 | 646.9327 | 159.7735 | 188.3117 | 227.3218 | 262.1171 | 302.2399 | 2.807%
8639 | 24-58.5 | -58.448 | 24.4972 | 642.8147 | 161.2101 | 189.2361 | 228.3665 | 263.2595 | 303.4851 | 2.916%
8640 | 24-58.5 | -58.7194 | 24.4972 | 639.1547 | 162.5237 | 190.0828 | 229.2829 | 264.2237 | 304.4901 | 3.021%
8641 | 24-59 | -58.9907 | 24.4972 | 635.9604 | 163.8194 | 190.9536 | 230.2471 | 265.2596 | 305.5971 | 3.128%
8642 | 24-59.5 | -59.262 | 24.4972 | 633.2391 | 165.0603 | 191.8255 | 231.2244 | 266.3209 | 306.7452 | 3.236%
8643 | 24-59.5 | -59.5333 | 24.4972 | 630.9969 | 166.2034 | 192.6572 | 232.1532 | 267.3263 | 307.8289 | 3.339%
8644 | 24-60 | -59.8046 | 24.4972 | 629.2388 | 167.3148 | 193.5146 | 233.136 | 268.4141 | 309.031 | 3.443%
8645 | 24-60 | -60.076 | 24.4972 | 627.9689 | 168.358 | 194.3745 | 234.1395 | 269.5411 | 310.296 | 3.543%
8646 | 24-60.5 | -60.3473 | 24.4972 | 627.1902 | 169.3002 | 195.2069 | 235.1206 | 270.6519 | 311.5532 | 3.637%
8647 | 24-60.5 | -60.6186 | 24.4972 | 626.9046 | 170.207 | 196.0788 | 236.1869 | 271.8932 | 312.9981 | 3.729%
8648 | 24-61 | -60.8899 | 24.4972 | 627.1126 | 171.0347 | 196.9505 | 237.2773 | 273.1837 | 314.5245 | 3.815%
8649 | 24-61 | -61.1613 | 24.4972 | 627.8139 | 171.7618 | 197.7889 | 238.3422 | 274.4577 | 316.0466 | 3.891%
8650 | 24-61.5 | -61.4326 | 24.4972 | 629.0068 | 172.4741 | 198.6637 | 239.4858 | 275.8529 | 317.7436 | 3.966%
8651 | 24-61.5 | -61.7039 | 24.4972 | 630.6884 | 173.1584 | 199.5158 | 240.6154 | 277.2434 | 319.4485 | 4.037%
8652 | 24-62 | -61.9752 | 24.4972 | 632.8549 | 173.7979 | 200.3179 | 241.6871 | 278.5696 | 321.082 | 4.103%
8653 | 24-62 | -62.2465 | 24.4972 | 635.5013 | 174.4561 | 201.1638 | 242.847 | 280.0285 | 322.9044 | 4.17%
8654 | 24-62.5 | -62.5179 | 24.4972 | 638.6216 | 175.0905 | 201.9855 | 243.983 | 281.4642 | 324.7052 | 4.235%
8655 | 24-63 | -62.7892 | 24.4972 | 642.209 | 175.6847 | 202.7524 | 245.0397 | 282.7968 | 326.3736 | 4.296%
8656 | 24-63 | -63.0605 | 24.4972 | 646.2556 | 176.2802 | 203.5234 | 246.1049 | 284.1425 | 328.0608 | 4.357%
8657 | 24-63.5 | -63.3318 | 24.4972 | 650.7528 | 176.8363 | 204.24 | 247.0903 | 285.3838 | 329.6132 | 4.415%
8658 | 24-63.5 | -63.6031 | 24.4972 | 655.6914 | 177.3486 | 204.8954 | 247.9848 | 286.5054 | 331.0106 | 4.469%
8659 | 24-64 | -63.8745 | 24.4972 | 661.0615 | 177.8564 | 205.5452 | 248.872 | 287.6181 | 332.3972 | 4.523%
8660 | 24-64 | -64.1458 | 24.4972 | 666.8526 | 178.317 | 206.1301 | 249.6642 | 288.6068 | 333.6244 | 4.573%
8661 | 24-64.5 | -64.4171 | 24.4972 | 673.0538 | 178.7404 | 206.6651 | 250.385 | 289.5036 | 334.7343 | 4.619%
8662 | 24-64.5 | -64.6884 | 24.4972 | 679.654 | 179.1714 | 207.2126 | 251.1269 | 290.4302 | 335.8851 | 4.666%
8663 | 24-65 | -64.9598 | 24.4972 | 686.6415 | 179.5536 | 207.6871 | 251.754 | 291.201 | 336.8292 | 4.709%
8664 | 24-65 | -65.2311 | 24.4972 | 694.0047 | 179.9064 | 208.116 | 252.3073 | 291.8703 | 337.6373 | 4.751%
8665 | 24-65.5 | -65.5024 | 24.4972 | 701.7317 | 180.2783 | 208.5689 | 252.893 | 292.5799 | 338.4954 | 4.794%
8666 | 24-66 | -65.7737 | 24.4972 | 709.8107 | 180.5933 | 208.9318 | 253.3305 | 293.0838 | 339.0759 | 4.835%
8667 | 24-66 | -66.045 | 24.4972 | 718.2296 | 180.8703 | 209.2365 | 253.6746 | 293.4597 | 339.4852 | 4.872%
8668 | 24-66.5 | -66.3164 | 24.4972 | 726.9768 | 181.1486 | 209.5449 | 254.0268 | 293.8484 | 339.9131 | 4.91%
8669 | 24-66.5 | -66.5877 | 24.4972 | 736.0404 | 181.3751 | 209.7864 | 254.2868 | 294.1206 | 340.1948 | 4.942%
8670 | 24-67 | -66.859 | 24.4972 | 745.4089 | 181.5776 | 210.0012 | 254.5162 | 294.3588 | 340.4391 | 4.971%
8671 | 24-67 | -67.1303 | 24.4972 | 755.0709 | 181.7838 | 210.2279 | 254.7723 | 294.6386 | 340.7439 | 5%
8672 | 24-67.5 | -67.4016 | 24.4972 | 765.0153 | 181.9307 | 210.3827 | 254.9356 | 294.8062 | 340.9131 | 5.022%
8673 | 24-67.5 | -67.673 | 24.4972 | 775.2311 | 182.053 | 210.5156 | 255.0829 | 294.9647 | 341.0826 | 5.039%
8674 | 24-68 | -67.9443 | 24.4972 | 785.7079 | 182.1755 | 210.662 | 255.2682 | 295.1857 | 341.346 | 5.054%
8675 | 24-68 | -68.2156 | 24.4972 | 796.4352 | 182.2316 | 210.7218 | 255.3324 | 295.2527 | 341.4153 | 5.063%
8676 | 24-68.5 | -68.4869 | 24.4972 | 807.403 | 182.2738 | 210.7725 | 255.3967 | 295.3297 | 341.5074 | 5.068%
8677 | 24-69 | -68.7583 | 24.4972 | 818.6016 | 182.3281 | 210.8524 | 255.5211 | 295.4977 | 341.7297 | 5.073%
8678 | 24-69 | -69.0296 | 24.4972 | 830.0218 | 182.3159 | 210.8441 | 255.5204 | 295.5052 | 341.7478 | 5.07%
8679 | 24-69.5 | -69.3009 | 24.4972 | 841.6543 | 182.31 | 210.8558 | 255.5643 | 295.582 | 341.867 | 5.066%
8680 | 24-69.5 | -69.5722 | 24.4972 | 853.4905 | 182.3376 | 210.9281 | 255.7168 | 295.8153 | 342.2027 | 5.064%
8681 | 24-70 | -69.8435 | 24.4972 | 865.5221 | 182.3232 | 210.9581 | 255.8282 | 296.0099 | 342.5039 | 5.055%
8682 | 24-70 | -70.1149 | 24.4972 | 877.7409 | 182.322 | 211.0179 | 255.9987 | 296.2931 | 342.9312 | 5.045%
8683 | 24-70.5 | -70.3862 | 24.4972 | 890.1392 | 182.3463 | 211.1219 | 256.2469 | 296.6873 | 343.5113 | 5.037%
8684 | 24-70.5 | -70.6575 | 24.4972 | 902.7095 | 182.3192 | 211.1534 | 256.3859 | 296.9366 | 343.9022 | 5.024%
8685 | 24-71 | -70.9288 | 24.4972 | 915.4449 | 182.3065 | 211.1986 | 256.537 | 297.1958 | 344.3 | 5.014%
8686 | 24-71 | -71.2001 | 24.4972 | 928.3384 | 182.3137 | 211.2622 | 256.703 | 297.4659 | 344.7029 | 5.006%
8687 | 24-71.5 | -71.4715 | 24.4972 | 941.3834 | 182.2788 | 211.2494 | 256.732 | 297.5385 | 344.8324 | 4.998%
8688 | 24-71.5 | -71.7428 | 24.4972 | 954.5739 | 182.2657 | 211.2573 | 256.7786 | 297.625 | 344.9703 | 4.993%
8689 | 24-72 | -72.0141 | 24.4972 | 967.9037 | 182.2768 | 211.2893 | 256.8481 | 297.7325 | 345.1261 | 4.991%
8690 | 24-72.5 | -72.2854 | 24.4972 | 981.3672 | 182.294 | 211.315 | 256.8888 | 297.7878 | 345.1997 | 4.993%
8691 | 24-72.5 | -72.5568 | 24.4972 | 994.9588 | 182.3937 | 211.4501 | 257.0844 | 298.0421 | 345.5263 | 5.003%
8692 | 24-73 | -72.8281 | 24.4972 | 1008.6735 | 182.542 | 211.6471 | 257.3642 | 298.4018 | 345.9843 | 5.018%
8693 | 24-73 | -73.0994 | 24.4972 | 1022.5061 | 182.5924 | 211.6989 | 257.4163 | 298.4528 | 346.0324 | 5.025%
8694 | 24-73.5 | -73.3707 | 24.4972 | 1036.452 | 182.6216 | 211.7109 | 257.3959 | 298.3985 | 345.934 | 5.032%
8695 | 24-73.5 | -73.642 | 24.4972 | 1050.5066 | 182.6219 | 211.6732 | 257.2892 | 298.2216 | 345.6673 | 5.038%
8696 | 24-74 | -73.9134 | 24.4972 | 1064.6656 | 182.5782 | 211.5631 | 257.0598 | 297.872 | 345.1654 | 5.041%
8697 | 24-74 | -74.1847 | 24.4972 | 1078.9247 | 182.5686 | 211.4997 | 256.8993 | 297.613 | 344.7809 | 5.048%
8698 | 24-74.5 | -74.456 | 24.4972 | 1093.2801 | 182.5656 | 211.4444 | 256.7493 | 297.3667 | 344.4117 | 5.055%
8699 | 24-74.5 | -74.7273 | 24.4972 | 1107.7279 | 182.5204 | 211.3259 | 256.4995 | 296.985 | 343.8627 | 5.059%
8700 | 24-75 | -74.9986 | 24.4972 | 1122.2646 | 182.4921 | 211.2353 | 256.297 | 296.6698 | 343.4048 | 5.064%
8701 | 24-75.5 | -75.27 | 24.4972 | 1136.8867 | 182.4201 | 211.0904 | 256.0229 | 296.267 | 342.8398 | 5.064%
8702 | 24-75.5 | -75.5413 | 24.4972 | 1151.5909 | 182.2028 | 210.7532 | 255.4769 | 295.5156 | 341.8325 | 5.048%
8703 | 24-76 | -75.8126 | 24.4972 | 1166.3741 | 181.8565 | 210.2535 | 254.7129 | 294.494 | 340.4918 | 5.018%
8704 | 24-76 | -76.0839 | 24.4972 | 1181.2333 | 181.4147 | 209.6282 | 253.7726 | 293.2472 | 338.8662 | 4.977%
8705 | 24-76.5 | -76.3553 | 24.4972 | 1196.1656 | 180.9632 | 208.9825 | 252.7924 | 291.9412 | 337.1565 | 4.936%
8706 | 24-76.5 | -76.6266 | 24.4972 | 1211.1682 | 180.6472 | 208.5239 | 252.0879 | 290.9966 | 335.9144 | 4.908%
8707 | 24-77 | -76.8979 | 24.4972 | 1226.2385 | 180.4133 | 208.1801 | 251.5542 | 290.2774 | 334.965 | 4.888%
8708 | 24-77 | -77.1692 | 24.4972 | 1241.3741 | 180.2068 | 207.8782 | 251.0877 | 289.6501 | 334.1385 | 4.871%
8709 | 24-77.5 | -77.4405 | 24.4972 | 1256.5725 | 180.0443 | 207.6472 | 250.7391 | 289.1872 | 333.5342 | 4.856%
8710 | 24-77.5 | -77.7119 | 24.4972 | 1271.8314 | 179.8686 | 207.4028 | 250.3771 | 288.7113 | 332.9179 | 4.839%
8711 | 24-78 | -77.9832 | 24.4972 | 1287.1487 | 179.6504 | 207.1031 | 249.9385 | 288.1383 | 332.1794 | 4.817%
8712 | 24-78.5 | -78.2545 | 24.4972 | 1302.5222 | 179.4428 | 206.8305 | 249.556 | 287.6503 | 331.5624 | 4.795%
8713 | 24-78.5 | -78.5258 | 24.4972 | 1317.9499 | 179.1553 | 206.4603 | 249.047 | 287.009 | 330.7599 | 4.763%
8714 | 24-79 | -78.7971 | 24.4972 | 1333.4299 | 178.778 | 205.9787 | 248.3914 | 286.1884 | 329.7393 | 4.721%
8715 | 24-79 | -79.0685 | 24.4972 | 1348.9604 | 178.3921 | 205.5312 | 247.806 | 285.4743 | 328.8713 | 4.676%
8716 | 24-79.5 | -79.3398 | 24.4972 | 1364.5396 | 178.0918 | 205.1971 | 247.3714 | 284.9464 | 328.232 | 4.641%
8717 | 24-79.5 | -79.6111 | 24.4972 | 1380.1658 | 177.9167 | 204.9879 | 247.0957 | 284.6084 | 327.8192 | 4.62%
8718 | 24-80 | -79.8824 | 24.4972 | 1395.8374 | 177.8038 | 204.8521 | 246.9229 | 284.4015 | 327.5719 | 4.607%
8719 | 24-80 | -80.1537 | 24.4972 | 1411.5528 | 177.6748 | 204.6864 | 246.6958 | 284.1163 | 327.2162 | 4.593%
8720 | 24-80.5 | -80.4251 | 24.4972 | 1427.3106 | 177.5489 | 204.5147 | 246.4465 | 283.7922 | 326.8004 | 4.58%
8721 | 24-80.5 | -80.6964 | 24.4972 | 1443.1093 | 177.4903 | 204.4243 | 246.3011 | 283.5929 | 326.5342 | 4.576%
8722 | 24-81 | -80.9677 | 24.4972 | 1458.9475 | 177.4129 | 204.2974 | 246.0878 | 283.2947 | 326.1301 | 4.571%
8723 | 24-81 | -81.239 | 24.4972 | 1474.8239 | 177.3438 | 204.178 | 245.8803 | 283.0002 | 325.7269 | 4.567%
8724 | 24-81.5 | -81.5104 | 24.4972 | 1490.7373 | 177.342 | 204.1514 | 245.8089 | 282.8836 | 325.5531 | 4.57%
8725 | 24-82 | -81.7817 | 24.4972 | 1506.6864 | 177.3514 | 204.1323 | 245.7382 | 282.7606 | 325.3636 | 4.576%
8726 | 24-82 | -82.053 | 24.4972 | 1522.6701 | 177.4499 | 204.2257 | 245.8189 | 282.8257 | 325.4063 | 4.591%
8727 | 24-82.5 | -82.3243 | 24.4972 | 1538.6872 | 177.7126 | 204.5346 | 246.201 | 283.2741 | 325.9319 | 4.624%
8728 | 24-82.5 | -82.5956 | 24.4972 | 1554.7368 | 178.1109 | 204.9849 | 246.7712 | 283.954 | 326.7413 | 4.672%
8729 | 24-83 | -82.867 | 24.4972 | 1570.8176 | 178.5425 | 205.4855 | 247.4305 | 284.7614 | 327.7261 | 4.723%
8730 | 24-83 | -83.1383 | 24.4972 | 1586.9288 | 178.9379 | 205.9938 | 248.1389 | 285.6607 | 328.8576 | 4.766%
8731 | 24-83.5 | -83.4096 | 24.4972 | 1603.0694 | 179.2051 | 206.3574 | 248.6662 | 286.3456 | 329.7358 | 4.793%
8732 | 24-83.5 | -83.6809 | 24.4972 | 1619.2385 | 179.4113 | 206.6618 | 249.14 | 286.9845 | 330.5792 | 4.81%
8733 | 24-84 | -83.9522 | 24.4972 | 1635.4351 | 179.5926 | 206.9576 | 249.6353 | 287.6763 | 331.5159 | 4.821%
8734 | 24-84 | -84.2236 | 24.4972 | 1651.6584 | 179.688 | 207.1552 | 250.0139 | 288.2351 | 332.3015 | 4.821%
8735 | 24-84.5 | -84.4949 | 24.4972 | 1667.9076 | 179.7803 | 207.3665 | 250.4367 | 288.8692 | 333.2018 | 4.818%
8736 | 24-85 | -84.7662 | 24.4972 | 1684.1819 | 179.8995 | 207.6313 | 250.9603 | 289.6512 | 334.3097 | 4.815%
8737 | 24-85 | -85.0375 | 24.4972 | 1700.4805 | 179.946 | 207.8034 | 251.3577 | 290.2755 | 335.2216 | 4.805%
8738 | 24-85.5 | -85.3089 | 24.4972 | 1716.8027 | 179.9719 | 207.9587 | 251.7461 | 290.8994 | 336.1446 | 4.79%
8739 | 24-85.5 | -85.5802 | 24.4972 | 1733.1478 | 179.9867 | 208.1113 | 252.1477 | 291.553 | 337.119 | 4.774%
8740 | 24-86 | -85.8515 | 24.4972 | 1749.5151 | 179.8996 | 208.1296 | 252.3605 | 291.9656 | 337.7885 | 4.746%
8741 | 24-86 | -86.1228 | 24.4972 | 1765.9039 | 179.7603 | 208.0825 | 252.4856 | 292.2697 | 338.3244 | 4.714%
8742 | 24-86.5 | -86.3941 | 24.4972 | 1782.3136 | 179.5686 | 207.9681 | 252.519 | 292.459 | 338.7178 | 4.676%
8743 | 24-86.5 | -86.6655 | 24.4972 | 1798.7435 | 179.2402 | 207.6739 | 252.3002 | 292.3268 | 338.7049 | 4.625%
8744 | 24-87 | -86.9368 | 24.4972 | 1815.1931 | 178.8802 | 207.3512 | 252.0594 | 292.1805 | 338.689 | 4.57%
8745 | 24-87 | -87.2081 | 24.4972 | 1831.6618 | 178.489 | 206.9985 | 251.793 | 292.0139 | 338.6608 | 4.511%
8746 | 24-87.5 | -87.4794 | 24.4972 | 1848.1491 | 177.989 | 206.4971 | 251.3091 | 291.563 | 338.266 | 4.443%
8747 | 24-88 | -87.7507 | 24.4972 | 1864.6543 | 177.4374 | 205.9338 | 250.7467 | 291.0186 | 337.7596 | 4.371%
8748 | 24-88 | -88.0221 | 24.4972 | 1881.177 | 176.8277 | 205.3 | 250.0938 | 290.3652 | 337.1223 | 4.293%
8749 | 24-88.5 | -88.2934 | 24.4972 | 1897.7167 | 176.1114 | 204.5272 | 249.2416 | 289.4541 | 336.1555 | 4.207%
8750 | 24-88.5 | -88.5647 | 24.4972 | 1914.2729 | 175.3759 | 203.7536 | 248.4056 | 288.5771 | 335.246 | 4.12%
8751 | 24-89 | -88.836 | 24.4972 | 1930.8451 | 174.6096 | 202.9621 | 247.5542 | 287.6878 | 334.329 | 4.032%
8752 | 24-89 | -89.1074 | 24.4972 | 1947.4328 | 173.7672 | 202.0822 | 246.5615 | 286.6051 | 333.153 | 3.94%
8753 | 24-89.5 | -89.3787 | 24.4972 | 1964.0356 | 172.9347 | 201.2335 | 245.6097 | 285.5721 | 332.0378 | 3.85%
8754 | 24-89.5 | -89.65 | 24.4972 | 1980.6532 | 172.0935 | 200.3865 | 244.6512 | 284.524 | 330.8962 | 3.763%
8755 | 24-90 | -89.9213 | 24.4972 | 1997.285 | 171.1982 | 199.4792 | 243.5839 | 283.3182 | 329.535 | 3.675%
8756 | 24-90 | -90.1926 | 24.4972 | 2013.9306 | 170.331 | 198.6146 | 242.5525 | 282.14 | 328.1898 | 3.592%
8757 | 24-90.5 | -90.464 | 24.4972 | 2030.5898 | 169.468 | 197.761 | 241.5109 | 280.9293 | 326.7824 | 3.512%
8758 | 24-90.5 | -90.7353 | 24.4972 | 2047.262 | 168.5647 | 196.8737 | 240.3992 | 279.6114 | 325.2207 | 3.433%
8759 | 25-50 | -50.0371 | 24.7685 | 942.6309 | 113.8853 | 150.0853 | 188.2554 | 214.2682 | 243.8792 | 0.8177%
8760 | 25-50.5 | -50.3084 | 24.7685 | 929.9081 | 115.6472 | 152.5189 | 189.8291 | 216.1331 | 246.0858 | 0.8619%
8761 | 25-50.5 | -50.5797 | 24.7685 | 917.345 | 117.3612 | 154.8447 | 191.3277 | 217.8991 | 248.1645 | 0.9069%
8762 | 25-51 | -50.851 | 24.7685 | 904.9483 | 119.035 | 157.0556 | 192.7658 | 219.5978 | 250.1683 | 0.9529%
8763 | 25-51 | -51.1224 | 24.7685 | 892.725 | 120.6955 | 159.15 | 194.1806 | 221.2867 | 252.1803 | 1.001%
8764 | 25-51.5 | -51.3937 | 24.7685 | 880.6823 | 122.2704 | 161.0569 | 195.4947 | 222.8576 | 254.0539 | 1.048%
8765 | 25-51.5 | -51.665 | 24.7685 | 868.8278 | 123.7858 | 162.8049 | 196.7534 | 224.3813 | 255.8922 | 1.095%
8766 | 25-52 | -51.9363 | 24.7685 | 857.1693 | 125.2689 | 164.4115 | 198 | 225.9207 | 257.7826 | 1.142%
8767 | 25-52 | -52.2077 | 24.7685 | 845.7149 | 126.6598 | 165.8124 | 199.145 | 227.334 | 259.5173 | 1.188%
8768 | 25-52.5 | -52.479 | 24.7685 | 834.4731 | 128.0176 | 167.0849 | 200.2678 | 228.7313 | 261.2443 | 1.234%
8769 | 25-53 | -52.7503 | 24.7685 | 823.4527 | 129.382 | 168.2671 | 201.4214 | 230.1848 | 263.06 | 1.281%
8770 | 25-53 | -53.0216 | 24.7685 | 812.6626 | 130.6633 | 169.286 | 202.4992 | 231.5429 | 264.7567 | 1.326%
8771 | 25-53.5 | -53.2929 | 24.7685 | 802.1122 | 131.9422 | 170.2447 | 203.6006 | 232.9417 | 266.5157 | 1.373%
8772 | 25-53.5 | -53.5643 | 24.7685 | 791.8111 | 133.2616 | 171.1828 | 204.7746 | 234.4457 | 268.4209 | 1.422%
8773 | 25-54 | -53.8356 | 24.7685 | 781.7691 | 134.5338 | 172.0292 | 205.9183 | 235.9121 | 270.2798 | 1.47%
8774 | 25-54 | -54.1069 | 24.7685 | 771.9965 | 135.8617 | 172.9029 | 207.1486 | 237.4976 | 272.2982 | 1.522%
8775 | 25-54.5 | -54.3782 | 24.7685 | 762.5036 | 137.2796 | 173.8409 | 208.5018 | 239.2486 | 274.535 | 1.58%
8776 | 25-54.5 | -54.6495 | 24.7685 | 753.3009 | 138.6767 | 174.7734 | 209.8302 | 240.9555 | 276.7035 | 1.638%
8777 | 25-55 | -54.9209 | 24.7685 | 744.3994 | 140.1391 | 175.7587 | 211.2236 | 242.7387 | 278.9617 | 1.701%
8778 | 25-55 | -55.1922 | 24.7685 | 735.8099 | 141.6797 | 176.8045 | 212.6902 | 244.6066 | 281.3185 | 1.77%
8779 | 25-55.5 | -55.4635 | 24.7685 | 727.5436 | 143.185 | 177.8174 | 214.0642 | 246.3221 | 283.447 | 1.84%
8780 | 25-55.5 | -55.7348 | 24.7685 | 719.6115 | 144.725 | 178.8443 | 215.4454 | 248.0374 | 285.5655 | 1.914%
8781 | 25-56 | -56.0061 | 24.7685 | 712.0249 | 146.2998 | 179.8849 | 216.8342 | 249.7537 | 287.6764 | 1.993%
8782 | 25-56.5 | -56.2775 | 24.7685 | 704.7949 | 147.8244 | 180.8763 | 218.1265 | 251.3267 | 289.585 | 2.071%
8783 | 25-56.5 | -56.5488 | 24.7685 | 697.9327 | 149.3989 | 181.8882 | 219.4361 | 252.9129 | 291.5013 | 2.156%
8784 | 25-57 | -56.8201 | 24.7685 | 691.4492 | 151.0122 | 182.9117 | 220.7477 | 254.4909 | 293.3959 | 2.246%
8785 | 25-57 | -57.0914 | 24.7685 | 685.3552 | 152.5863 | 183.887 | 221.9621 | 255.923 | 295.0833 | 2.337%
8786 | 25-57.5 | -57.3628 | 24.7685 | 679.6611 | 154.222 | 184.8866 | 223.1922 | 257.3614 | 296.7643 | 2.436%
8787 | 25-57.5 | -57.6341 | 24.7685 | 674.3772 | 155.8842 | 185.8911 | 224.4061 | 258.7616 | 298.3792 | 2.541%
8788 | 25-58 | -57.9054 | 24.7685 | 669.5132 | 157.4652 | 186.8336 | 225.5014 | 259.9874 | 299.7494 | 2.646%
8789 | 25-58 | -58.1767 | 24.7685 | 665.0782 | 159.036 | 187.8072 | 226.6341 | 261.256 | 301.1688 | 2.756%
8790 | 25-58.5 | -58.448 | 24.7685 | 661.0809 | 160.5498 | 188.778 | 227.751 | 262.4955 | 302.542 | 2.868%
8791 | 25-58.5 | -58.7194 | 24.7685 | 657.5294 | 161.9349 | 189.6638 | 228.7259 | 263.5371 | 303.6476 | 2.976%
8792 | 25-59 | -58.9907 | 24.7685 | 654.4308 | 163.2929 | 190.5643 | 229.733 | 264.6285 | 304.8255 | 3.087%
8793 | 25-59.5 | -59.262 | 24.7685 | 651.7917 | 164.5863 | 191.4557 | 230.7362 | 265.7217 | 306.0128 | 3.197%
8794 | 25-59.5 | -59.5333 | 24.7685 | 649.6176 | 165.7717 | 192.2971 | 231.6743 | 266.7359 | 307.1044 | 3.302%
8795 | 25-60 | -59.8046 | 24.7685 | 647.9133 | 166.9221 | 193.1606 | 232.6621 | 267.8273 | 308.308 | 3.408%
8796 | 25-60 | -60.076 | 24.7685 | 646.6825 | 168.0011 | 194.0235 | 233.6658 | 268.9514 | 309.5662 | 3.511%
8797 | 25-60.5 | -60.3473 | 24.7685 | 645.9278 | 168.9762 | 194.856 | 234.6414 | 270.0509 | 310.8046 | 3.607%
8798 | 25-60.5 | -60.6186 | 24.7685 | 645.651 | 169.9089 | 195.7238 | 235.695 | 271.2711 | 312.2178 | 3.701%
8799 | 25-61 | -60.8899 | 24.7685 | 645.8526 | 170.7505 | 196.5875 | 236.7671 | 272.5331 | 313.7025 | 3.788%
8800 | 25-61 | -61.1613 | 24.7685 | 646.5323 | 171.4811 | 197.4167 | 237.8124 | 273.7769 | 315.1812 | 3.865%
8801 | 25-61.5 | -61.4326 | 24.7685 | 647.6885 | 172.1941 | 198.2866 | 238.9443 | 275.1534 | 316.8507 | 3.939%
8802 | 25-61.5 | -61.7039 | 24.7685 | 649.3186 | 172.8801 | 199.1384 | 240.0698 | 276.5361 | 318.5429 | 4.011%
8803 | 25-62 | -61.9752 | 24.7685 | 651.4191 | 173.5256 | 199.9463 | 241.1468 | 277.8668 | 320.1799 | 4.078%
8804 | 25-62 | -62.2465 | 24.7685 | 653.9855 | 174.1967 | 200.8079 | 242.327 | 279.3502 | 322.0319 | 4.146%
8805 | 25-62.5 | -62.5179 | 24.7685 | 657.0122 | 174.8508 | 201.6541 | 243.4957 | 280.8262 | 323.8822 | 4.213%
8806 | 25-63 | -62.7892 | 24.7685 | 660.493 | 175.4711 | 202.454 | 244.5962 | 282.2131 | 325.6172 | 4.276%
8807 | 25-63 | -63.0605 | 24.7685 | 664.4208 | 176.0998 | 203.2668 | 245.7177 | 283.6286 | 327.3906 | 4.341%
8808 | 25-63.5 | -63.3318 | 24.7685 | 668.7875 | 176.6932 | 204.0302 | 246.7658 | 284.9474 | 329.0385 | 4.403%
8809 | 25-63.5 | -63.6031 | 24.7685 | 673.5847 | 177.2444 | 204.7346 | 247.726 | 286.1504 | 330.5361 | 4.461%
8810 | 25-64 | -63.8745 | 24.7685 | 678.8033 | 177.792 | 205.4354 | 248.6827 | 287.3503 | 332.0313 | 4.519%
8811 | 25-64 | -64.1458 | 24.7685 | 684.4335 | 178.2921 | 206.0715 | 249.5456 | 288.4284 | 333.3705 | 4.573%
8812 | 25-64.5 | -64.4171 | 24.7685 | 690.4654 | 178.7538 | 206.6566 | 250.3363 | 289.4138 | 334.5919 | 4.624%
8813 | 25-64.5 | -64.6884 | 24.7685 | 696.8884 | 179.2224 | 207.253 | 251.1462 | 290.4267 | 335.8512 | 4.675%
8814 | 25-65 | -64.9598 | 24.7685 | 703.6918 | 179.6414 | 207.7746 | 251.8374 | 291.2777 | 336.8952 | 4.722%
8815 | 25-65 | -65.2311 | 24.7685 | 710.8647 | 180.03 | 208.2482 | 252.4505 | 292.0209 | 337.7943 | 4.768%
8816 | 25-65.5 | -65.5024 | 24.7685 | 718.396 | 180.4361 | 208.7438 | 253.0926 | 292.7999 | 338.7373 | 4.815%
8817 | 25-66 | -65.7737 | 24.7685 | 726.2745 | 180.7834 | 209.1462 | 253.5815 | 293.3665 | 339.3939 | 4.86%
8818 | 25-66 | -66.045 | 24.7685 | 734.4891 | 181.091 | 209.4882 | 253.9741 | 293.8013 | 339.8746 | 4.901%
8819 | 25-66.5 | -66.3164 | 24.7685 | 743.0285 | 181.3985 | 209.8327 | 254.3738 | 294.248 | 340.3732 | 4.942%
8820 | 25-66.5 | -66.5877 | 24.7685 | 751.8818 | 181.649 | 210.1036 | 254.6721 | 294.5667 | 340.7116 | 4.978%
8821 | 25-67 | -66.859 | 24.7685 | 761.0378 | 181.8721 | 210.3434 | 254.9335 | 294.8437 | 341.0025 | 5.01%
8822 | 25-67 | -67.1303 | 24.7685 | 770.4858 | 182.0977 | 210.5933 | 255.2188 | 295.1581 | 341.3483 | 5.041%
8823 | 25-67.5 | -67.4016 | 24.7685 | 780.2152 | 182.2623 | 210.7682 | 255.406 | 295.353 | 341.5487 | 5.065%
8824 | 25-67.5 | -67.673 | 24.7685 | 790.2154 | 182.402 | 210.92 | 255.5741 | 295.5337 | 341.7417 | 5.085%
8825 | 25-68 | -67.9443 | 24.7685 | 800.4765 | 182.5423 | 211.0846 | 255.7777 | 295.7726 | 342.0219 | 5.103%
8826 | 25-68 | -68.2156 | 24.7685 | 810.9884 | 182.6151 | 211.1603 | 255.8556 | 295.8506 | 342.0983 | 5.115%
8827 | 25-68.5 | -68.4869 | 24.7685 | 821.7414 | 182.6727 | 211.2246 | 255.9298 | 295.9331 | 342.1899 | 5.123%
8828 | 25-69 | -68.7583 | 24.7685 | 832.7263 | 182.7413 | 211.3162 | 256.0607 | 296.1021 | 342.4055 | 5.13%
8829 | 25-69 | -69.0296 | 24.7685 | 843.9339 | 182.7396 | 211.3153 | 256.0611 | 296.1038 | 342.409 | 5.129%
8830 | 25-69.5 | -69.3009 | 24.7685 | 855.3554 | 182.7415 | 211.3315 | 256.1032 | 296.1721 | 342.5109 | 5.128%
8831 | 25-69.5 | -69.5722 | 24.7685 | 866.9823 | 182.7746 | 211.4061 | 256.252 | 296.3954 | 342.8283 | 5.126%
8832 | 25-70 | -69.8435 | 24.7685 | 878.8066 | 182.7589 | 211.4284 | 256.3439 | 296.5586 | 343.0829 | 5.118%
8833 | 25-70 | -70.1149 | 24.7685 | 890.8202 | 182.7541 | 211.4761 | 256.4871 | 296.799 | 343.4475 | 5.109%
8834 | 25-70.5 | -70.3862 | 24.7685 | 903.0156 | 182.7739 | 211.5657 | 256.7029 | 297.1425 | 343.9537 | 5.101%
8835 | 25-70.5 | -70.6575 | 24.7685 | 915.3855 | 182.7428 | 211.5839 | 256.8118 | 297.3446 | 344.2757 | 5.089%
8836 | 25-71 | -70.9288 | 24.7685 | 927.9229 | 182.7274 | 211.6181 | 256.9369 | 297.5626 | 344.6128 | 5.079%
8837 | 25-71 | -71.2001 | 24.7685 | 940.621 | 182.7337 | 211.6736 | 257.0817 | 297.7982 | 344.9643 | 5.072%
8838 | 25-71.5 | -71.4715 | 24.7685 | 953.4735 | 182.6998 | 211.6562 | 257.0958 | 297.8454 | 345.0549 | 5.064%
8839 | 25-71.5 | -71.7428 | 24.7685 | 966.474 | 182.6911 | 211.6646 | 257.1355 | 297.9174 | 345.1684 | 5.061%
8840 | 25-72 | -72.0141 | 24.7685 | 979.6167 | 182.7102 | 211.7024 | 257.2067 | 298.022 | 345.3153 | 5.061%
8841 | 25-72.5 | -72.2854 | 24.7685 | 992.8959 | 182.7371 | 211.7374 | 257.2554 | 298.0839 | 345.3932 | 5.064%
8842 | 25-72.5 | -72.5568 | 24.7685 | 1006.3062 | 182.8509 | 211.8877 | 257.4676 | 298.3557 | 345.7383 | 5.076%
8843 | 25-73 | -72.8281 | 24.7685 | 1019.8423 | 183.0166 | 212.104 | 257.7696 | 298.7399 | 346.2234 | 5.094%
8844 | 25-73 | -73.0994 | 24.7685 | 1033.4993 | 183.0843 | 212.1739 | 257.841 | 298.8109 | 346.2919 | 5.104%
8845 | 25-73.5 | -73.3707 | 24.7685 | 1047.2724 | 183.1347 | 212.2104 | 257.8501 | 298.7907 | 346.2329 | 5.114%
8846 | 25-73.5 | -73.642 | 24.7685 | 1061.157 | 183.159 | 212.202 | 257.7814 | 298.66 | 346.0223 | 5.122%
8847 | 25-74 | -73.9134 | 24.7685 | 1075.1488 | 183.1398 | 212.1227 | 257.5936 | 298.3623 | 345.585 | 5.129%
8848 | 25-74 | -74.1847 | 24.7685 | 1089.2437 | 183.1536 | 212.0882 | 257.4706 | 298.1492 | 345.2564 | 5.138%
8849 | 25-74.5 | -74.456 | 24.7685 | 1103.4375 | 183.1727 | 212.0589 | 257.3529 | 297.941 | 344.9323 | 5.149%
8850 | 25-74.5 | -74.7273 | 24.7685 | 1117.7266 | 183.147 | 211.9624 | 257.129 | 297.5886 | 344.4167 | 5.156%
8851 | 25-75 | -74.9986 | 24.7685 | 1132.1073 | 183.1357 | 211.8894 | 256.9449 | 297.2923 | 343.9777 | 5.164%
8852 | 25-75.5 | -75.27 | 24.7685 | 1146.576 | 183.0778 | 211.758 | 256.6827 | 296.8993 | 343.4197 | 5.166%
8853 | 25-75.5 | -75.5413 | 24.7685 | 1161.1296 | 182.8701 | 211.4287 | 256.1415 | 296.1493 | 342.4092 | 5.152%
8854 | 25-76 | -75.8126 | 24.7685 | 1175.7646 | 182.5305 | 210.9333 | 255.3771 | 295.1225 | 341.0571 | 5.123%
8855 | 25-76 | -76.0839 | 24.7685 | 1190.4783 | 182.0965 | 210.3144 | 254.4405 | 293.8765 | 339.4285 | 5.083%
8856 | 25-76.5 | -76.3553 | 24.7685 | 1205.2675 | 181.6609 | 209.6871 | 253.4828 | 292.5966 | 337.7493 | 5.044%
8857 | 25-76.5 | -76.6266 | 24.7685 | 1220.1295 | 181.3715 | 209.2629 | 252.8256 | 291.7118 | 336.5822 | 5.019%
8858 | 25-77 | -76.8979 | 24.7685 | 1235.0617 | 181.1599 | 208.9494 | 252.3359 | 291.0498 | 335.7064 | 5.001%
8859 | 25-77 | -77.1692 | 24.7685 | 1250.0615 | 180.9544 | 208.6513 | 251.8783 | 290.4367 | 334.9008 | 4.983%
8860 | 25-77.5 | -77.4405 | 24.7685 | 1265.1265 | 180.7733 | 208.4 | 251.5071 | 289.9494 | 334.2705 | 4.966%
8861 | 25-77.5 | -77.7119 | 24.7685 | 1280.2543 | 180.5752 | 208.1322 | 251.1209 | 289.4492 | 333.6302 | 4.945%
8862 | 25-78 | -77.9832 | 24.7685 | 1295.4426 | 180.346 | 207.8264 | 250.6853 | 288.8888 | 332.917 | 4.921%
8863 | 25-78.5 | -78.2545 | 24.7685 | 1310.6893 | 180.1401 | 207.5659 | 250.3338 | 288.451 | 332.3745 | 4.897%
8864 | 25-78.5 | -78.5258 | 24.7685 | 1325.9925 | 179.8388 | 207.1892 | 249.8323 | 287.8317 | 331.613 | 4.861%
8865 | 25-79 | -78.7971 | 24.7685 | 1341.35 | 179.4109 | 206.6546 | 249.1215 | 286.9554 | 330.5372 | 4.811%
8866 | 25-79 | -79.0685 | 24.7685 | 1356.76 | 178.9233 | 206.1092 | 248.4199 | 286.1094 | 329.5198 | 4.752%
8867 | 25-79.5 | -79.3398 | 24.7685 | 1372.2207 | 178.4962 | 205.6607 | 247.847 | 285.4221 | 328.6971 | 4.701%
8868 | 25-79.5 | -79.6111 | 24.7685 | 1387.7304 | 178.1926 | 205.3318 | 247.4248 | 284.9136 | 328.0864 | 4.664%
8869 | 25-80 | -79.8824 | 24.7685 | 1403.2873 | 177.9445 | 205.0618 | 247.0843 | 284.5087 | 327.6055 | 4.634%
8870 | 25-80 | -80.1537 | 24.7685 | 1418.89 | 177.69 | 204.7505 | 246.6719 | 284.0015 | 326.9846 | 4.605%
8871 | 25-80.5 | -80.4251 | 24.7685 | 1434.5368 | 177.4518 | 204.4434 | 246.2497 | 283.4701 | 326.3206 | 4.579%
8872 | 25-80.5 | -80.6964 | 24.7685 | 1450.2263 | 177.3067 | 204.2511 | 245.9777 | 283.1219 | 325.8792 | 4.564%
8873 | 25-81 | -80.9677 | 24.7685 | 1465.957 | 177.1748 | 204.0637 | 245.6955 | 282.7475 | 325.3913 | 4.552%
8874 | 25-81 | -81.239 | 24.7685 | 1481.7277 | 177.0697 | 203.9076 | 245.4513 | 282.4175 | 324.9549 | 4.543%
8875 | 25-81.5 | -81.5104 | 24.7685 | 1497.537 | 177.0351 | 203.848 | 245.3478 | 282.2707 | 324.7539 | 4.542%
8876 | 25-82 | -81.7817 | 24.7685 | 1513.3837 | 177.0034 | 203.7849 | 245.2295 | 282.0974 | 324.5118 | 4.541%
8877 | 25-82 | -82.053 | 24.7685 | 1529.2664 | 177.077 | 203.856 | 245.2934 | 282.152 | 324.5525 | 4.552%
8878 | 25-82.5 | -82.3243 | 24.7685 | 1545.1842 | 177.3525 | 204.1928 | 245.7296 | 282.6804 | 325.1906 | 4.585%
8879 | 25-82.5 | -82.5956 | 24.7685 | 1561.1359 | 177.7991 | 204.6957 | 246.3874 | 283.4821 | 326.164 | 4.637%
8880 | 25-83 | -82.867 | 24.7685 | 1577.1203 | 178.2847 | 205.2406 | 247.1223 | 284.3959 | 327.2932 | 4.692%
8881 | 25-83 | -83.1383 | 24.7685 | 1593.1366 | 178.7123 | 205.7678 | 247.8723 | 285.3589 | 328.5163 | 4.736%
8882 | 25-83.5 | -83.4096 | 24.7685 | 1609.1836 | 179.0064 | 206.1461 | 248.4314 | 286.0927 | 329.4647 | 4.765%
8883 | 25-83.5 | -83.6809 | 24.7685 | 1625.2604 | 179.2205 | 206.4615 | 248.9296 | 286.7692 | 330.3622 | 4.782%
8884 | 25-84 | -83.9522 | 24.7685 | 1641.3661 | 179.4029 | 206.7639 | 249.4413 | 287.4871 | 331.3374 | 4.793%
8885 | 25-84 | -84.2236 | 24.7685 | 1657.4998 | 179.4994 | 206.9663 | 249.8312 | 288.0638 | 332.149 | 4.793%
8886 | 25-84.5 | -84.4949 | 24.7685 | 1673.6607 | 179.5871 | 207.1734 | 250.2507 | 288.6954 | 333.0481 | 4.789%
8887 | 25-85 | -84.7662 | 24.7685 | 1689.8479 | 179.6937 | 207.4221 | 250.752 | 289.4494 | 334.1208 | 4.785%
8888 | 25-85 | -85.0375 | 24.7685 | 1706.0606 | 179.7188 | 207.5643 | 251.1051 | 290.0155 | 334.9573 | 4.772%
8889 | 25-85.5 | -85.3089 | 24.7685 | 1722.2982 | 179.7258 | 207.6905 | 251.4468 | 290.5752 | 335.7946 | 4.757%
8890 | 25-85.5 | -85.5802 | 24.7685 | 1738.5597 | 179.727 | 207.8179 | 251.8027 | 291.1628 | 336.6775 | 4.74%
8891 | 25-86 | -85.8515 | 24.7685 | 1754.8445 | 179.6313 | 207.8135 | 251.9675 | 291.5022 | 337.2418 | 4.714%
8892 | 25-86 | -86.1228 | 24.7685 | 1771.152 | 179.5065 | 207.7704 | 252.0774 | 291.7711 | 337.7168 | 4.685%
8893 | 25-86.5 | -86.3941 | 24.7685 | 1787.4814 | 179.356 | 207.6918 | 252.1351 | 291.9717 | 338.1039 | 4.654%
8894 | 25-86.5 | -86.6655 | 24.7685 | 1803.8322 | 179.0929 | 207.4629 | 251.9788 | 291.8973 | 338.141 | 4.612%
8895 | 25-87 | -86.9368 | 24.7685 | 1820.2036 | 178.805 | 207.2149 | 251.8148 | 291.8276 | 338.1995 | 4.567%
8896 | 25-87 | -87.2081 | 24.7685 | 1836.5951 | 178.4895 | 206.9427 | 251.6344 | 291.7502 | 338.2625 | 4.518%
8897 | 25-87.5 | -87.4794 | 24.7685 | 1853.0061 | 178.0662 | 206.5241 | 251.2413 | 291.3961 | 337.9696 | 4.459%
8898 | 25-88 | -87.7507 | 24.7685 | 1869.4361 | 177.5902 | 206.0433 | 250.7708 | 290.9506 | 337.5692 | 4.396%
8899 | 25-88 | -88.0221 | 24.7685 | 1885.8845 | 177.0545 | 205.4905 | 250.2088 | 290.3958 | 337.0383 | 4.327%
8900 | 25-88.5 | -88.2934 | 24.7685 | 1902.3507 | 176.4112 | 204.7953 | 249.4449 | 289.5819 | 336.1782 | 4.249%
8901 | 25-88.5 | -88.5647 | 24.7685 | 1918.8343 | 175.7521 | 204.0985 | 248.6999 | 288.8083 | 335.386 | 4.169%
8902 | 25-89 | -88.836 | 24.7685 | 1935.3348 | 175.0643 | 203.3829 | 247.9427 | 288.0298 | 334.5993 | 4.087%
8903 | 25-89 | -89.1074 | 24.7685 | 1951.8517 | 174.3007 | 202.5753 | 247.0436 | 287.0604 | 333.5605 | 4.001%
8904 | 25-89.5 | -89.3787 | 24.7685 | 1968.3846 | 173.5461 | 201.7959 | 246.1858 | 286.1452 | 332.5917 | 3.918%
8905 | 25-89.5 | -89.65 | 24.7685 | 1984.9329 | 172.7813 | 201.0146 | 245.3203 | 285.2163 | 331.6018 | 3.835%
8906 | 25-90 | -89.9213 | 24.7685 | 2001.4963 | 171.9605 | 200.1673 | 244.3405 | 284.1248 | 330.3879 | 3.751%
8907 | 25-90 | -90.1926 | 24.7685 | 2018.0744 | 171.1673 | 199.3591 | 243.3919 | 283.055 | 329.1827 | 3.673%
8908 | 25-90.5 | -90.464 | 24.7685 | 2034.6667 | 170.3766 | 198.5568 | 242.4255 | 281.9428 | 327.9029 | 3.597%
8909 | 25-90.5 | -90.7353 | 24.7685 | 2051.2728 | 169.5429 | 197.7127 | 241.3768 | 280.7074 | 326.4477 | 3.521%
8910 | 25-50 | -50.0371 | 25.0398 | 955.09 | 113.1318 | 148.9339 | 187.361 | 213.0651 | 242.2993 | 0.7971%
8911 | 25-50.5 | -50.3084 | 25.0398 | 942.5599 | 114.8919 | 151.3857 | 188.9333 | 214.9285 | 244.504 | 0.8402%
8912 | 25-50.5 | -50.5797 | 25.0398 | 930.192 | 116.6128 | 153.7474 | 190.4406 | 216.7053 | 246.5959 | 0.8845%
8913 | 25-51 | -50.851 | 25.0398 | 917.9927 | 118.3012 | 156.0104 | 191.8965 | 218.4272 | 248.6296 | 0.9301%
8914 | 25-51 | -51.1224 | 25.0398 | 905.969 | 119.9835 | 158.1666 | 193.3386 | 220.1534 | 250.691 | 0.9775%
8915 | 25-51.5 | -51.3937 | 25.0398 | 894.1279 | 121.582 | 160.1402 | 194.6826 | 221.7656 | 252.62 | 1.024%
8916 | 25-51.5 | -51.665 | 25.0398 | 882.4768 | 123.1197 | 161.9569 | 195.9699 | 223.3294 | 254.5124 | 1.071%
8917 | 25-52 | -51.9363 | 25.0398 | 871.0234 | 124.6228 | 163.6328 | 197.243 | 224.9061 | 256.4533 | 1.119%
8918 | 25-52 | -52.2077 | 25.0398 | 859.7757 | 126.029 | 165.1019 | 198.4076 | 226.3461 | 258.2235 | 1.165%
8919 | 25-52.5 | -52.479 | 25.0398 | 848.7418 | 127.393 | 166.4351 | 199.5395 | 227.7566 | 259.9688 | 1.211%
8920 | 25-53 | -52.7503 | 25.0398 | 837.9302 | 128.7525 | 167.6664 | 200.6906 | 229.2094 | 261.7858 | 1.258%
8921 | 25-53 | -53.0216 | 25.0398 | 827.3496 | 130.0216 | 168.7183 | 201.757 | 230.5549 | 263.4682 | 1.302%
8922 | 25-53.5 | -53.2929 | 25.0398 | 817.0091 | 131.2793 | 169.6944 | 202.8355 | 231.9253 | 265.1922 | 1.347%
8923 | 25-53.5 | -53.5643 | 25.0398 | 806.9179 | 132.5676 | 170.6328 | 203.9742 | 233.3841 | 267.0398 | 1.395%
8924 | 25-54 | -53.8356 | 25.0398 | 797.0855 | 133.7993 | 171.461 | 205.0699 | 234.787 | 268.816 | 1.441%
8925 | 25-54 | -54.1069 | 25.0398 | 787.5217 | 135.0804 | 172.3051 | 206.2442 | 236.2977 | 270.736 | 1.49%
8926 | 25-54.5 | -54.3782 | 25.0398 | 778.2363 | 136.4468 | 173.2037 | 207.5357 | 237.9653 | 272.8625 | 1.544%
8927 | 25-54.5 | -54.6495 | 25.0398 | 769.2395 | 137.7904 | 174.0954 | 208.7999 | 239.585 | 274.9151 | 1.599%
8928 | 25-55 | -54.9209 | 25.0398 | 760.5416 | 139.2042 | 175.0449 | 210.1363 | 241.2903 | 277.0695 | 1.659%
8929 | 25-55 | -55.1922 | 25.0398 | 752.1528 | 140.7037 | 176.0618 | 211.5563 | 243.0944 | 279.3408 | 1.725%
8930 | 25-55.5 | -55.4635 | 25.0398 | 744.0838 | 142.1786 | 177.0553 | 212.8974 | 244.7635 | 281.4061 | 1.793%
8931 | 25-55.5 | -55.7348 | 25.0398 | 736.345 | 143.7026 | 178.075 | 214.2657 | 246.4602 | 283.4986 | 1.864%
8932 | 25-56 | -56.0061 | 25.0398 | 728.947 | 145.2767 | 179.1211 | 215.6622 | 248.1861 | 285.6212 | 1.941%
8933 | 25-56.5 | -56.2775 | 25.0398 | 721.9003 | 146.8107 | 180.1258 | 216.9731 | 249.7826 | 287.5593 | 2.019%
8934 | 25-56.5 | -56.5488 | 25.0398 | 715.2152 | 148.4014 | 181.1562 | 218.3109 | 251.4062 | 289.5244 | 2.103%
8935 | 25-57 | -56.8201 | 25.0398 | 708.9021 | 150.0383 | 182.2038 | 219.6609 | 253.0367 | 291.4886 | 2.192%
8936 | 25-57 | -57.0914 | 25.0398 | 702.971 | 151.6451 | 183.2102 | 220.9258 | 254.5381 | 293.2686 | 2.284%
8937 | 25-57.5 | -57.3628 | 25.0398 | 697.4315 | 153.3256 | 184.2475 | 222.2189 | 256.0642 | 295.0681 | 2.383%
8938 | 25-57.5 | -57.6341 | 25.0398 | 692.2933 | 155.0464 | 185.2955 | 223.5064 | 257.5676 | 296.8228 | 2.49%
8939 | 25-58 | -57.9054 | 25.0398 | 687.5652 | 156.6936 | 186.2836 | 224.6797 | 258.9031 | 298.3423 | 2.597%
8940 | 25-58 | -58.1767 | 25.0398 | 683.2558 | 158.3351 | 187.3028 | 225.8908 | 260.2824 | 299.9124 | 2.71%
8941 | 25-58.5 | -58.448 | 25.0398 | 679.373 | 159.9179 | 188.3174 | 227.0823 | 261.6269 | 301.4284 | 2.824%
8942 | 25-58.5 | -58.7194 | 25.0398 | 675.9243 | 161.3673 | 189.2411 | 228.1206 | 262.7569 | 302.6537 | 2.935%
8943 | 25-59 | -58.9907 | 25.0398 | 672.9163 | 162.7823 | 190.1713 | 229.1774 | 263.9176 | 303.9253 | 3.048%
8944 | 25-59.5 | -59.262 | 25.0398 | 670.3549 | 164.124 | 191.0836 | 230.2149 | 265.0582 | 305.1761 | 3.16%
8945 | 25-59.5 | -59.5333 | 25.0398 | 668.2454 | 165.348 | 191.9357 | 231.1701 | 266.0956 | 306.2986 | 3.268%
8946 | 25-60 | -59.8046 | 25.0398 | 666.5919 | 166.5327 | 192.8053 | 232.1684 | 267.2019 | 307.5226 | 3.375%
8947 | 25-60 | -60.076 | 25.0398 | 665.3979 | 167.6418 | 193.6699 | 233.1756 | 268.3315 | 308.7886 | 3.479%
8948 | 25-60.5 | -60.3473 | 25.0398 | 664.666 | 168.6431 | 194.4998 | 234.1468 | 269.4247 | 310.0182 | 3.577%
8949 | 25-60.5 | -60.6186 | 25.0398 | 664.3975 | 169.5967 | 195.3601 | 235.1873 | 270.6262 | 311.4058 | 3.672%
8950 | 25-61 | -60.8899 | 25.0398 | 664.593 | 170.451 | 196.2123 | 236.2395 | 271.8598 | 312.8517 | 3.76%
8951 | 25-61 | -61.1613 | 25.0398 | 665.2523 | 171.1835 | 197.0279 | 237.2615 | 273.071 | 314.2859 | 3.837%
8952 | 25-61.5 | -61.4326 | 25.0398 | 666.3738 | 171.8946 | 197.8862 | 238.3735 | 274.4193 | 315.9169 | 3.911%
8953 | 25-61.5 | -61.7039 | 25.0398 | 667.9552 | 172.5763 | 198.7298 | 239.4837 | 275.7798 | 317.5782 | 3.982%
8954 | 25-62 | -61.9752 | 25.0398 | 669.9934 | 173.2217 | 199.535 | 240.5534 | 277.0983 | 319.1969 | 4.049%
8955 | 25-62 | -62.2465 | 25.0398 | 672.484 | 173.8996 | 200.4034 | 241.7402 | 278.5879 | 321.0542 | 4.118%
8956 | 25-62.5 | -62.5179 | 25.0398 | 675.4222 | 174.5671 | 201.2653 | 242.928 | 280.0861 | 322.9303 | 4.186%
8957 | 25-63 | -62.7892 | 25.0398 | 678.8021 | 175.2076 | 202.0898 | 244.0606 | 281.5117 | 324.7122 | 4.252%
8958 | 25-63 | -63.0605 | 25.0398 | 682.6171 | 175.8644 | 202.9379 | 245.2292 | 282.9857 | 326.5574 | 4.319%
8959 | 25-63.5 | -63.3318 | 25.0398 | 686.86 | 176.491 | 203.7431 | 246.3331 | 284.3734 | 328.29 | 4.385%
8960 | 25-63.5 | -63.6031 | 25.0398 | 691.5228 | 177.0782 | 204.4928 | 247.354 | 285.6516 | 329.8804 | 4.447%
8961 | 25-64 | -63.8745 | 25.0398 | 696.5972 | 177.6639 | 205.2425 | 248.3776 | 286.9355 | 331.4802 | 4.509%
8962 | 25-64 | -64.1458 | 25.0398 | 702.0742 | 178.2023 | 205.9283 | 249.3094 | 288.1007 | 332.9286 | 4.567%
8963 | 25-64.5 | -64.4171 | 25.0398 | 707.9444 | 178.7017 | 206.5624 | 250.1679 | 289.1719 | 334.2578 | 4.622%
8964 | 25-64.5 | -64.6884 | 25.0398 | 714.1982 | 179.2074 | 207.2065 | 251.0431 | 290.2667 | 335.6191 | 4.677%
8965 | 25-65 | -64.9598 | 25.0398 | 720.8254 | 179.6639 | 207.7751 | 251.7973 | 291.1958 | 336.7593 | 4.728%
8966 | 25-65 | -65.2311 | 25.0398 | 727.816 | 180.0894 | 208.2945 | 252.4705 | 292.0125 | 337.7481 | 4.778%
8967 | 25-65.5 | -65.5024 | 25.0398 | 735.1595 | 180.5311 | 208.8334 | 253.1688 | 292.8598 | 338.7739 | 4.83%
8968 | 25-66 | -65.7737 | 25.0398 | 742.8454 | 180.912 | 209.2768 | 253.7106 | 293.4904 | 339.5078 | 4.879%
8969 | 25-66 | -66.045 | 25.0398 | 750.8632 | 181.252 | 209.6582 | 254.1541 | 293.9869 | 340.063 | 4.924%
8970 | 25-66.5 | -66.3164 | 25.0398 | 759.2024 | 181.5909 | 210.0411 | 254.6038 | 294.4942 | 340.6352 | 4.969%
8971 | 25-66.5 | -66.5877 | 25.0398 | 767.8525 | 181.8676 | 210.344 | 254.9434 | 294.8631 | 341.0342 | 5.008%
8972 | 25-67 | -66.859 | 25.0398 | 776.803 | 182.1137 | 210.6118 | 255.2412 | 295.1841 | 341.3784 | 5.043%
8973 | 25-67 | -67.1303 | 25.0398 | 786.0437 | 182.3612 | 210.8884 | 255.5611 | 295.5407 | 341.7753 | 5.077%
8974 | 25-67.5 | -67.4016 | 25.0398 | 795.5645 | 182.5463 | 211.0879 | 255.7794 | 295.7727 | 342.02 | 5.104%
8975 | 25-67.5 | -67.673 | 25.0398 | 805.3553 | 182.7071 | 211.2643 | 255.9779 | 295.9888 | 342.2543 | 5.127%
8976 | 25-68 | -67.9443 | 25.0398 | 815.4064 | 182.8703 | 211.4551 | 256.2124 | 296.2628 | 342.5745 | 5.149%
8977 | 25-68 | -68.2156 | 25.0398 | 825.7084 | 182.9657 | 211.5554 | 256.318 | 296.3709 | 342.6832 | 5.163%
8978 | 25-68.5 | -68.4869 | 25.0398 | 836.2518 | 183.0441 | 211.6414 | 256.4145 | 296.4758 | 342.7967 | 5.175%
8979 | 25-69 | -68.7583 | 25.0398 | 847.0277 | 183.1317 | 211.7516 | 256.5623 | 296.6592 | 343.0233 | 5.185%
8980 | 25-69 | -69.0296 | 25.0398 | 858.0272 | 183.1458 | 211.7659 | 256.5764 | 296.6727 | 343.0355 | 5.187%
8981 | 25-69.5 | -69.3009 | 25.0398 | 869.2419 | 183.1606 | 211.7946 | 256.6299 | 296.7508 | 343.1447 | 5.187%
8982 | 25-69.5 | -69.5722 | 25.0398 | 880.6635 | 183.2041 | 211.8793 | 256.7878 | 296.9817 | 343.4678 | 5.188%
8983 | 25-70 | -69.8435 | 25.0398 | 892.284 | 183.1903 | 211.8992 | 256.8692 | 297.1262 | 343.693 | 5.18%
8984 | 25-70 | -70.1149 | 25.0398 | 904.0957 | 183.1834 | 211.9375 | 256.9897 | 297.3306 | 344.0046 | 5.172%
8985 | 25-70.5 | -70.3862 | 25.0398 | 916.0912 | 183.1985 | 212.0127 | 257.1735 | 297.6243 | 344.4383 | 5.165%
8986 | 25-70.5 | -70.6575 | 25.0398 | 928.2634 | 183.1619 | 212.015 | 257.2478 | 297.7728 | 344.6826 | 5.153%
8987 | 25-71 | -70.9288 | 25.0398 | 940.6053 | 183.1406 | 212.0328 | 257.3377 | 297.9366 | 344.9413 | 5.143%
8988 | 25-71 | -71.2001 | 25.0398 | 953.1103 | 183.1409 | 212.0721 | 257.4481 | 298.1193 | 345.2165 | 5.137%
8989 | 25-71.5 | -71.4715 | 25.0398 | 965.772 | 183.1018 | 212.0411 | 257.4333 | 298.1224 | 345.2435 | 5.13%
8990 | 25-71.5 | -71.7428 | 25.0398 | 978.5844 | 183.0911 | 212.0411 | 257.4534 | 298.1633 | 345.3113 | 5.126%
8991 | 25-72 | -72.0141 | 25.0398 | 991.5415 | 183.1117 | 212.0764 | 257.5147 | 298.2505 | 345.4312 | 5.127%
8992 | 25-72.5 | -72.2854 | 25.0398 | 1004.6377 | 183.142 | 212.1127 | 257.5608 | 298.3056 | 345.4971 | 5.131%
8993 | 25-72.5 | -72.5568 | 25.0398 | 1017.8677 | 183.2628 | 212.2684 | 257.7752 | 298.5763 | 345.8365 | 5.145%
8994 | 25-73 | -72.8281 | 25.0398 | 1031.2262 | 183.4381 | 212.4927 | 258.0818 | 298.9615 | 346.3175 | 5.165%
8995 | 25-73 | -73.0994 | 25.0398 | 1044.7082 | 183.515 | 212.5692 | 258.1545 | 299.0282 | 346.3745 | 5.177%
8996 | 25-73.5 | -73.3707 | 25.0398 | 1058.309 | 183.5799 | 212.6203 | 258.1781 | 299.0217 | 346.328 | 5.189%
8997 | 25-73.5 | -73.642 | 25.0398 | 1072.0241 | 183.6228 | 212.6333 | 258.1349 | 298.9202 | 346.1509 | 5.201%
8998 | 25-74 | -73.9134 | 25.0398 | 1085.8491 | 183.6236 | 212.578 | 257.9779 | 298.6598 | 345.7586 | 5.21%
8999 | 25-74 | -74.1847 | 25.0398 | 1099.7798 | 183.6571 | 212.5667 | 257.8841 | 298.4813 | 345.4711 | 5.222%
9000 | 25-74.5 | -74.456 | 25.0398 | 1113.8121 | 183.695 | 212.5592 | 257.7925 | 298.3033 | 345.182 | 5.236%
9001 | 25-74.5 | -74.7273 | 25.0398 | 1127.9424 | 183.6862 | 212.4816 | 257.5908 | 297.9758 | 344.6945 | 5.245%
9002 | 25-75 | -74.9986 | 25.0398 | 1142.1668 | 183.6895 | 212.4233 | 257.4211 | 297.6932 | 344.2681 | 5.256%
9003 | 25-75.5 | -75.27 | 25.0398 | 1156.4818 | 183.6436 | 212.3027 | 257.1671 | 297.3055 | 343.7113 | 5.261%
9004 | 25-75.5 | -75.5413 | 25.0398 | 1170.8842 | 183.4442 | 211.9802 | 256.6296 | 296.5561 | 342.6973 | 5.249%
9005 | 25-76 | -75.8126 | 25.0398 | 1185.3707 | 183.1105 | 211.4891 | 255.8667 | 295.5277 | 341.3396 | 5.22%
9006 | 25-76 | -76.0839 | 25.0398 | 1199.9382 | 182.6799 | 210.8728 | 254.9308 | 294.2807 | 339.7077 | 5.181%
9007 | 25-76.5 | -76.3553 | 25.0398 | 1214.5838 | 182.2462 | 210.2478 | 253.9762 | 293.0047 | 338.0337 | 5.141%
9008 | 25-76.5 | -76.6266 | 25.0398 | 1229.3045 | 181.9592 | 209.8284 | 253.3283 | 292.1337 | 336.8859 | 5.117%
9009 | 25-77 | -76.8979 | 25.0398 | 1244.0978 | 181.7449 | 209.5143 | 252.8421 | 291.4794 | 336.0234 | 5.098%
9010 | 25-77 | -77.1692 | 25.0398 | 1258.9609 | 181.5257 | 209.2021 | 252.3702 | 290.8524 | 335.2046 | 5.078%
9011 | 25-77.5 | -77.4405 | 25.0398 | 1273.8915 | 181.322 | 208.9261 | 251.9713 | 290.3352 | 334.5423 | 5.056%
9012 | 25-77.5 | -77.7119 | 25.0398 | 1288.8872 | 181.097 | 208.6298 | 251.5548 | 289.8035 | 333.87 | 5.032%
9013 | 25-78 | -77.9832 | 25.0398 | 1303.9456 | 180.842 | 208.2988 | 251.0964 | 289.2236 | 333.142 | 5.003%
9014 | 25-78.5 | -78.2545 | 25.0398 | 1319.0645 | 180.6118 | 208.017 | 250.7298 | 288.7778 | 332.6012 | 4.974%
9015 | 25-78.5 | -78.5258 | 25.0398 | 1334.2419 | 180.2641 | 207.5919 | 250.1782 | 288.1082 | 331.7903 | 4.931%
9016 | 25-79 | -78.7971 | 25.0398 | 1349.4758 | 179.7496 | 206.9582 | 249.3491 | 287.0966 | 330.5605 | 4.869%
9017 | 25-79 | -79.0685 | 25.0398 | 1364.7642 | 179.1071 | 206.2633 | 248.4605 | 286.0297 | 329.2824 | 4.79%
9018 | 25-79.5 | -79.3398 | 25.0398 | 1380.1052 | 178.4976 | 205.6468 | 247.6751 | 285.0894 | 328.1592 | 4.716%
9019 | 25-79.5 | -79.6111 | 25.0398 | 1395.4971 | 178.0135 | 205.1495 | 247.0388 | 284.3251 | 327.2437 | 4.658%
9020 | 25-80 | -79.8824 | 25.0398 | 1410.9382 | 177.5874 | 204.7092 | 246.4805 | 283.6587 | 326.4497 | 4.607%
9021 | 25-80 | -80.1537 | 25.0398 | 1426.4268 | 177.1726 | 204.2333 | 245.8564 | 282.8963 | 325.5219 | 4.559%
9022 | 25-80.5 | -80.4251 | 25.0398 | 1441.9614 | 176.8065 | 203.779 | 245.2453 | 282.1375 | 324.5849 | 4.518%
9023 | 25-80.5 | -80.6964 | 25.0398 | 1457.5404 | 176.5598 | 203.4657 | 244.8211 | 281.6085 | 323.929 | 4.491%
9024 | 25-81 | -80.9677 | 25.0398 | 1473.1624 | 176.3482 | 203.1859 | 244.4266 | 281.1043 | 323.291 | 4.469%
9025 | 25-81 | -81.239 | 25.0398 | 1488.826 | 176.181 | 202.9603 | 244.1019 | 280.6844 | 322.7545 | 4.452%
9026 | 25-81.5 | -81.5104 | 25.0398 | 1504.5299 | 176.097 | 202.8474 | 243.9402 | 280.4757 | 322.4883 | 4.444%
9027 | 25-82 | -81.7817 | 25.0398 | 1520.2727 | 176.0181 | 202.7343 | 243.7685 | 280.247 | 322.1893 | 4.437%
9028 | 25-82 | -82.053 | 25.0398 | 1536.0532 | 176.0669 | 202.7855 | 243.8219 | 280.3011 | 322.2429 | 4.444%
9029 | 25-82.5 | -82.3243 | 25.0398 | 1551.8703 | 176.3582 | 203.1557 | 244.3228 | 280.9252 | 323.0155 | 4.476%
9030 | 25-82.5 | -82.5956 | 25.0398 | 1567.7227 | 176.8828 | 203.7345 | 245.1027 | 281.894 | 324.2115 | 4.534%
9031 | 25-83 | -82.867 | 25.0398 | 1583.6094 | 177.4665 | 204.3638 | 245.9711 | 282.9889 | 325.5806 | 4.597%
9032 | 25-83 | -83.1383 | 25.0398 | 1599.5293 | 177.9826 | 204.9656 | 246.8416 | 284.1171 | 327.024 | 4.649%
9033 | 25-83.5 | -83.4096 | 25.0398 | 1615.4813 | 178.3618 | 205.4157 | 247.5134 | 285.0031 | 328.1733 | 4.685%
9034 | 25-83.5 | -83.6809 | 25.0398 | 1631.4645 | 178.6439 | 205.7942 | 248.1086 | 285.8096 | 329.2412 | 4.709%
9035 | 25-84 | -83.9522 | 25.0398 | 1647.478 | 178.8685 | 206.1478 | 248.6981 | 286.6309 | 330.3512 | 4.724%
9036 | 25-84 | -84.2236 | 25.0398 | 1663.5208 | 178.9959 | 206.3933 | 249.1516 | 287.2908 | 331.2701 | 4.726%
9037 | 25-84.5 | -84.4949 | 25.0398 | 1679.5919 | 179.1087 | 206.6338 | 249.6186 | 287.9835 | 332.2466 | 4.726%
9038 | 25-85 | -84.7662 | 25.0398 | 1695.6907 | 179.2337 | 206.9055 | 250.1504 | 288.7749 | 333.3651 | 4.724%
9039 | 25-85 | -85.0375 | 25.0398 | 1711.8162 | 179.2697 | 207.0584 | 250.5135 | 289.3497 | 334.2084 | 4.714%
9040 | 25-85.5 | -85.3089 | 25.0398 | 1727.9676 | 179.2903 | 207.1959 | 250.8615 | 289.9103 | 335.0392 | 4.701%
9041 | 25-85.5 | -85.5802 | 25.0398 | 1744.1443 | 179.3109 | 207.3383 | 251.2235 | 290.4945 | 335.9059 | 4.688%
9042 | 25-86 | -85.8515 | 25.0398 | 1760.3453 | 179.241 | 207.3532 | 251.3951 | 290.8271 | 336.4456 | 4.666%
9043 | 25-86 | -86.1228 | 25.0398 | 1776.5701 | 179.1557 | 207.3444 | 251.5282 | 291.1068 | 336.9145 | 4.644%
9044 | 25-86.5 | -86.3941 | 25.0398 | 1792.818 | 179.06 | 207.3167 | 251.6278 | 291.3387 | 337.3179 | 4.622%
9045 | 25-86.5 | -86.6655 | 25.0398 | 1809.0881 | 178.8645 | 207.1538 | 251.5319 | 291.317 | 337.3961 | 4.59%
9046 | 25-87 | -86.9368 | 25.0398 | 1825.3801 | 178.6499 | 206.9804 | 251.442 | 291.3185 | 337.5203 | 4.555%
9047 | 25-87 | -87.2081 | 25.0398 | 1841.6931 | 178.4122 | 206.7901 | 251.3476 | 291.329 | 337.6714 | 4.516%
9048 | 25-87.5 | -87.4794 | 25.0398 | 1858.0265 | 178.0678 | 206.4568 | 251.0482 | 291.0747 | 337.4842 | 4.468%
9049 | 25-88 | -87.7507 | 25.0398 | 1874.3799 | 177.6695 | 206.0611 | 250.6734 | 290.7333 | 337.1963 | 4.413%
9050 | 25-88 | -88.0221 | 25.0398 | 1890.7527 | 177.2093 | 205.5919 | 250.2065 | 290.283 | 336.7799 | 4.353%
9051 | 25-88.5 | -88.2934 | 25.0398 | 1907.1442 | 176.6367 | 204.9755 | 249.5334 | 289.5699 | 336.0313 | 4.283%
9052 | 25-88.5 | -88.5647 | 25.0398 | 1923.554 | 176.0485 | 204.3557 | 248.88 | 288.9006 | 335.3581 | 4.21%
9053 | 25-89 | -88.836 | 25.0398 | 1939.9816 | 175.433 | 203.7156 | 248.2165 | 288.2325 | 334.7012 | 4.135%
9054 | 25-89 | -89.1074 | 25.0398 | 1956.4264 | 174.7412 | 202.9799 | 247.4114 | 287.3779 | 333.8022 | 4.055%
9055 | 25-89.5 | -89.3787 | 25.0398 | 1972.888 | 174.056 | 202.2672 | 246.6451 | 286.5778 | 332.9775 | 3.976%
9056 | 25-89.5 | -89.65 | 25.0398 | 1989.3659 | 173.3577 | 201.5473 | 245.8675 | 285.7625 | 332.1326 | 3.898%
9057 | 25-90 | -89.9213 | 25.0398 | 2005.8597 | 172.601 | 200.755 | 244.9686 | 284.7771 | 331.0562 | 3.818%
9058 | 25-90 | -90.1926 | 25.0398 | 2022.3689 | 171.8709 | 199.9972 | 244.0941 | 283.8045 | 329.9765 | 3.743%
9059 | 25-90.5 | -90.464 | 25.0398 | 2038.8931 | 171.1412 | 199.2392 | 243.1929 | 282.7776 | 328.8069 | 3.671%
9060 | 25-90.5 | -90.7353 | 25.0398 | 2055.4319 | 170.3655 | 198.4311 | 242.1969 | 281.6111 | 327.4407 | 3.598%
9061 | 25-50 | -50.0371 | 25.3111 | 967.7479 | 112.4757 | 147.9019 | 186.5368 | 211.9327 | 240.7892 | 0.779%
9062 | 25-50.5 | -50.3084 | 25.3111 | 955.4083 | 114.2281 | 150.3583 | 188.099 | 213.7825 | 242.9761 | 0.821%
9063 | 25-50.5 | -50.5797 | 25.3111 | 943.233 | 115.9507 | 152.7426 | 189.6072 | 215.5596 | 245.0674 | 0.8644%
9064 | 25-51 | -50.851 | 25.3111 | 931.2283 | 117.6492 | 155.0452 | 191.0744 | 217.2962 | 247.1199 | 0.9095%
9065 | 25-51 | -51.1224 | 25.3111 | 919.4011 | 119.3501 | 157.2538 | 192.5393 | 219.0538 | 249.2231 | 0.9567%
9066 | 25-51.5 | -51.3937 | 25.3111 | 907.7583 | 120.9698 | 159.2859 | 193.9101 | 220.7035 | 251.2027 | 1.004%
9067 | 25-51.5 | -51.665 | 25.3111 | 896.3071 | 122.5287 | 161.1641 | 195.2245 | 222.3053 | 253.1463 | 1.051%
9068 | 25-52 | -51.9363 | 25.3111 | 885.055 | 124.0521 | 162.9034 | 196.5239 | 223.9186 | 255.1365 | 1.099%
9069 | 25-52 | -52.2077 | 25.3111 | 874.0097 | 125.4747 | 164.4361 | 197.7088 | 225.3856 | 256.9417 | 1.145%
9070 | 25-52.5 | -52.479 | 25.3111 | 863.1791 | 126.8475 | 165.8271 | 198.8515 | 226.8103 | 258.7054 | 1.19%
9071 | 25-53 | -52.7503 | 25.3111 | 852.5716 | 128.2055 | 167.1067 | 200.0024 | 228.2641 | 260.5247 | 1.237%
9072 | 25-53 | -53.0216 | 25.3111 | 842.1955 | 129.4669 | 168.1963 | 201.0608 | 229.6002 | 262.1962 | 1.281%
9073 | 25-53.5 | -53.2929 | 25.3111 | 832.0595 | 130.7084 | 169.1951 | 202.1203 | 230.9468 | 263.8903 | 1.325%
9074 | 25-53.5 | -53.5643 | 25.3111 | 822.1726 | 131.9703 | 170.139 | 203.2275 | 232.3651 | 265.6862 | 1.371%
9075 | 25-54 | -53.8356 | 25.3111 | 812.5439 | 133.1674 | 170.9546 | 204.2803 | 233.7112 | 267.3884 | 1.415%
9076 | 25-54 | -54.1069 | 25.3111 | 803.1826 | 134.4074 | 171.7745 | 205.4028 | 235.1524 | 269.2169 | 1.462%
9077 | 25-54.5 | -54.3782 | 25.3111 | 794.0983 | 135.7273 | 172.6381 | 206.6348 | 236.7393 | 271.2359 | 1.514%
9078 | 25-54.5 | -54.6495 | 25.3111 | 785.3006 | 137.0217 | 173.4905 | 207.8357 | 238.2721 | 273.1723 | 1.566%
9079 | 25-55 | -54.9209 | 25.3111 | 776.7993 | 138.3902 | 174.4046 | 209.1145 | 239.8979 | 275.2196 | 1.623%
9080 | 25-55 | -55.1922 | 25.3111 | 768.6041 | 139.8509 | 175.3921 | 210.4858 | 241.634 | 277.3986 | 1.687%
9081 | 25-55.5 | -55.4635 | 25.3111 | 760.7252 | 141.2955 | 176.364 | 211.7888 | 243.2486 | 279.3889 | 1.751%
9082 | 25-55.5 | -55.7348 | 25.3111 | 753.1723 | 142.8015 | 177.373 | 213.1371 | 244.9159 | 281.4402 | 1.821%
9083 | 25-56 | -56.0061 | 25.3111 | 745.9554 | 144.3712 | 178.4198 | 214.5328 | 246.6392 | 283.5578 | 1.897%
9084 | 25-56.5 | -56.2775 | 25.3111 | 739.0844 | 145.9107 | 179.4333 | 215.8547 | 248.2486 | 285.511 | 1.974%
9085 | 25-56.5 | -56.5488 | 25.3111 | 732.569 | 147.5135 | 180.4777 | 217.2131 | 249.8993 | 287.5107 | 2.057%
9086 | 25-57 | -56.8201 | 25.3111 | 726.4188 | 149.1698 | 181.5449 | 218.594 | 251.5715 | 289.5301 | 2.146%
9087 | 25-57 | -57.0914 | 25.3111 | 720.6432 | 150.8037 | 182.5769 | 219.9008 | 253.1307 | 291.3874 | 2.237%
9088 | 25-57.5 | -57.3628 | 25.3111 | 715.2513 | 152.5175 | 183.645 | 221.2464 | 254.7304 | 293.2867 | 2.337%
9089 | 25-57.5 | -57.6341 | 25.3111 | 710.2518 | 154.2829 | 184.7284 | 222.5959 | 256.3221 | 295.1624 | 2.445%
9090 | 25-58 | -57.9054 | 25.3111 | 705.6531 | 155.9816 | 185.7544 | 223.8379 | 257.7567 | 296.8189 | 2.554%
9091 | 25-58 | -58.1767 | 25.3111 | 701.463 | 157.6818 | 186.8123 | 225.1201 | 259.239 | 298.5321 | 2.668%
9092 | 25-58.5 | -58.448 | 25.3111 | 697.689 | 159.3228 | 187.8645 | 226.381 | 260.6844 | 300.1884 | 2.785%
9093 | 25-58.5 | -58.7194 | 25.3111 | 694.3379 | 160.8268 | 188.8213 | 227.4804 | 261.9032 | 301.5372 | 2.898%
9094 | 25-59 | -58.9907 | 25.3111 | 691.4157 | 162.291 | 189.7792 | 228.5888 | 263.1393 | 302.9138 | 3.013%
9095 | 25-59.5 | -59.262 | 25.3111 | 688.928 | 163.6752 | 190.7119 | 229.6653 | 264.3372 | 304.2449 | 3.127%
9096 | 25-59.5 | -59.5333 | 25.3111 | 686.8795 | 164.9333 | 191.575 | 230.6429 | 265.4085 | 305.4157 | 3.235%
9097 | 25-60 | -59.8046 | 25.3111 | 685.2742 | 166.1474 | 192.4504 | 231.6563 | 266.5392 | 306.6757 | 3.344%
9098 | 25-60 | -60.076 | 25.3111 | 684.1151 | 167.2813 | 193.3157 | 232.6706 | 267.6822 | 307.9631 | 3.449%
9099 | 25-60.5 | -60.3473 | 25.3111 | 683.4045 | 168.3029 | 194.1412 | 233.6393 | 268.7749 | 309.1952 | 3.547%
9100 | 25-60.5 | -60.6186 | 25.3111 | 683.1439 | 169.2725 | 194.9921 | 234.6683 | 269.963 | 310.5668 | 3.643%
9101 | 25-61 | -60.8899 | 25.3111 | 683.3337 | 170.1382 | 195.8308 | 235.7016 | 271.1726 | 311.9824 | 3.731%
9102 | 25-61 | -61.1613 | 25.3111 | 683.9737 | 170.8737 | 196.6307 | 236.7006 | 272.3535 | 313.3774 | 3.807%
9103 | 25-61.5 | -61.4326 | 25.3111 | 685.0624 | 171.583 | 197.4736 | 237.7887 | 273.6696 | 314.9659 | 3.881%
9104 | 25-61.5 | -61.7039 | 25.3111 | 686.5978 | 172.2574 | 198.3038 | 238.877 | 274.9997 | 316.5862 | 3.952%
9105 | 25-62 | -61.9752 | 25.3111 | 688.5769 | 172.8988 | 199.101 | 239.9312 | 276.2956 | 318.1731 | 4.019%
9106 | 25-62 | -62.2465 | 25.3111 | 690.9958 | 173.5789 | 199.9696 | 241.1147 | 277.778 | 320.0185 | 4.088%
9107 | 25-62.5 | -62.5179 | 25.3111 | 693.8501 | 174.2542 | 200.8396 | 242.3106 | 279.2841 | 321.9019 | 4.157%
9108 | 25-63 | -62.7892 | 25.3111 | 697.1342 | 174.9091 | 201.6812 | 243.4648 | 280.7354 | 323.7142 | 4.224%
9109 | 25-63 | -63.0605 | 25.3111 | 700.8422 | 175.5885 | 202.5581 | 244.6724 | 282.258 | 325.6197 | 4.294%
9110 | 25-63.5 | -63.3318 | 25.3111 | 704.9673 | 176.2436 | 203.3996 | 245.8255 | 283.7071 | 327.4285 | 4.362%
9111 | 25-63.5 | -63.6031 | 25.3111 | 709.5023 | 176.8629 | 204.1901 | 246.9016 | 285.0542 | 329.1042 | 4.427%
9112 | 25-64 | -63.8745 | 25.3111 | 714.4394 | 177.4841 | 204.9854 | 247.9879 | 286.4167 | 330.802 | 4.493%
9113 | 25-64 | -64.1458 | 25.3111 | 719.7702 | 178.059 | 205.7183 | 248.9843 | 287.6633 | 332.3519 | 4.555%
9114 | 25-64.5 | -64.4171 | 25.3111 | 725.4861 | 178.5945 | 206.3985 | 249.9055 | 288.8129 | 333.7786 | 4.613%
9115 | 25-64.5 | -64.6884 | 25.3111 | 731.578 | 179.1355 | 207.0867 | 250.8396 | 289.9803 | 335.2291 | 4.672%
9116 | 25-65 | -64.9598 | 25.3111 | 738.0366 | 179.6282 | 207.7 | 251.6523 | 290.9808 | 336.4562 | 4.728%
9117 | 25-65 | -65.2311 | 25.3111 | 744.8524 | 180.0903 | 208.2639 | 252.3829 | 291.8672 | 337.5291 | 4.783%
9118 | 25-65.5 | -65.5024 | 25.3111 | 752.0156 | 180.5669 | 208.8451 | 253.1355 | 292.7797 | 338.6333 | 4.839%
9119 | 25-66 | -65.7737 | 25.3111 | 759.5163 | 180.9814 | 209.329 | 253.7292 | 293.4727 | 339.4421 | 4.892%
9120 | 25-66 | -66.045 | 25.3111 | 767.3447 | 181.3541 | 209.7498 | 254.223 | 294.0296 | 340.0698 | 4.941%
9121 | 25-66.5 | -66.3164 | 25.3111 | 775.4908 | 181.7253 | 210.1713 | 254.7214 | 294.5952 | 340.7114 | 4.991%
9122 | 25-66.5 | -66.5877 | 25.3111 | 783.9447 | 182.0294 | 210.5065 | 255.1013 | 295.0114 | 341.1663 | 5.033%
9123 | 25-67 | -66.859 | 25.3111 | 792.6964 | 182.2997 | 210.803 | 255.4348 | 295.3747 | 341.5604 | 5.071%
9124 | 25-67 | -67.1303 | 25.3111 | 801.7363 | 182.57 | 211.1073 | 255.79 | 295.7737 | 342.0083 | 5.109%
9125 | 25-67.5 | -67.4016 | 25.3111 | 811.0547 | 182.7772 | 211.3333 | 256.0422 | 296.0464 | 342.3017 | 5.139%
9126 | 25-67.5 | -67.673 | 25.3111 | 820.642 | 182.962 | 211.5384 | 256.2771 | 296.306 | 342.5879 | 5.165%
9127 | 25-68 | -67.9443 | 25.3111 | 830.489 | 183.1522 | 211.7614 | 256.552 | 296.6281 | 342.9652 | 5.19%
9128 | 25-68 | -68.2156 | 25.3111 | 840.5864 | 183.2753 | 211.8943 | 256.698 | 296.7836 | 343.1295 | 5.208%
9129 | 25-68.5 | -68.4869 | 25.3111 | 850.9253 | 183.38 | 212.0101 | 256.8297 | 296.9284 | 343.2883 | 5.223%
9130 | 25-69 | -68.7583 | 25.3111 | 861.4971 | 183.4916 | 212.1463 | 257.0061 | 297.1423 | 343.547 | 5.237%
9131 | 25-69 | -69.0296 | 25.3111 | 872.2931 | 183.5266 | 212.1836 | 257.0461 | 297.1838 | 343.5895 | 5.243%
9132 | 25-69.5 | -69.3009 | 25.3111 | 883.3052 | 183.5593 | 212.2321 | 257.1222 | 297.2869 | 343.7261 | 5.245%
9133 | 25-69.5 | -69.5722 | 25.3111 | 894.5253 | 183.6177 | 212.3335 | 257.2991 | 297.5389 | 344.0725 | 5.248%
9134 | 25-70 | -69.8435 | 25.3111 | 905.9457 | 183.6096 | 212.3564 | 257.3787 | 297.6763 | 344.2838 | 5.241%
9135 | 25-70 | -70.1149 | 25.3111 | 917.5589 | 183.6036 | 212.3896 | 257.4835 | 297.8539 | 344.5546 | 5.234%
9136 | 25-70.5 | -70.3862 | 25.3111 | 929.3576 | 183.6161 | 212.4535 | 257.64 | 298.1043 | 344.9244 | 5.228%
9137 | 25-70.5 | -70.6575 | 25.3111 | 941.3348 | 183.5751 | 212.4408 | 257.6804 | 298.1999 | 345.0915 | 5.216%
9138 | 25-71 | -70.9288 | 25.3111 | 953.4838 | 183.547 | 212.4403 | 257.7313 | 298.3037 | 345.2638 | 5.207%
9139 | 25-71 | -71.2001 | 25.3111 | 965.798 | 183.5387 | 212.4592 | 257.7997 | 298.423 | 345.4482 | 5.202%
9140 | 25-71.5 | -71.4715 | 25.3111 | 978.2712 | 183.4909 | 212.409 | 257.7474 | 298.3701 | 345.3958 | 5.195%
9141 | 25-71.5 | -71.7428 | 25.3111 | 990.8972 | 183.4736 | 212.3944 | 257.7384 | 298.3674 | 345.4018 | 5.191%
9142 | 25-72 | -72.0141 | 25.3111 | 1003.6704 | 183.4901 | 212.4197 | 257.7791 | 298.4232 | 345.4767 | 5.193%
9143 | 25-72.5 | -72.2854 | 25.3111 | 1016.5851 | 183.5157 | 212.4464 | 257.8068 | 298.4513 | 345.5047 | 5.196%
9144 | 25-72.5 | -72.5568 | 25.3111 | 1029.636 | 183.6323 | 212.5922 | 258.0015 | 298.6923 | 345.8019 | 5.21%
9145 | 25-73 | -72.8281 | 25.3111 | 1042.818 | 183.804 | 212.8067 | 258.287 | 299.045 | 346.2361 | 5.231%
9146 | 25-73 | -73.0994 | 25.3111 | 1056.126 | 183.8794 | 212.8755 | 258.3408 | 299.0814 | 346.2482 | 5.244%
9147 | 25-73.5 | -73.3707 | 25.3111 | 1069.5553 | 183.9511 | 212.931 | 258.3642 | 299.0701 | 346.1908 | 5.258%
9148 | 25-73.5 | -73.642 | 25.3111 | 1083.1015 | 184.0071 | 212.9581 | 258.3366 | 298.9854 | 346.0316 | 5.272%
9149 | 25-74 | -73.9134 | 25.3111 | 1096.76 | 184.0227 | 212.9203 | 258.2014 | 298.7507 | 345.6696 | 5.283%
9150 | 25-74 | -74.1847 | 25.3111 | 1110.5269 | 184.0715 | 212.9271 | 258.1302 | 298.599 | 345.4141 | 5.298%
9151 | 25-74.5 | -74.456 | 25.3111 | 1124.3979 | 184.1245 | 212.9373 | 258.0607 | 298.4472 | 345.1559 | 5.314%
9152 | 25-74.5 | -74.7273 | 25.3111 | 1138.3693 | 184.1295 | 212.8759 | 257.8791 | 298.1434 | 344.6965 | 5.326%
9153 | 25-75 | -74.9986 | 25.3111 | 1152.4374 | 184.1444 | 212.8295 | 257.7213 | 297.8724 | 344.2812 | 5.339%
9154 | 25-75.5 | -75.27 | 25.3111 | 1166.5987 | 184.1093 | 212.7189 | 257.4756 | 297.4911 | 343.7282 | 5.346%
9155 | 25-75.5 | -75.5413 | 25.3111 | 1180.8497 | 183.9218 | 212.409 | 256.9516 | 296.7559 | 342.729 | 5.335%
9156 | 25-76 | -75.8126 | 25.3111 | 1195.1872 | 183.6041 | 211.9371 | 256.2131 | 295.7567 | 341.4065 | 5.309%
9157 | 25-76 | -76.0839 | 25.3111 | 1209.6081 | 183.1885 | 211.3402 | 255.3042 | 294.5441 | 339.818 | 5.271%
9158 | 25-76.5 | -76.3553 | 25.3111 | 1224.1094 | 182.7606 | 210.7247 | 254.3659 | 293.291 | 338.1752 | 5.232%
9159 | 25-76.5 | -76.6266 | 25.3111 | 1238.6883 | 182.4683 | 210.3019 | 253.7181 | 292.4241 | 337.0368 | 5.206%
9160 | 25-77 | -76.8979 | 25.3111 | 1253.342 | 182.2386 | 209.9723 | 253.2168 | 291.7556 | 336.1615 | 5.184%
9161 | 25-77 | -77.1692 | 25.3111 | 1268.0678 | 181.9973 | 209.6361 | 252.7186 | 291.1005 | 335.3133 | 5.161%
9162 | 25-77.5 | -77.4405 | 25.3111 | 1282.8633 | 181.7684 | 209.3332 | 252.2906 | 290.5527 | 334.619 | 5.135%
9163 | 25-77.5 | -77.7119 | 25.3111 | 1297.7259 | 181.5144 | 209.0061 | 251.8413 | 289.9872 | 333.9122 | 5.106%
9164 | 25-78 | -77.9832 | 25.3111 | 1312.6535 | 181.2253 | 208.6396 | 251.346 | 289.37 | 333.1474 | 5.071%
9165 | 25-78.5 | -78.2545 | 25.3111 | 1327.6437 | 180.9565 | 208.3177 | 250.9383 | 288.8831 | 332.5666 | 5.036%
9166 | 25-78.5 | -78.5258 | 25.3111 | 1342.6944 | 180.5424 | 207.8183 | 250.3004 | 288.1172 | 331.6485 | 4.983%
9167 | 25-79 | -78.7971 | 25.3111 | 1357.8036 | 179.9132 | 207.0509 | 249.3052 | 286.9103 | 330.1891 | 4.905%
9168 | 25-79 | -79.0685 | 25.3111 | 1372.9693 | 179.0627 | 206.1598 | 248.1647 | 285.5403 | 328.5475 | 4.8%
9169 | 25-79.5 | -79.3398 | 25.3111 | 1388.1896 | 178.2159 | 205.3247 | 247.0965 | 284.2577 | 327.0116 | 4.698%
9170 | 25-79.5 | -79.6111 | 25.3111 | 1403.4627 | 177.5074 | 204.6167 | 246.1868 | 283.1621 | 325.6958 | 4.614%
9171 | 25-80 | -79.8824 | 25.3111 | 1418.7867 | 176.8783 | 203.9821 | 245.3766 | 282.1903 | 324.533 | 4.54%
9172 | 25-80 | -80.1537 | 25.3111 | 1434.1602 | 176.2749 | 203.3254 | 244.5178 | 281.1435 | 323.2617 | 4.471%
9173 | 25-80.5 | -80.4251 | 25.3111 | 1449.5813 | 175.7306 | 202.7003 | 243.6858 | 280.1175 | 322.0025 | 4.411%
9174 | 25-80.5 | -80.6964 | 25.3111 | 1465.0487 | 175.3159 | 202.2241 | 243.0528 | 279.3373 | 321.0453 | 4.365%
9175 | 25-81 | -80.9677 | 25.3111 | 1480.5607 | 174.9735 | 201.8074 | 242.4854 | 278.6271 | 320.1625 | 4.328%
9176 | 25-81 | -81.239 | 25.3111 | 1496.116 | 174.7185 | 201.4792 | 242.0349 | 278.0607 | 319.4553 | 4.301%
9177 | 25-81.5 | -81.5104 | 25.3111 | 1511.7132 | 174.5743 | 201.2995 | 241.7967 | 277.7675 | 319.0958 | 4.285%
9178 | 25-82 | -81.7817 | 25.3111 | 1527.3509 | 174.4453 | 201.1334 | 241.5686 | 277.4804 | 318.7372 | 4.271%
9179 | 25-82 | -82.053 | 25.3111 | 1543.0279 | 174.4718 | 201.1686 | 241.6183 | 277.5438 | 318.8171 | 4.274%
9180 | 25-82.5 | -82.3243 | 25.3111 | 1558.743 | 174.7873 | 201.5822 | 242.1988 | 278.2832 | 319.7495 | 4.307%
9181 | 25-82.5 | -82.5956 | 25.3111 | 1574.4949 | 175.4254 | 202.261 | 243.135 | 279.4629 | 321.2238 | 4.373%
9182 | 25-83 | -82.867 | 25.3111 | 1590.2825 | 176.1471 | 203.0064 | 244.1815 | 280.7957 | 322.9042 | 4.448%
9183 | 25-83 | -83.1383 | 25.3111 | 1606.1048 | 176.789 | 203.7168 | 245.2204 | 282.1504 | 324.6455 | 4.511%
9184 | 25-83.5 | -83.4096 | 25.3111 | 1621.9605 | 177.282 | 204.2674 | 246.0459 | 283.2413 | 326.0628 | 4.557%
9185 | 25-83.5 | -83.6809 | 25.3111 | 1637.8489 | 177.6731 | 204.7419 | 246.7846 | 284.2368 | 327.3756 | 4.592%
9186 | 25-84 | -83.9522 | 25.3111 | 1653.7688 | 178.0045 | 205.1894 | 247.5104 | 285.2351 | 328.7122 | 4.617%
9187 | 25-84 | -84.2236 | 25.3111 | 1669.7193 | 178.238 | 205.5304 | 248.0983 | 286.0663 | 329.8471 | 4.631%
9188 | 25-84.5 | -84.4949 | 25.3111 | 1685.6995 | 178.4293 | 205.8514 | 248.6758 | 286.8979 | 330.9969 | 4.639%
9189 | 25-85 | -84.7662 | 25.3111 | 1701.7085 | 178.6011 | 206.1815 | 249.2853 | 287.785 | 332.2327 | 4.643%
9190 | 25-85 | -85.0375 | 25.3111 | 1717.7454 | 178.6673 | 206.3695 | 249.6907 | 288.4085 | 333.132 | 4.637%
9191 | 25-85.5 | -85.3089 | 25.3111 | 1733.8095 | 178.7193 | 206.5403 | 250.0744 | 289.0063 | 334.0008 | 4.629%
9192 | 25-85.5 | -85.5802 | 25.3111 | 1749.8999 | 178.7775 | 206.7205 | 250.4731 | 289.6249 | 334.898 | 4.622%
9193 | 25-86 | -85.8515 | 25.3111 | 1766.0159 | 178.7523 | 206.7785 | 250.6829 | 289.9895 | 335.4604 | 4.607%
9194 | 25-86 | -86.1228 | 25.3111 | 1782.1567 | 178.7198 | 206.8198 | 250.8594 | 290.3041 | 335.9521 | 4.593%
9195 | 25-86.5 | -86.3941 | 25.3111 | 1798.3217 | 178.6853 | 206.8497 | 251.0077 | 290.5739 | 336.3779 | 4.58%
9196 | 25-86.5 | -86.6655 | 25.3111 | 1814.51 | 178.5573 | 206.7504 | 250.9658 | 290.5943 | 336.4816 | 4.559%
9197 | 25-87 | -86.9368 | 25.3111 | 1830.7211 | 178.4155 | 206.6482 | 250.9411 | 290.6529 | 336.6505 | 4.534%
9198 | 25-87 | -87.2081 | 25.3111 | 1846.9544 | 178.2556 | 206.5364 | 250.9235 | 290.7361 | 336.8672 | 4.506%
9199 | 25-87.5 | -87.4794 | 25.3111 | 1863.2091 | 177.9905 | 206.2861 | 250.7108 | 290.5698 | 336.7674 | 4.468%
9200 | 25-88 | -87.7507 | 25.3111 | 1879.4846 | 177.6707 | 205.9746 | 250.4273 | 290.3248 | 336.5802 | 4.424%
9201 | 25-88 | -88.0221 | 25.3111 | 1895.7805 | 177.2866 | 205.5885 | 250.0533 | 289.9751 | 336.272 | 4.372%
9202 | 25-88.5 | -88.2934 | 25.3111 | 1912.0961 | 176.7846 | 205.05 | 249.4687 | 289.359 | 335.6295 | 4.31%
9203 | 25-88.5 | -88.5647 | 25.3111 | 1928.4308 | 176.2629 | 204.5051 | 248.9027 | 288.7878 | 335.0663 | 4.244%
9204 | 25-89 | -88.836 | 25.3111 | 1944.7842 | 175.7119 | 203.9372 | 248.3269 | 288.2213 | 334.5271 | 4.175%
9205 | 25-89 | -89.1074 | 25.3111 | 1961.1557 | 175.0833 | 203.2692 | 247.6091 | 287.4724 | 333.7557 | 4.101%
9206 | 25-89.5 | -89.3787 | 25.3111 | 1977.5448 | 174.4583 | 202.619 | 246.9281 | 286.7794 | 333.0647 | 4.027%
9207 | 25-89.5 | -89.65 | 25.3111 | 1993.9511 | 173.8166 | 201.9563 | 246.2331 | 286.0712 | 332.3572 | 3.953%
9208 | 25-90 | -89.9213 | 25.3111 | 2010.374 | 173.1143 | 201.2153 | 245.4119 | 285.1892 | 331.4159 | 3.876%
9209 | 25-90 | -90.1926 | 25.3111 | 2026.8132 | 172.4378 | 200.5047 | 244.6098 | 284.3135 | 330.4637 | 3.804%
9210 | 25-90.5 | -90.464 | 25.3111 | 2043.2681 | 171.7592 | 199.7883 | 243.7735 | 283.3745 | 329.4106 | 3.734%
9211 | 25-90.5 | -90.7353 | 25.3111 | 2059.7384 | 171.0316 | 199.0131 | 242.8305 | 282.2807 | 328.1417 | 3.663%
9212 | 26-50 | -50.0371 | 25.5824 | 980.597 | 111.956 | 147.0443 | 185.8595 | 211.0056 | 239.5565 | 0.7645%
9213 | 26-50.5 | -50.3084 | 25.5824 | 968.4455 | 113.6965 | 149.4933 | 187.4072 | 212.8363 | 241.7186 | 0.8055%
9214 | 26-50.5 | -50.5797 | 25.5824 | 956.4601 | 115.4165 | 151.888 | 188.911 | 214.6062 | 243.7994 | 0.8481%
9215 | 26-51 | -50.851 | 25.5824 | 944.6471 | 117.1212 | 154.2186 | 190.3844 | 216.3498 | 245.8595 | 0.8927%
9216 | 26-51 | -51.1224 | 25.5824 | 933.0133 | 118.8373 | 156.4692 | 191.8675 | 218.1314 | 247.9935 | 0.9397%
9217 | 26-51.5 | -51.3937 | 25.5824 | 921.5654 | 120.4754 | 158.5496 | 193.2603 | 219.8101 | 250.0106 | 0.9866%
9218 | 26-51.5 | -51.665 | 25.5824 | 910.3103 | 122.0534 | 160.4797 | 194.5971 | 221.4408 | 251.9912 | 1.034%
9219 | 26-52 | -51.9363 | 25.5824 | 899.2555 | 123.5955 | 162.2737 | 195.9184 | 223.0819 | 254.016 | 1.082%
9220 | 26-52 | -52.2077 | 25.5824 | 888.4085 | 125.0348 | 163.8627 | 197.1201 | 224.5676 | 255.8418 | 1.128%
9221 | 26-52.5 | -52.479 | 25.5824 | 877.7768 | 126.4187 | 165.3062 | 198.2718 | 226.0002 | 257.6117 | 1.174%
9222 | 26-53 | -52.7503 | 25.5824 | 867.3686 | 127.7803 | 166.6312 | 199.4228 | 227.451 | 259.4242 | 1.22%
9223 | 26-53 | -53.0216 | 25.5824 | 857.192 | 129.0396 | 167.7604 | 200.4733 | 228.7737 | 261.075 | 1.264%
9224 | 26-53.5 | -53.2929 | 25.5824 | 847.2553 | 130.2704 | 168.7854 | 201.5145 | 230.0937 | 262.7322 | 1.308%
9225 | 26-53.5 | -53.5643 | 25.5824 | 837.5671 | 131.511 | 169.7382 | 202.5915 | 231.4709 | 264.4733 | 1.353%
9226 | 26-54 | -53.8356 | 25.5824 | 828.1361 | 132.679 | 170.5453 | 203.6049 | 232.7639 | 266.1052 | 1.395%
9227 | 26-54 | -54.1069 | 25.5824 | 818.9714 | 133.884 | 171.3455 | 204.6815 | 234.1434 | 267.8524 | 1.441%
9228 | 26-54.5 | -54.3782 | 25.5824 | 810.0819 | 135.1641 | 172.179 | 205.862 | 235.6608 | 269.7794 | 1.49%
9229 | 26-54.5 | -54.6495 | 25.5824 | 801.4768 | 136.4151 | 172.9959 | 207.0063 | 237.1162 | 271.6124 | 1.54%
9230 | 26-55 | -54.9209 | 25.5824 | 793.1654 | 137.7438 | 173.8781 | 208.2338 | 238.6716 | 273.5656 | 1.595%
9231 | 26-55 | -55.1922 | 25.5824 | 785.1571 | 139.1704 | 174.8391 | 209.5624 | 240.3488 | 275.6654 | 1.656%
9232 | 26-55.5 | -55.4635 | 25.5824 | 777.4612 | 140.5871 | 175.7902 | 210.83 | 241.9136 | 277.5876 | 1.719%
9233 | 26-55.5 | -55.7348 | 25.5824 | 770.0872 | 142.0744 | 176.787 | 212.1574 | 243.5513 | 279.5983 | 1.787%
9234 | 26-56 | -56.0061 | 25.5824 | 763.0443 | 143.6361 | 177.8313 | 213.5484 | 245.2677 | 281.7062 | 1.861%
9235 | 26-56.5 | -56.2775 | 25.5824 | 756.3419 | 145.1756 | 178.8486 | 214.8749 | 246.8823 | 283.665 | 1.937%
9236 | 26-56.5 | -56.5488 | 25.5824 | 749.9891 | 146.7848 | 179.902 | 216.2475 | 248.5521 | 285.6897 | 2.019%
9237 | 26-57 | -56.8201 | 25.5824 | 743.9948 | 148.4548 | 180.9841 | 217.6531 | 250.2583 | 287.7547 | 2.108%
9238 | 26-57 | -57.0914 | 25.5824 | 738.3679 | 150.1095 | 182.0368 | 218.9945 | 251.8656 | 289.6768 | 2.2%
9239 | 26-57.5 | -57.3628 | 25.5824 | 733.1168 | 151.8484 | 183.1292 | 220.3824 | 253.5254 | 291.6582 | 2.3%
9240 | 26-57.5 | -57.6341 | 25.5824 | 728.2496 | 153.6442 | 184.2403 | 221.7818 | 255.1888 | 293.6328 | 2.408%
9241 | 26-58 | -57.9054 | 25.5824 | 723.7741 | 155.3799 | 185.296 | 223.0789 | 256.7036 | 295.4009 | 2.518%
9242 | 26-58 | -58.1767 | 25.5824 | 719.6977 | 157.1245 | 186.3849 | 224.4205 | 258.2735 | 297.2368 | 2.634%
9243 | 26-58.5 | -58.448 | 25.5824 | 716.0271 | 158.8119 | 187.4681 | 225.7416 | 259.8079 | 299.0185 | 2.752%
9244 | 26-58.5 | -58.7194 | 25.5824 | 712.7686 | 160.3592 | 188.4528 | 226.8954 | 261.1076 | 300.4812 | 2.867%
9245 | 26-59 | -58.9907 | 25.5824 | 709.928 | 161.8642 | 189.4362 | 228.0546 | 262.4196 | 301.9652 | 2.983%
9246 | 26-59.5 | -59.262 | 25.5824 | 707.5102 | 163.2844 | 190.3895 | 229.1733 | 263.6811 | 303.387 | 3.098%
9247 | 26-59.5 | -59.5333 | 25.5824 | 705.5196 | 164.5712 | 191.2643 | 230.1774 | 264.7936 | 304.6173 | 3.207%
9248 | 26-60 | -59.8046 | 25.5824 | 703.9598 | 165.8102 | 192.1466 | 231.2103 | 265.9563 | 305.9253 | 3.317%
9249 | 26-60 | -60.076 | 25.5824 | 702.8338 | 166.964 | 193.0134 | 232.2355 | 267.12 | 307.2455 | 3.422%
9250 | 26-60.5 | -60.3473 | 25.5824 | 702.1435 | 168.0003 | 193.8339 | 233.2041 | 268.2175 | 308.4889 | 3.521%
9251 | 26-60.5 | -60.6186 | 25.5824 | 701.8904 | 168.9802 | 194.6744 | 234.2236 | 269.3972 | 309.8538 | 3.616%
9252 | 26-61 | -60.8899 | 25.5824 | 702.0748 | 169.8526 | 195.4985 | 235.2395 | 270.587 | 311.2467 | 3.704%
9253 | 26-61 | -61.1613 | 25.5824 | 702.6964 | 170.5911 | 196.2815 | 236.2159 | 271.7399 | 312.6071 | 3.78%
9254 | 26-61.5 | -61.4326 | 25.5824 | 703.7541 | 171.2988 | 197.1073 | 237.2793 | 273.0239 | 314.1544 | 3.854%
9255 | 26-61.5 | -61.7039 | 25.5824 | 705.2458 | 171.9658 | 197.9218 | 238.3431 | 274.3209 | 315.7308 | 3.923%
9256 | 26-62 | -61.9752 | 25.5824 | 707.1689 | 172.6004 | 198.7075 | 239.3777 | 275.589 | 317.2798 | 3.99%
9257 | 26-62 | -62.2465 | 25.5824 | 709.5199 | 173.2791 | 199.5721 | 240.5522 | 277.0575 | 319.1049 | 4.059%
9258 | 26-62.5 | -62.5179 | 25.5824 | 712.2944 | 173.9581 | 200.4446 | 241.7487 | 278.5621 | 320.984 | 4.128%
9259 | 26-63 | -62.7892 | 25.5824 | 715.4875 | 174.6223 | 201.2971 | 242.916 | 280.0286 | 322.8139 | 4.196%
9260 | 26-63 | -63.0605 | 25.5824 | 719.0938 | 175.3195 | 202.1975 | 244.1568 | 281.5935 | 324.773 | 4.267%
9261 | 26-63.5 | -63.3318 | 25.5824 | 723.1069 | 175.9983 | 203.0704 | 245.3542 | 283.0995 | 326.6538 | 4.338%
9262 | 26-63.5 | -63.6031 | 25.5824 | 727.5201 | 176.6459 | 203.8977 | 246.4816 | 284.5115 | 328.4112 | 4.406%
9263 | 26-64 | -63.8745 | 25.5824 | 732.3262 | 177.3002 | 204.7364 | 247.6283 | 285.9508 | 330.2057 | 4.475%
9264 | 26-64 | -64.1458 | 25.5824 | 737.5175 | 177.9103 | 205.5145 | 248.6866 | 287.275 | 331.8522 | 4.541%
9265 | 26-64.5 | -64.4171 | 25.5824 | 743.0859 | 178.4804 | 206.238 | 249.6656 | 288.4959 | 333.3664 | 4.603%
9266 | 26-64.5 | -64.6884 | 25.5824 | 749.023 | 179.0545 | 206.9667 | 250.6519 | 289.7264 | 334.893 | 4.666%
9267 | 26-65 | -64.9598 | 25.5824 | 755.3201 | 179.581 | 207.6205 | 251.5162 | 290.7888 | 336.194 | 4.726%
9268 | 26-65 | -65.2311 | 25.5824 | 761.9682 | 180.0771 | 208.2251 | 252.2983 | 291.7365 | 337.34 | 4.784%
9269 | 26-65.5 | -65.5024 | 25.5824 | 768.9581 | 180.5867 | 208.8456 | 253.1002 | 292.7076 | 338.5137 | 4.845%
9270 | 26-66 | -65.7737 | 25.5824 | 776.2807 | 181.0332 | 209.3673 | 253.741 | 293.4561 | 339.3882 | 4.901%
9271 | 26-66 | -66.045 | 25.5824 | 783.9267 | 181.4376 | 209.8253 | 254.2806 | 294.0668 | 340.0789 | 4.955%
9272 | 26-66.5 | -66.3164 | 25.5824 | 791.8865 | 181.8408 | 210.2839 | 254.8243 | 294.6849 | 340.7815 | 5.009%
9273 | 26-66.5 | -66.5877 | 25.5824 | 800.1509 | 182.1726 | 210.6503 | 255.2405 | 295.1421 | 341.2822 | 5.055%
9274 | 26-67 | -66.859 | 25.5824 | 808.7104 | 182.4678 | 210.9749 | 255.6071 | 295.5425 | 341.7181 | 5.097%
9275 | 26-67 | -67.1303 | 25.5824 | 817.5559 | 182.7623 | 211.3074 | 255.9973 | 295.9826 | 342.2142 | 5.138%
9276 | 26-67.5 | -67.4016 | 25.5824 | 826.678 | 182.993 | 211.5613 | 256.284 | 296.296 | 342.5555 | 5.171%
9277 | 26-67.5 | -67.673 | 25.5824 | 836.0676 | 183.2042 | 211.7981 | 256.5592 | 296.6039 | 342.8997 | 5.201%
9278 | 26-68 | -67.9443 | 25.5824 | 845.716 | 183.4252 | 212.0588 | 256.8832 | 296.9856 | 343.3492 | 5.23%
9279 | 26-68 | -68.2156 | 25.5824 | 855.6142 | 183.581 | 212.2321 | 257.082 | 297.2057 | 343.5923 | 5.252%
9280 | 26-68.5 | -68.4869 | 25.5824 | 865.7537 | 183.718 | 212.3871 | 257.2644 | 297.4116 | 343.8247 | 5.272%
9281 | 26-69 | -68.7583 | 25.5824 | 876.1261 | 183.8605 | 212.5599 | 257.4866 | 297.6798 | 344.1476 | 5.29%
9282 | 26-69 | -69.0296 | 25.5824 | 886.7231 | 183.9225 | 212.629 | 257.5659 | 297.7675 | 344.2444 | 5.299%
9283 | 26-69.5 | -69.3009 | 25.5824 | 897.5369 | 183.9784 | 212.7047 | 257.6753 | 297.9094 | 344.4262 | 5.305%
9284 | 26-69.5 | -69.5722 | 25.5824 | 908.5595 | 184.0565 | 212.8286 | 257.8792 | 298.1923 | 344.8079 | 5.31%
9285 | 26-70 | -69.8435 | 25.5824 | 919.7836 | 184.0585 | 212.8599 | 257.9639 | 298.3311 | 345.0156 | 5.305%
9286 | 26-70 | -70.1149 | 25.5824 | 931.2017 | 184.0575 | 212.8934 | 258.0599 | 298.4908 | 345.2565 | 5.299%
9287 | 26-70.5 | -70.3862 | 25.5824 | 942.8067 | 184.0714 | 212.9511 | 258.1966 | 298.7072 | 345.5744 | 5.294%
9288 | 26-70.5 | -70.6575 | 25.5824 | 954.592 | 184.028 | 212.9258 | 258.2058 | 298.7527 | 345.6675 | 5.284%
9289 | 26-71 | -70.9288 | 25.5824 | 966.5507 | 183.9941 | 212.9077 | 258.2178 | 298.7964 | 345.7526 | 5.276%
9290 | 26-71 | -71.2001 | 25.5824 | 978.6765 | 183.977 | 212.9051 | 258.2425 | 298.8494 | 345.8423 | 5.271%
9291 | 26-71.5 | -71.4715 | 25.5824 | 990.9633 | 183.9186 | 212.833 | 258.1478 | 298.7338 | 345.7015 | 5.264%
9292 | 26-71.5 | -71.7428 | 25.5824 | 1003.4051 | 183.8919 | 212.7994 | 258.1028 | 298.6781 | 345.6331 | 5.261%
9293 | 26-72 | -72.0141 | 25.5824 | 1015.9962 | 183.8994 | 212.8076 | 258.1121 | 298.6884 | 345.6445 | 5.262%
9294 | 26-72.5 | -72.2854 | 25.5824 | 1028.731 | 183.9084 | 212.8082 | 258.0972 | 298.6576 | 345.5932 | 5.264%
9295 | 26-72.5 | -72.5568 | 25.5824 | 1041.6043 | 184.0034 | 212.9213 | 258.2396 | 298.8271 | 345.7951 | 5.277%
9296 | 26-73 | -72.8281 | 25.5824 | 1054.6109 | 184.1513 | 213.0997 | 258.4679 | 299.1018 | 346.1254 | 5.296%
9297 | 26-73 | -73.0994 | 25.5824 | 1067.7459 | 184.211 | 213.1431 | 258.4796 | 299.0796 | 346.0583 | 5.308%
9298 | 26-73.5 | -73.3707 | 25.5824 | 1081.0047 | 184.2807 | 213.1933 | 258.4915 | 299.0505 | 345.9753 | 5.323%
9299 | 26-73.5 | -73.642 | 25.5824 | 1094.3826 | 184.3453 | 213.2304 | 258.4762 | 298.9803 | 345.8331 | 5.338%
9300 | 26-74 | -73.9134 | 25.5824 | 1107.8754 | 184.3711 | 213.2054 | 258.3582 | 298.7672 | 345.498 | 5.351%
9301 | 26-74 | -74.1847 | 25.5824 | 1121.4788 | 184.4315 | 213.2275 | 258.3088 | 298.6433 | 345.2779 | 5.367%
9302 | 26-74.5 | -74.456 | 25.5824 | 1135.1889 | 184.4967 | 213.2541 | 258.263 | 298.5222 | 345.0592 | 5.385%
9303 | 26-74.5 | -74.7273 | 25.5824 | 1149.0017 | 184.5133 | 213.2082 | 258.1034 | 298.247 | 344.6364 | 5.398%
9304 | 26-75 | -74.9986 | 25.5824 | 1162.9136 | 184.5381 | 213.1735 | 257.9603 | 297.9936 | 344.242 | 5.413%
9305 | 26-75.5 | -75.27 | 25.5824 | 1176.921 | 184.5159 | 213.0777 | 257.7325 | 297.6328 | 343.7128 | 5.422%
9306 | 26-75.5 | -75.5413 | 25.5824 | 1191.0205 | 184.3533 | 212.799 | 257.2502 | 296.9493 | 342.7776 | 5.415%
9307 | 26-76 | -75.8126 | 25.5824 | 1205.2089 | 184.0803 | 212.3853 | 256.5926 | 296.0529 | 341.5846 | 5.394%
9308 | 26-76 | -76.0839 | 25.5824 | 1219.483 | 183.7159 | 211.8566 | 255.781 | 294.9656 | 340.1558 | 5.361%
9309 | 26-76.5 | -76.3553 | 25.5824 | 1233.8397 | 183.3242 | 211.2919 | 254.9182 | 293.8123 | 338.6427 | 5.325%
9310 | 26-76.5 | -76.6266 | 25.5824 | 1248.2762 | 183.0421 | 210.8871 | 254.3024 | 292.9912 | 337.5676 | 5.299%
9311 | 26-77 | -76.8979 | 25.5824 | 1262.7898 | 182.8019 | 210.5493 | 253.7974 | 292.3239 | 336.7 | 5.276%
9312 | 26-77 | -77.1692 | 25.5824 | 1277.3777 | 182.5388 | 210.1904 | 253.2755 | 291.6447 | 335.8278 | 5.248%
9313 | 26-77.5 | -77.4405 | 25.5824 | 1292.0373 | 182.2856 | 209.8621 | 252.8214 | 291.0709 | 335.1081 | 5.219%
9314 | 26-77.5 | -77.7119 | 25.5824 | 1306.7664 | 182.0029 | 209.5052 | 252.3411 | 290.4739 | 334.3701 | 5.184%
9315 | 26-78 | -77.9832 | 25.5824 | 1321.5623 | 181.6802 | 209.1032 | 251.8085 | 289.8185 | 333.5668 | 5.144%
9316 | 26-78.5 | -78.2545 | 25.5824 | 1336.423 | 181.3734 | 208.7417 | 251.3594 | 289.2897 | 332.9443 | 5.103%
9317 | 26-78.5 | -78.5258 | 25.5824 | 1351.3462 | 180.89 | 208.1636 | 250.6286 | 288.4184 | 331.9069 | 5.04%
9318 | 26-79 | -78.7971 | 25.5824 | 1366.3299 | 180.123 | 207.246 | 249.4435 | 286.9852 | 330.1784 | 4.943%
9319 | 26-79 | -79.0685 | 25.5824 | 1381.3719 | 179.0223 | 206.1223 | 248.0002 | 285.2474 | 328.0917 | 4.808%
9320 | 26-79.5 | -79.3398 | 25.5824 | 1396.4705 | 177.8888 | 205.0209 | 246.5827 | 283.5385 | 326.0374 | 4.672%
9321 | 26-79.5 | -79.6111 | 25.5824 | 1411.6237 | 176.9135 | 204.0591 | 245.3396 | 282.0351 | 324.2251 | 4.558%
9322 | 26-80 | -79.8824 | 25.5824 | 1426.8297 | 176.0578 | 203.2067 | 244.244 | 280.7152 | 322.6391 | 4.459%
9323 | 26-80 | -80.1537 | 25.5824 | 1442.0869 | 175.2358 | 202.3475 | 243.1208 | 279.3465 | 320.9774 | 4.366%
9324 | 26-80.5 | -80.4251 | 25.5824 | 1457.3936 | 174.4601 | 201.518 | 242.0231 | 277.9978 | 319.3278 | 4.281%
9325 | 26-80.5 | -80.6964 | 25.5824 | 1472.7481 | 173.7968 | 200.8276 | 241.1129 | 276.8824 | 317.9666 | 4.209%
9326 | 26-81 | -80.9677 | 25.5824 | 1488.1491 | 173.2535 | 200.2306 | 240.3142 | 275.894 | 316.7498 | 4.152%
9327 | 26-81 | -81.239 | 25.5824 | 1503.595 | 172.8774 | 199.7759 | 239.7056 | 275.1404 | 315.8215 | 4.112%
9328 | 26-81.5 | -81.5104 | 25.5824 | 1519.0843 | 172.6701 | 199.5261 | 239.3869 | 274.758 | 315.3634 | 4.088%
9329 | 26-82 | -81.7817 | 25.5824 | 1534.6158 | 172.4911 | 199.3074 | 239.1033 | 274.4141 | 314.9472 | 4.069%
9330 | 26-82 | -82.053 | 25.5824 | 1550.188 | 172.4983 | 199.3308 | 239.1552 | 274.4943 | 315.0631 | 4.068%
9331 | 26-82.5 | -82.3243 | 25.5824 | 1565.7999 | 172.8577 | 199.7988 | 239.8306 | 275.3682 | 316.1793 | 4.102%
9332 | 26-82.5 | -82.5956 | 25.5824 | 1581.4501 | 173.638 | 200.5961 | 240.9479 | 276.7895 | 317.9695 | 4.18%
9333 | 26-83 | -82.867 | 25.5824 | 1597.1374 | 174.5247 | 201.4749 | 242.1956 | 278.3887 | 319.9963 | 4.268%
9334 | 26-83 | -83.1383 | 25.5824 | 1612.8608 | 175.3105 | 202.3047 | 243.4173 | 279.9876 | 322.0574 | 4.343%
9335 | 26-83.5 | -83.4096 | 25.5824 | 1628.6191 | 175.9259 | 202.9598 | 244.4021 | 281.2909 | 323.752 | 4.4%
9336 | 26-83.5 | -83.6809 | 25.5824 | 1644.4113 | 176.4504 | 203.5448 | 245.304 | 282.5002 | 325.3405 | 4.446%
9337 | 26-84 | -83.9522 | 25.5824 | 1660.2364 | 176.9413 | 204.1192 | 246.2111 | 283.7316 | 326.9734 | 4.488%
9338 | 26-84 | -84.2236 | 25.5824 | 1676.0934 | 177.3602 | 204.6053 | 246.9984 | 284.8135 | 328.4208 | 4.521%
9339 | 26-84.5 | -84.4949 | 25.5824 | 1691.9813 | 177.6983 | 205.0464 | 247.7382 | 285.8469 | 329.82 | 4.545%
9340 | 26-85 | -84.7662 | 25.5824 | 1707.8993 | 177.948 | 205.455 | 248.4506 | 286.8598 | 331.2089 | 4.558%
9341 | 26-85 | -85.0375 | 25.5824 | 1723.8465 | 178.0454 | 205.6781 | 248.8972 | 287.5297 | 332.1603 | 4.557%
9342 | 26-85.5 | -85.3089 | 25.5824 | 1739.822 | 178.1267 | 205.8796 | 249.313 | 288.16 | 333.0616 | 4.553%
9343 | 26-85.5 | -85.5802 | 25.5824 | 1755.8249 | 178.2215 | 206.0974 | 249.7496 | 288.8156 | 333.9937 | 4.551%
9344 | 26-86 | -85.8515 | 25.5824 | 1771.8546 | 178.2395 | 206.1965 | 249.995 | 289.2089 | 334.575 | 4.544%
9345 | 26-86 | -86.1228 | 25.5824 | 1787.9102 | 178.2574 | 206.284 | 250.2081 | 289.549 | 335.0765 | 4.537%
9346 | 26-86.5 | -86.3941 | 25.5824 | 1803.991 | 178.281 | 206.3657 | 250.3944 | 289.8412 | 335.5033 | 4.534%
9347 | 26-86.5 | -86.6655 | 25.5824 | 1820.0963 | 178.2175 | 206.3234 | 250.3936 | 289.8846 | 335.6053 | 4.522%
9348 | 26-87 | -86.9368 | 25.5824 | 1836.2254 | 178.1458 | 206.285 | 250.4187 | 289.9768 | 335.7853 | 4.508%
9349 | 26-87 | -87.2081 | 25.5824 | 1852.3776 | 178.0613 | 206.244 | 250.4606 | 290.1059 | 336.0283 | 4.491%
9350 | 26-87.5 | -87.4794 | 25.5824 | 1868.5523 | 177.8739 | 206.0694 | 250.3169 | 289.9994 | 335.9748 | 4.464%
9351 | 26-88 | -87.7507 | 25.5824 | 1884.7488 | 177.6319 | 205.837 | 250.1118 | 289.8298 | 335.8571 | 4.43%
9352 | 26-88 | -88.0221 | 25.5824 | 1900.9666 | 177.3239 | 205.5308 | 249.8216 | 289.5654 | 335.6342 | 4.388%
9353 | 26-88.5 | -88.2934 | 25.5824 | 1917.205 | 176.8915 | 205.0661 | 249.3155 | 289.0306 | 335.0748 | 4.334%
9354 | 26-88.5 | -88.5647 | 25.5824 | 1933.4635 | 176.4342 | 204.5903 | 248.8248 | 288.5389 | 334.5946 | 4.275%
9355 | 26-89 | -88.836 | 25.5824 | 1949.7415 | 175.9419 | 204.0869 | 248.3213 | 288.051 | 334.1404 | 4.213%
9356 | 26-89 | -89.1074 | 25.5824 | 1966.0385 | 175.3665 | 203.477 | 247.6723 | 287.3801 | 333.4575 | 4.143%
9357 | 26-89.5 | -89.3787 | 25.5824 | 1982.3539 | 174.7918 | 202.8818 | 247.0634 | 286.7752 | 332.8737 | 4.073%
9358 | 26-89.5 | -89.65 | 25.5824 | 1998.6874 | 174.1979 | 202.2713 | 246.4436 | 286.1646 | 332.2912 | 4.002%
9359 | 26-90 | -89.9213 | 25.5824 | 2015.0383 | 173.5425 | 201.5801 | 245.7005 | 285.3883 | 331.4901 | 3.928%
9360 | 26-90 | -90.1926 | 25.5824 | 2031.4062 | 172.9123 | 200.9171 | 244.9768 | 284.6215 | 330.6849 | 3.858%
9361 | 26-90.5 | -90.464 | 25.5824 | 2047.7907 | 172.2781 | 200.2438 | 244.2154 | 283.7888 | 329.7774 | 3.791%
9362 | 26-90.5 | -90.7353 | 25.5824 | 2064.1913 | 171.592 | 199.5035 | 243.3362 | 282.7876 | 328.6375 | 3.721%
9363 | 26-50 | -50.0371 | 25.8538 | 993.6299 | 111.5278 | 146.3048 | 185.2568 | 210.1621 | 238.4176 | 0.7521%
9364 | 26-50.5 | -50.3084 | 25.8538 | 981.6638 | 113.2501 | 148.7348 | 186.7843 | 211.9671 | 240.5473 | 0.7921%
9365 | 26-50.5 | -50.5797 | 25.8538 | 969.8656 | 114.9611 | 151.1281 | 188.2775 | 213.7223 | 242.6082 | 0.8339%
9366 | 26-51 | -50.851 | 25.8538 | 958.2415 | 116.6657 | 153.4747 | 189.7503 | 215.4636 | 244.6637 | 0.8778%
9367 | 26-51 | -51.1224 | 25.8538 | 946.7978 | 118.3909 | 155.7577 | 191.2442 | 217.258 | 246.8128 | 0.9245%
9368 | 26-51.5 | -51.3937 | 25.8538 | 935.5412 | 120.0422 | 157.8776 | 192.6516 | 218.954 | 248.8502 | 0.9713%
9369 | 26-51.5 | -51.665 | 25.8538 | 924.4787 | 121.6349 | 159.8515 | 194.0033 | 220.6013 | 250.8491 | 1.018%
9370 | 26-52 | -51.9363 | 25.8538 | 913.6173 | 123.1924 | 161.6928 | 195.3388 | 222.2569 | 252.8883 | 1.067%
9371 | 26-52 | -52.2077 | 25.8538 | 902.9642 | 124.6468 | 163.3322 | 196.5519 | 223.7515 | 254.7195 | 1.113%
9372 | 26-52.5 | -52.479 | 25.8538 | 892.5271 | 126.0423 | 164.8242 | 197.709 | 225.1846 | 256.4836 | 1.159%
9373 | 26-53 | -52.7503 | 25.8538 | 882.3134 | 127.4096 | 166.1921 | 198.8578 | 226.6268 | 258.2791 | 1.205%
9374 | 26-53 | -53.0216 | 25.8538 | 872.3313 | 128.6707 | 167.3596 | 199.8995 | 227.932 | 259.9016 | 1.249%
9375 | 26-53.5 | -53.2929 | 25.8538 | 862.5886 | 129.8958 | 168.4132 | 200.9228 | 229.2237 | 261.5171 | 1.292%
9376 | 26-53.5 | -53.5643 | 25.8538 | 853.0937 | 131.1212 | 169.3789 | 201.9711 | 230.5597 | 263.201 | 1.336%
9377 | 26-54 | -53.8356 | 25.8538 | 843.8549 | 132.2675 | 170.1832 | 202.9495 | 231.8041 | 264.7673 | 1.378%
9378 | 26-54 | -54.1069 | 25.8538 | 834.8808 | 133.4457 | 170.9704 | 203.9868 | 233.1302 | 266.4434 | 1.422%
9379 | 26-54.5 | -54.3782 | 25.8538 | 826.18 | 134.6941 | 171.7809 | 205.1241 | 234.5895 | 268.2939 | 1.47%
9380 | 26-54.5 | -54.6495 | 25.8538 | 817.7613 | 135.9097 | 172.5668 | 206.2198 | 235.979 | 270.0394 | 1.518%
9381 | 26-55 | -54.9209 | 25.8538 | 809.6335 | 137.2051 | 173.4205 | 207.403 | 237.4745 | 271.9131 | 1.571%
9382 | 26-55 | -55.1922 | 25.8538 | 801.8054 | 138.6029 | 174.3573 | 208.6943 | 239.1016 | 273.9466 | 1.63%
9383 | 26-55.5 | -55.4635 | 25.8538 | 794.2859 | 139.9947 | 175.2886 | 209.9312 | 240.6248 | 275.8139 | 1.691%
9384 | 26-55.5 | -55.7348 | 25.8538 | 787.084 | 141.4637 | 176.272 | 211.2388 | 242.2363 | 277.7903 | 1.758%
9385 | 26-56 | -56.0061 | 25.8538 | 780.2084 | 143.0148 | 177.3104 | 212.6223 | 243.9436 | 279.8867 | 1.831%
9386 | 26-56.5 | -56.2775 | 25.8538 | 773.6678 | 144.5497 | 178.3272 | 213.9489 | 245.5586 | 281.8464 | 1.906%
9387 | 26-56.5 | -56.5488 | 25.8538 | 767.4709 | 146.1591 | 179.3843 | 215.3295 | 247.2404 | 283.8878 | 1.987%
9388 | 26-57 | -56.8201 | 25.8538 | 761.626 | 147.8351 | 180.4752 | 216.7521 | 248.9716 | 285.9877 | 2.076%
9389 | 26-57 | -57.0914 | 25.8538 | 756.1413 | 149.5016 | 181.5421 | 218.1201 | 250.6179 | 287.9643 | 2.167%
9390 | 26-57.5 | -57.3628 | 25.8538 | 751.0247 | 151.2552 | 182.6511 | 219.5403 | 252.3254 | 290.0126 | 2.268%
9391 | 26-57.5 | -57.6341 | 25.8538 | 746.2839 | 153.0685 | 183.7812 | 220.9773 | 254.0447 | 292.066 | 2.376%
9392 | 26-58 | -57.9054 | 25.8538 | 741.9259 | 154.8267 | 184.8574 | 222.3158 | 255.6216 | 293.9222 | 2.486%
9393 | 26-58 | -58.1767 | 25.8538 | 737.9577 | 156.6012 | 185.9681 | 223.7034 | 257.2617 | 295.8586 | 2.603%
9394 | 26-58.5 | -58.448 | 25.8538 | 734.3856 | 158.3242 | 187.0739 | 225.073 | 258.8705 | 297.7471 | 2.722%
9395 | 26-58.5 | -58.7194 | 25.8538 | 731.2153 | 159.9055 | 188.0802 | 226.2741 | 260.243 | 299.3149 | 2.837%
9396 | 26-59 | -58.9907 | 25.8538 | 728.4521 | 161.444 | 189.0851 | 227.4808 | 261.6283 | 300.9048 | 2.955%
9397 | 26-59.5 | -59.262 | 25.8538 | 726.1007 | 162.8951 | 190.0571 | 228.6416 | 262.9555 | 302.4217 | 3.071%
9398 | 26-59.5 | -59.5333 | 25.8538 | 724.1651 | 164.207 | 190.9426 | 229.6736 | 264.1131 | 303.7188 | 3.181%
9399 | 26-60 | -59.8046 | 25.8538 | 722.6486 | 165.4677 | 191.8308 | 230.7266 | 265.3103 | 305.0794 | 3.29%
9400 | 26-60 | -60.076 | 25.8538 | 721.5539 | 166.6389 | 192.6977 | 231.7628 | 266.4958 | 306.4355 | 3.396%
9401 | 26-60.5 | -60.3473 | 25.8538 | 720.8829 | 167.6872 | 193.5116 | 232.7307 | 267.599 | 307.6925 | 3.494%
9402 | 26-60.5 | -60.6186 | 25.8538 | 720.6368 | 168.6747 | 194.3391 | 233.7388 | 268.769 | 309.0502 | 3.589%
9403 | 26-61 | -60.8899 | 25.8538 | 720.8161 | 169.5509 | 195.1455 | 234.7345 | 269.9364 | 310.4182 | 3.676%
9404 | 26-61 | -61.1613 | 25.8538 | 721.4203 | 170.2918 | 195.9088 | 235.6851 | 271.0578 | 311.7403 | 3.752%
9405 | 26-61.5 | -61.4326 | 25.8538 | 722.4485 | 170.9981 | 196.7141 | 236.7193 | 272.304 | 313.2392 | 3.825%
9406 | 26-61.5 | -61.7039 | 25.8538 | 723.8989 | 171.6581 | 197.5095 | 237.754 | 273.5621 | 314.7646 | 3.894%
9407 | 26-62 | -61.9752 | 25.8538 | 725.7688 | 172.2827 | 198.28 | 238.7643 | 274.7971 | 316.2693 | 3.96%
9408 | 26-62 | -62.2465 | 25.8538 | 728.0551 | 172.9558 | 199.1351 | 239.9226 | 276.2426 | 318.063 | 4.028%
9409 | 26-62.5 | -62.5179 | 25.8538 | 730.7539 | 173.6334 | 200.0038 | 241.1107 | 277.7343 | 319.9234 | 4.097%
9410 | 26-63 | -62.7892 | 25.8538 | 733.8606 | 174.3017 | 200.8605 | 242.2823 | 279.205 | 321.7572 | 4.166%
9411 | 26-63 | -63.0605 | 25.8538 | 737.3699 | 175.0117 | 201.7785 | 243.549 | 280.8037 | 323.76 | 4.238%
9412 | 26-63.5 | -63.3318 | 25.8538 | 741.2763 | 175.7095 | 202.6776 | 244.7848 | 282.3599 | 325.7055 | 4.31%
9413 | 26-63.5 | -63.6031 | 25.8538 | 745.5735 | 176.3807 | 203.5366 | 245.9574 | 283.8302 | 327.537 | 4.381%
9414 | 26-64 | -63.8745 | 25.8538 | 750.2546 | 177.0642 | 204.4136 | 247.1578 | 285.3378 | 329.4177 | 4.453%
9415 | 26-64 | -64.1458 | 25.8538 | 755.3126 | 177.7063 | 205.2324 | 248.2714 | 286.7308 | 331.1494 | 4.522%
9416 | 26-64.5 | -64.4171 | 25.8538 | 760.74 | 178.3087 | 205.9955 | 249.3018 | 288.0142 | 332.7391 | 4.587%
9417 | 26-64.5 | -64.6884 | 25.8538 | 766.5288 | 178.9132 | 206.7603 | 250.3331 | 289.298 | 334.3286 | 4.654%
9418 | 26-65 | -64.9598 | 25.8538 | 772.671 | 179.4708 | 207.4509 | 251.2434 | 290.4146 | 335.6936 | 4.718%
9419 | 26-65 | -65.2311 | 25.8538 | 779.1581 | 179.9985 | 208.0932 | 252.0727 | 291.4182 | 336.9057 | 4.78%
9420 | 26-65.5 | -65.5024 | 25.8538 | 785.9816 | 180.5391 | 208.7502 | 252.9201 | 292.443 | 338.1427 | 4.844%
9421 | 26-66 | -65.7737 | 25.8538 | 793.1328 | 181.0164 | 209.3082 | 253.606 | 293.2448 | 339.0798 | 4.905%
9422 | 26-66 | -66.045 | 25.8538 | 800.603 | 181.4517 | 209.8026 | 254.1906 | 293.9082 | 339.8325 | 4.963%
9423 | 26-66.5 | -66.3164 | 25.8538 | 808.3831 | 181.8863 | 210.2975 | 254.7784 | 294.5774 | 340.5943 | 5.021%
9424 | 26-66.5 | -66.5877 | 25.8538 | 816.4644 | 182.2455 | 210.6945 | 255.23 | 295.0739 | 341.1388 | 5.071%
9425 | 26-67 | -66.859 | 25.8538 | 824.838 | 182.5658 | 211.0473 | 255.6293 | 295.5111 | 341.6158 | 5.117%
9426 | 26-67 | -67.1303 | 25.8538 | 833.4951 | 182.8852 | 211.4092 | 256.056 | 295.9941 | 342.1625 | 5.161%
9427 | 26-67.5 | -67.4016 | 25.8538 | 842.4268 | 183.1411 | 211.6935 | 256.3817 | 296.3545 | 342.5602 | 5.197%
9428 | 26-67.5 | -67.673 | 25.8538 | 851.6246 | 183.3806 | 211.9655 | 256.7036 | 296.7198 | 342.9749 | 5.231%
9429 | 26-68 | -67.9443 | 25.8538 | 861.0798 | 183.6346 | 212.268 | 257.0842 | 297.1721 | 343.512 | 5.264%
9430 | 26-68 | -68.2156 | 25.8538 | 870.7841 | 183.8261 | 212.4876 | 257.347 | 297.4731 | 343.8567 | 5.291%
9431 | 26-68.5 | -68.4869 | 25.8538 | 880.7291 | 183.9991 | 212.689 | 257.5931 | 297.7595 | 344.1897 | 5.314%
9432 | 26-69 | -68.7583 | 25.8538 | 890.9069 | 184.1769 | 212.9064 | 257.8753 | 298.1021 | 344.6046 | 5.337%
9433 | 26-69 | -69.0296 | 25.8538 | 901.3094 | 184.27 | 213.0139 | 258.0053 | 298.252 | 344.7773 | 5.35%
9434 | 26-69.5 | -69.3009 | 25.8538 | 911.9291 | 184.3523 | 213.1212 | 258.1546 | 298.4416 | 345.0161 | 5.359%
9435 | 26-69.5 | -69.5722 | 25.8538 | 922.7582 | 184.452 | 213.2695 | 258.3875 | 298.7573 | 345.4349 | 5.367%
9436 | 26-70 | -69.8435 | 25.8538 | 933.7896 | 184.4666 | 213.3124 | 258.481 | 298.9017 | 345.644 | 5.365%
9437 | 26-70 | -70.1149 | 25.8538 | 945.0161 | 184.4736 | 213.3499 | 258.5736 | 299.0502 | 345.8634 | 5.361%
9438 | 26-70.5 | -70.3862 | 25.8538 | 956.4309 | 184.492 | 213.4058 | 258.6969 | 299.2413 | 346.1406 | 5.358%
9439 | 26-70.5 | -70.6575 | 25.8538 | 968.0271 | 184.4487 | 213.3715 | 258.6804 | 299.2443 | 346.1696 | 5.349%
9440 | 26-71 | -70.9288 | 25.8538 | 979.7984 | 184.4103 | 213.3377 | 258.6566 | 299.2319 | 346.1729 | 5.342%
9441 | 26-71 | -71.2001 | 25.8538 | 991.7384 | 184.3844 | 213.3138 | 258.6377 | 299.2188 | 346.1682 | 5.337%
9442 | 26-71.5 | -71.4715 | 25.8538 | 1003.8412 | 184.3145 | 213.2184 | 258.4987 | 299.0379 | 345.9356 | 5.33%
9443 | 26-71.5 | -71.7428 | 25.8538 | 1016.1008 | 184.2759 | 213.1618 | 258.4112 | 298.9204 | 345.781 | 5.327%
9444 | 26-72 | -72.0141 | 25.8538 | 1028.5117 | 184.2694 | 213.1453 | 258.377 | 298.8685 | 345.7068 | 5.327%
9445 | 26-72.5 | -72.2854 | 25.8538 | 1041.0684 | 184.2511 | 213.1047 | 258.297 | 298.749 | 345.5375 | 5.328%
9446 | 26-72.5 | -72.5568 | 25.8538 | 1053.7656 | 184.3087 | 213.164 | 258.357 | 298.8083 | 345.5946 | 5.337%
9447 | 26-73 | -72.8281 | 25.8538 | 1066.5982 | 184.4143 | 213.2825 | 258.4951 | 298.9634 | 345.7689 | 5.352%
9448 | 26-73 | -73.0994 | 25.8538 | 1079.5615 | 184.4464 | 213.2861 | 258.4459 | 298.8597 | 345.5949 | 5.362%
9449 | 26-73.5 | -73.3707 | 25.8538 | 1092.6508 | 184.5071 | 213.3223 | 258.4352 | 298.7998 | 345.4706 | 5.377%
9450 | 26-73.5 | -73.642 | 25.8538 | 1105.8614 | 184.5765 | 213.3651 | 258.4272 | 298.738 | 345.3387 | 5.393%
9451 | 26-74 | -73.9134 | 25.8538 | 1119.1891 | 184.6084 | 213.3484 | 258.3213 | 298.5407 | 345.024 | 5.406%
9452 | 26-74 | -74.1847 | 25.8538 | 1132.6298 | 184.6768 | 213.3824 | 258.2905 | 298.4423 | 344.8378 | 5.424%
9453 | 26-74.5 | -74.456 | 25.8538 | 1146.1793 | 184.7511 | 213.4232 | 258.2677 | 298.353 | 344.6619 | 5.442%
9454 | 26-74.5 | -74.7273 | 25.8538 | 1159.8339 | 184.7766 | 213.3911 | 258.1309 | 298.1093 | 344.2816 | 5.457%
9455 | 26-75 | -74.9986 | 25.8538 | 1173.5898 | 184.8087 | 213.3668 | 258.0034 | 297.8768 | 343.9146 | 5.472%
9456 | 26-75.5 | -75.27 | 25.8538 | 1187.4435 | 184.8007 | 213.2896 | 257.8015 | 297.549 | 343.4272 | 5.483%
9457 | 26-75.5 | -75.5413 | 25.8538 | 1201.3916 | 184.6755 | 213.0604 | 257.3894 | 296.9557 | 342.6067 | 5.481%
9458 | 26-76 | -75.8126 | 25.8538 | 1215.4308 | 184.4742 | 212.7414 | 256.8657 | 296.2307 | 341.631 | 5.467%
9459 | 26-76 | -76.0839 | 25.8538 | 1229.5578 | 184.1949 | 212.3262 | 256.2156 | 295.351 | 340.4665 | 5.444%
9460 | 26-76.5 | -76.3553 | 25.8538 | 1243.7697 | 183.8669 | 211.8491 | 255.4814 | 294.3659 | 339.1706 | 5.415%
9461 | 26-76.5 | -76.6266 | 25.8538 | 1258.0636 | 183.6072 | 211.4795 | 254.923 | 293.624 | 338.2019 | 5.39%
9462 | 26-77 | -76.8979 | 25.8538 | 1272.4367 | 183.3585 | 211.1369 | 254.4204 | 292.9668 | 337.3544 | 5.365%
9463 | 26-77 | -77.1692 | 25.8538 | 1286.8862 | 183.0719 | 210.7538 | 253.8739 | 292.2634 | 336.4589 | 5.333%
9464 | 26-77.5 | -77.4405 | 25.8538 | 1301.4095 | 182.7927 | 210.3985 | 253.3919 | 291.6614 | 335.7114 | 5.299%
9465 | 26-77.5 | -77.7119 | 25.8538 | 1316.0043 | 182.4799 | 210.0095 | 252.8771 | 291.0284 | 334.9363 | 5.259%
9466 | 26-78 | -77.9832 | 25.8538 | 1330.668 | 182.1219 | 209.5694 | 252.3023 | 290.3278 | 334.0847 | 5.213%
9467 | 26-78.5 | -78.2545 | 25.8538 | 1345.3985 | 181.7759 | 209.1655 | 251.8068 | 289.7494 | 333.4099 | 5.166%
9468 | 26-78.5 | -78.5258 | 25.8538 | 1360.1934 | 181.2243 | 208.5088 | 250.9813 | 288.7693 | 332.2473 | 5.092%
9469 | 26-79 | -78.7971 | 25.8538 | 1375.0507 | 180.3198 | 207.4406 | 249.6034 | 287.1046 | 330.2414 | 4.977%
9470 | 26-79 | -79.0685 | 25.8538 | 1389.9683 | 178.9649 | 206.0744 | 247.8409 | 284.976 | 327.6784 | 4.811%
9471 | 26-79.5 | -79.3398 | 25.8538 | 1404.9443 | 177.5259 | 204.6818 | 246.0375 | 282.7926 | 325.0435 | 4.64%
9472 | 26-79.5 | -79.6111 | 25.8538 | 1419.9767 | 176.2517 | 203.4324 | 244.4126 | 280.8195 | 322.6562 | 4.493%
9473 | 26-80 | -79.8824 | 25.8538 | 1435.0638 | 175.1347 | 202.3328 | 242.99 | 279.0981 | 320.5795 | 4.366%
9474 | 26-80 | -80.1537 | 25.8538 | 1450.2038 | 174.0646 | 201.252 | 241.5755 | 277.3731 | 318.4839 | 4.248%
9475 | 26-80.5 | -80.4251 | 25.8538 | 1465.395 | 173.0333 | 200.2058 | 240.1948 | 275.68 | 316.4168 | 4.137%
9476 | 26-80.5 | -80.6964 | 25.8538 | 1480.6358 | 172.0966 | 199.2878 | 238.9896 | 274.2072 | 314.624 | 4.038%
9477 | 26-81 | -80.9677 | 25.8538 | 1495.9246 | 171.3312 | 198.5006 | 237.946 | 272.9235 | 313.0522 | 3.959%
9478 | 26-81 | -81.239 | 25.8538 | 1511.26 | 170.8187 | 197.9146 | 237.1723 | 271.974 | 311.8916 | 3.906%
9479 | 26-81.5 | -81.5104 | 25.8538 | 1526.6404 | 170.549 | 197.5952 | 236.7734 | 271.5025 | 311.3347 | 3.876%
9480 | 26-82 | -81.7817 | 25.8538 | 1542.0645 | 170.3215 | 197.3254 | 236.4359 | 271.1029 | 310.8621 | 3.851%
9481 | 26-82 | -82.053 | 25.8538 | 1557.531 | 170.3089 | 197.3354 | 236.4868 | 271.1953 | 311.0071 | 3.848%
9482 | 26-82.5 | -82.3243 | 25.8538 | 1573.0385 | 170.7083 | 197.8517 | 237.2469 | 272.1896 | 312.2883 | 3.884%
9483 | 26-82.5 | -82.5956 | 25.8538 | 1588.5858 | 171.6221 | 198.7582 | 238.532 | 273.8354 | 314.3725 | 3.97%
9484 | 26-83 | -82.867 | 25.8538 | 1604.1717 | 172.6706 | 199.7651 | 239.9729 | 275.6904 | 316.7319 | 4.07%
9485 | 26-83 | -83.1383 | 25.8538 | 1619.7951 | 173.6094 | 200.7163 | 241.3791 | 277.5346 | 319.1127 | 4.156%
9486 | 26-83.5 | -83.4096 | 25.8538 | 1635.4547 | 174.3692 | 201.487 | 242.5375 | 279.0673 | 321.1053 | 4.226%
9487 | 26-83.5 | -83.6809 | 25.8538 | 1651.1497 | 175.0534 | 202.1966 | 243.6215 | 280.5137 | 322.9982 | 4.287%
9488 | 26-84 | -83.9522 | 25.8538 | 1666.8788 | 175.7302 | 202.9127 | 244.7296 | 282.0025 | 324.9568 | 4.346%
9489 | 26-84 | -84.2236 | 25.8538 | 1682.6411 | 176.3604 | 203.558 | 245.7345 | 283.3572 | 326.7434 | 4.401%
9490 | 26-84.5 | -84.4949 | 25.8538 | 1698.4356 | 176.8665 | 204.1287 | 246.6486 | 284.6069 | 328.4093 | 4.442%
9491 | 26-85 | -84.7662 | 25.8538 | 1714.2614 | 177.2085 | 204.6189 | 247.468 | 285.7502 | 329.9566 | 4.466%
9492 | 26-85 | -85.0375 | 25.8538 | 1730.1176 | 177.3355 | 204.8752 | 247.953 | 286.463 | 330.9557 | 4.468%
9493 | 26-85.5 | -85.3089 | 25.8538 | 1746.0033 | 177.4436 | 205.1047 | 248.398 | 287.1229 | 331.8863 | 4.468%
9494 | 26-85.5 | -85.5802 | 25.8538 | 1761.9176 | 177.5728 | 205.3583 | 248.8718 | 287.8159 | 332.8554 | 4.471%
9495 | 26-86 | -85.8515 | 25.8538 | 1777.8598 | 177.6324 | 205.4982 | 249.1547 | 288.2422 | 333.4627 | 4.47%
9496 | 26-86 | -86.1228 | 25.8538 | 1793.829 | 177.6989 | 205.631 | 249.4053 | 288.6104 | 333.9791 | 4.471%
9497 | 26-86.5 | -86.3941 | 25.8538 | 1809.8245 | 177.7785 | 205.7629 | 249.629 | 288.9254 | 334.4086 | 4.476%
9498 | 26-86.5 | -86.6655 | 25.8538 | 1825.8455 | 177.7778 | 205.7763 | 249.6686 | 288.9919 | 334.5099 | 4.474%
9499 | 26-87 | -86.9368 | 25.8538 | 1841.8914 | 177.7742 | 205.799 | 249.7396 | 289.1124 | 334.6941 | 4.47%
9500 | 26-87 | -87.2081 | 25.8538 | 1857.9614 | 177.763 | 205.8248 | 249.8335 | 289.2765 | 334.9485 | 4.464%
9501 | 26-87.5 | -87.4794 | 25.8538 | 1874.0549 | 177.6512 | 205.7214 | 249.7502 | 289.2172 | 334.9233 | 4.448%
9502 | 26-88 | -87.7507 | 25.8538 | 1890.1712 | 177.4858 | 205.5645 | 249.6157 | 289.1108 | 334.8574 | 4.424%
9503 | 26-88 | -88.0221 | 25.8538 | 1906.3096 | 177.2534 | 205.3353 | 249.4017 | 288.9196 | 334.702 | 4.392%
9504 | 26-88.5 | -88.2934 | 25.8538 | 1922.4697 | 176.89 | 204.941 | 248.9662 | 288.4533 | 334.2064 | 4.347%
9505 | 26-88.5 | -88.5647 | 25.8538 | 1938.6508 | 176.4957 | 204.5298 | 248.5403 | 288.0248 | 333.7856 | 4.297%
9506 | 26-89 | -88.836 | 25.8538 | 1954.8522 | 176.0601 | 204.0851 | 248.0968 | 287.5964 | 333.3887 | 4.241%
9507 | 26-89 | -89.1074 | 25.8538 | 1971.0736 | 175.5338 | 203.5277 | 247.5044 | 286.9849 | 332.7675 | 4.176%
9508 | 26-89.5 | -89.3787 | 25.8538 | 1987.3142 | 175.0018 | 202.9823 | 246.9566 | 286.4513 | 332.2669 | 4.11%
9509 | 26-89.5 | -89.65 | 25.8538 | 2003.5737 | 174.4459 | 202.4194 | 246.4035 | 285.9256 | 331.7916 | 4.041%
9510 | 26-90 | -89.9213 | 25.8538 | 2019.8515 | 173.828 | 201.7751 | 245.7351 | 285.2513 | 331.1265 | 3.969%
9511 | 26-90 | -90.1926 | 25.8538 | 2036.1471 | 173.2347 | 201.1576 | 245.0899 | 284.5958 | 330.4736 | 3.9%
9512 | 26-90.5 | -90.464 | 25.8538 | 2052.46 | 172.6354 | 200.5262 | 244.4062 | 283.8765 | 329.7245 | 3.834%
9513 | 26-90.5 | -90.7353 | 25.8538 | 2068.7898 | 171.9816 | 199.8198 | 243.595 | 282.9775 | 328.7301 | 3.765%
9514 | 26-50 | -50.0371 | 26.1251 | 1006.8393 | 111.2049 | 145.7039 | 184.7495 | 209.438 | 237.4273 | 0.7423%
9515 | 26-50.5 | -50.3084 | 26.1251 | 995.0562 | 112.9024 | 148.1039 | 186.253 | 211.2139 | 239.5217 | 0.7812%
9516 | 26-50.5 | -50.5797 | 26.1251 | 983.4424 | 114.5965 | 150.4832 | 187.7304 | 212.9487 | 241.5565 | 0.8221%
9517 | 26-51 | -50.851 | 26.1251 | 972.0039 | 116.2928 | 152.8323 | 189.1963 | 214.6799 | 243.5979 | 0.8653%
9518 | 26-51 | -51.1224 | 26.1251 | 960.7471 | 118.019 | 155.1361 | 190.6938 | 216.4774 | 245.7493 | 0.9116%
9519 | 26-51.5 | -51.3937 | 26.1251 | 949.6785 | 119.6764 | 157.2848 | 192.1082 | 218.1793 | 247.7909 | 0.9581%
9520 | 26-51.5 | -51.665 | 26.1251 | 938.8047 | 121.2783 | 159.2933 | 193.4672 | 219.831 | 249.79 | 1.005%
9521 | 26-52 | -51.9363 | 26.1251 | 928.1327 | 122.8477 | 161.1744 | 194.81 | 221.4887 | 251.8244 | 1.053%
9522 | 26-52 | -52.2077 | 26.1251 | 917.6695 | 124.3158 | 162.8587 | 196.0295 | 222.9828 | 253.646 | 1.1%
9523 | 26-52.5 | -52.479 | 26.1251 | 907.4223 | 125.7232 | 164.3949 | 197.1885 | 224.4092 | 255.3922 | 1.146%
9524 | 26-53 | -52.7503 | 26.1251 | 897.3987 | 127.098 | 165.8024 | 198.3329 | 225.8371 | 257.1606 | 1.192%
9525 | 26-53 | -53.0216 | 26.1251 | 887.6061 | 128.3643 | 167.0059 | 199.3651 | 227.1215 | 258.7477 | 1.236%
9526 | 26-53.5 | -53.2929 | 26.1251 | 878.0524 | 129.5893 | 168.0876 | 200.3723 | 228.3848 | 260.3193 | 1.279%
9527 | 26-53.5 | -53.5643 | 26.1251 | 868.7455 | 130.807 | 169.0706 | 201.3965 | 229.6835 | 261.9493 | 1.323%
9528 | 26-54 | -53.8356 | 26.1251 | 859.6933 | 131.9411 | 169.8792 | 202.3463 | 230.886 | 263.4568 | 1.364%
9529 | 26-54 | -54.1069 | 26.1251 | 850.9041 | 133.1031 | 170.6616 | 203.3523 | 232.1677 | 265.0721 | 1.407%
9530 | 26-54.5 | -54.3782 | 26.1251 | 842.3862 | 134.3314 | 171.4581 | 204.4556 | 233.5802 | 266.8596 | 1.454%
9531 | 26-54.5 | -54.6495 | 26.1251 | 834.1478 | 135.5229 | 172.22 | 205.5122 | 234.9158 | 268.5327 | 1.501%
9532 | 26-55 | -54.9209 | 26.1251 | 826.1973 | 136.7951 | 173.0508 | 206.6598 | 236.3628 | 270.3419 | 1.552%
9533 | 26-55 | -55.1922 | 26.1251 | 818.5432 | 138.1719 | 173.9675 | 207.9213 | 237.9505 | 272.324 | 1.61%
9534 | 26-55.5 | -55.4635 | 26.1251 | 811.1938 | 139.5439 | 174.8811 | 209.1335 | 239.4423 | 274.1513 | 1.67%
9535 | 26-55.5 | -55.7348 | 26.1251 | 804.1576 | 140.9962 | 175.8511 | 210.424 | 241.0329 | 276.1021 | 1.736%
9536 | 26-56 | -56.0061 | 26.1251 | 797.4429 | 142.5352 | 176.8812 | 211.7985 | 242.7306 | 278.1879 | 1.808%
9537 | 26-56.5 | -56.2775 | 26.1251 | 791.0578 | 144.0619 | 177.8936 | 213.1212 | 244.3421 | 280.1445 | 1.882%
9538 | 26-56.5 | -56.5488 | 26.1251 | 785.0104 | 145.6653 | 178.9492 | 214.5032 | 246.0281 | 282.1937 | 1.963%
9539 | 26-57 | -56.8201 | 26.1251 | 779.3086 | 147.3391 | 180.0422 | 215.934 | 247.7735 | 284.3151 | 2.05%
9540 | 26-57 | -57.0914 | 26.1251 | 773.9601 | 149.0072 | 181.1155 | 217.318 | 249.4453 | 286.3291 | 2.142%
9541 | 26-57.5 | -57.3628 | 26.1251 | 768.9722 | 150.7635 | 182.2323 | 218.7582 | 251.1849 | 288.4248 | 2.241%
9542 | 26-57.5 | -57.6341 | 26.1251 | 764.352 | 152.5809 | 183.3716 | 220.2189 | 252.9425 | 290.5349 | 2.349%
9543 | 26-58 | -57.9054 | 26.1251 | 760.1063 | 154.3457 | 184.4578 | 221.5837 | 254.5621 | 292.4543 | 2.459%
9544 | 26-58 | -58.1767 | 26.1251 | 756.2413 | 156.1344 | 185.58 | 223.0024 | 256.2526 | 294.4656 | 2.576%
9545 | 26-58.5 | -58.448 | 26.1251 | 752.7629 | 157.8795 | 186.6988 | 224.4069 | 257.9182 | 296.4385 | 2.695%
9546 | 26-58.5 | -58.7194 | 26.1251 | 749.6766 | 159.4839 | 187.7197 | 225.646 | 259.3524 | 298.0979 | 2.811%
9547 | 26-59 | -58.9907 | 26.1251 | 746.9872 | 161.0476 | 188.742 | 226.8956 | 260.806 | 299.7881 | 2.929%
9548 | 26-59.5 | -59.262 | 26.1251 | 744.6989 | 162.5239 | 189.731 | 228.098 | 262.1994 | 301.4022 | 3.045%
9549 | 26-59.5 | -59.5333 | 26.1251 | 742.8156 | 163.8572 | 190.6271 | 229.1597 | 263.4058 | 302.7724 | 3.156%
9550 | 26-60 | -59.8046 | 26.1251 | 741.3402 | 165.1369 | 191.5214 | 230.2351 | 264.6417 | 304.1923 | 3.266%
9551 | 26-60 | -60.076 | 26.1251 | 740.2753 | 166.3237 | 192.389 | 231.2844 | 265.8529 | 305.59 | 3.371%
9552 | 26-60.5 | -60.3473 | 26.1251 | 739.6226 | 167.3827 | 193.1966 | 232.2534 | 266.9648 | 306.8655 | 3.47%
9553 | 26-60.5 | -60.6186 | 26.1251 | 739.3833 | 168.3769 | 194.0114 | 233.2512 | 268.1273 | 308.2195 | 3.564%
9554 | 26-61 | -60.8899 | 26.1251 | 739.5576 | 169.2565 | 194.8002 | 234.2275 | 269.2737 | 309.5649 | 3.651%
9555 | 26-61 | -61.1613 | 26.1251 | 740.1454 | 169.9998 | 195.5436 | 235.1526 | 270.3642 | 310.8495 | 3.726%
9556 | 26-61.5 | -61.4326 | 26.1251 | 741.1456 | 170.7063 | 196.3279 | 236.1568 | 271.5721 | 312.2994 | 3.799%
9557 | 26-61.5 | -61.7039 | 26.1251 | 742.5566 | 171.3604 | 197.1031 | 237.1615 | 272.7905 | 313.7734 | 3.867%
9558 | 26-62 | -61.9752 | 26.1251 | 744.376 | 171.9741 | 197.8568 | 238.1464 | 273.9914 | 315.2334 | 3.931%
9559 | 26-62 | -62.2465 | 26.1251 | 746.6009 | 172.6385 | 198.6988 | 239.2839 | 275.4088 | 316.9894 | 3.999%
9560 | 26-62.5 | -62.5179 | 26.1251 | 749.2275 | 173.3105 | 199.5584 | 240.4566 | 276.8787 | 318.8202 | 4.068%
9561 | 26-63 | -62.7892 | 26.1251 | 752.2518 | 173.9784 | 200.4134 | 241.6242 | 278.3431 | 320.6448 | 4.136%
9562 | 26-63 | -63.0605 | 26.1251 | 755.6689 | 174.6967 | 201.3435 | 242.9093 | 279.9665 | 322.6798 | 4.209%
9563 | 26-63.5 | -63.3318 | 26.1251 | 759.4735 | 175.4092 | 202.2632 | 244.1762 | 281.5637 | 324.6787 | 4.282%
9564 | 26-63.5 | -63.6031 | 26.1251 | 763.6598 | 176.0997 | 203.1484 | 245.3864 | 283.0825 | 326.5721 | 4.355%
9565 | 26-64 | -63.8745 | 26.1251 | 768.2216 | 176.8081 | 204.058 | 246.6324 | 284.6481 | 328.5257 | 4.429%
9566 | 26-64 | -64.1458 | 26.1251 | 773.1521 | 177.4788 | 204.9127 | 247.7937 | 286.1001 | 330.33 | 4.501%
9567 | 26-64.5 | -64.4171 | 26.1251 | 778.4445 | 178.1104 | 205.711 | 248.8689 | 287.437 | 331.9833 | 4.57%
9568 | 26-64.5 | -64.6884 | 26.1251 | 784.0912 | 178.743 | 206.5082 | 249.9395 | 288.766 | 333.6249 | 4.64%
9569 | 26-65 | -64.9598 | 26.1251 | 790.0848 | 179.3291 | 207.2322 | 250.8907 | 289.9301 | 335.0451 | 4.707%
9570 | 26-65 | -65.2311 | 26.1251 | 796.4174 | 179.8859 | 207.9086 | 251.7623 | 290.9836 | 336.3156 | 4.773%
9571 | 26-65.5 | -65.5024 | 26.1251 | 803.0808 | 180.4547 | 208.5987 | 252.6504 | 292.0558 | 337.608 | 4.841%
9572 | 26-66 | -65.7737 | 26.1251 | 810.0671 | 180.9604 | 209.1902 | 253.3779 | 292.9066 | 338.6028 | 4.905%
9573 | 26-66 | -66.045 | 26.1251 | 817.3678 | 181.4247 | 209.7187 | 254.005 | 293.6202 | 339.4148 | 4.967%
9574 | 26-66.5 | -66.3164 | 26.1251 | 824.9745 | 181.8884 | 210.2478 | 254.6348 | 294.3385 | 340.2339 | 5.029%
9575 | 26-66.5 | -66.5877 | 26.1251 | 832.879 | 182.2729 | 210.6731 | 255.119 | 294.8712 | 340.8187 | 5.083%
9576 | 26-67 | -66.859 | 26.1251 | 841.0727 | 182.617 | 211.0523 | 255.5488 | 295.3423 | 341.3335 | 5.132%
9577 | 26-67 | -67.1303 | 26.1251 | 849.5473 | 182.9603 | 211.4426 | 256.0108 | 295.8671 | 341.9293 | 5.18%
9578 | 26-67.5 | -67.4016 | 26.1251 | 858.2944 | 183.241 | 211.757 | 256.3758 | 296.2751 | 342.3849 | 5.219%
9579 | 26-67.5 | -67.673 | 26.1251 | 867.3057 | 183.5081 | 212.0643 | 256.7453 | 296.7 | 342.8734 | 5.256%
9580 | 26-68 | -67.9443 | 26.1251 | 876.5732 | 183.7942 | 212.4084 | 257.1838 | 297.2257 | 343.5029 | 5.293%
9581 | 26-68 | -68.2156 | 26.1251 | 886.0886 | 184.0208 | 212.6748 | 257.5134 | 297.6128 | 343.9572 | 5.324%
9582 | 26-68.5 | -68.4869 | 26.1251 | 895.8442 | 184.23 | 212.9244 | 257.828 | 297.9872 | 344.4022 | 5.352%
9583 | 26-69 | -68.7583 | 26.1251 | 905.832 | 184.4442 | 213.1893 | 258.1765 | 298.4141 | 344.9234 | 5.378%
9584 | 26-69 | -69.0296 | 26.1251 | 916.0446 | 184.5701 | 213.3388 | 258.3636 | 298.6356 | 345.1854 | 5.395%
9585 | 26-69.5 | -69.3009 | 26.1251 | 926.4743 | 184.6805 | 213.4805 | 258.5579 | 298.8798 | 345.4905 | 5.408%
9586 | 26-69.5 | -69.5722 | 26.1251 | 937.114 | 184.8033 | 213.6554 | 258.8226 | 299.2321 | 345.9511 | 5.42%
9587 | 26-70 | -69.8435 | 26.1251 | 947.9565 | 184.8331 | 213.713 | 258.9293 | 299.3878 | 346.1686 | 5.42%
9588 | 26-70 | -70.1149 | 26.1251 | 958.9949 | 184.8514 | 213.7591 | 259.0252 | 299.5337 | 346.3779 | 5.418%
9589 | 26-70.5 | -70.3862 | 26.1251 | 970.2226 | 184.8779 | 213.8187 | 259.1437 | 299.7112 | 346.63 | 5.417%
9590 | 26-70.5 | -70.6575 | 26.1251 | 981.6329 | 184.8379 | 213.7803 | 259.1098 | 299.6833 | 346.6106 | 5.41%
9591 | 26-71 | -70.9288 | 26.1251 | 993.2196 | 184.7976 | 213.7351 | 259.0576 | 299.6251 | 346.5461 | 5.404%
9592 | 26-71 | -71.2001 | 26.1251 | 1004.9765 | 184.7649 | 213.6932 | 259.0005 | 299.5536 | 346.4574 | 5.4%
9593 | 26-71.5 | -71.4715 | 26.1251 | 1016.8977 | 184.685 | 213.5766 | 258.8203 | 299.3116 | 346.1388 | 5.393%
9594 | 26-71.5 | -71.7428 | 26.1251 | 1028.9774 | 184.6346 | 213.4971 | 258.6903 | 299.132 | 345.8973 | 5.39%
9595 | 26-72 | -72.0141 | 26.1251 | 1041.2102 | 184.6132 | 213.4541 | 258.6092 | 299.0129 | 345.7305 | 5.39%
9596 | 26-72.5 | -72.2854 | 26.1251 | 1053.5905 | 184.5657 | 213.3694 | 258.459 | 298.7978 | 345.4339 | 5.388%
9597 | 26-72.5 | -72.5568 | 26.1251 | 1066.1133 | 184.5838 | 213.3715 | 258.4315 | 298.7399 | 345.3372 | 5.394%
9598 | 26-73 | -72.8281 | 26.1251 | 1078.7736 | 184.6446 | 213.4267 | 258.4745 | 298.769 | 345.3471 | 5.405%
9599 | 26-73 | -73.0994 | 26.1251 | 1091.5664 | 184.6471 | 213.3879 | 258.3609 | 298.5794 | 345.0607 | 5.413%
9600 | 26-73.5 | -73.3707 | 26.1251 | 1104.4873 | 184.696 | 213.4063 | 258.3223 | 298.4815 | 344.8861 | 5.426%
9601 | 26-73.5 | -73.642 | 26.1251 | 1117.5317 | 184.7669 | 213.4501 | 258.3144 | 298.4193 | 344.7527 | 5.443%
9602 | 26-74 | -73.9134 | 26.1251 | 1130.6952 | 184.8007 | 213.4363 | 258.213 | 298.2281 | 344.4464 | 5.457%
9603 | 26-74 | -74.1847 | 26.1251 | 1143.9738 | 184.8731 | 213.4776 | 258.1951 | 298.1482 | 344.2857 | 5.475%
9604 | 26-74.5 | -74.456 | 26.1251 | 1157.3635 | 184.9529 | 213.5286 | 258.1913 | 298.0866 | 344.1484 | 5.494%
9605 | 26-74.5 | -74.7273 | 26.1251 | 1170.8604 | 184.9835 | 213.507 | 258.0744 | 297.8724 | 343.8097 | 5.509%
9606 | 26-75 | -74.9986 | 26.1251 | 1184.4607 | 185.0191 | 213.4901 | 257.9614 | 297.6612 | 343.4729 | 5.524%
9607 | 26-75.5 | -75.27 | 26.1251 | 1198.161 | 185.0216 | 213.4288 | 257.7849 | 297.3683 | 343.0323 | 5.536%
9608 | 26-75.5 | -75.5413 | 26.1251 | 1211.9578 | 184.9303 | 213.2468 | 257.4429 | 296.8673 | 342.3315 | 5.537%
9609 | 26-76 | -75.8126 | 26.1251 | 1225.8478 | 184.7971 | 213.0197 | 257.0512 | 296.3132 | 341.5743 | 5.532%
9610 | 26-76 | -76.0839 | 26.1251 | 1239.8278 | 184.5994 | 212.7147 | 256.5599 | 295.6391 | 340.6728 | 5.517%
9611 | 26-76.5 | -76.3553 | 26.1251 | 1253.8948 | 184.3318 | 212.322 | 255.9515 | 294.8201 | 339.5927 | 5.494%
9612 | 26-76.5 | -76.6266 | 26.1251 | 1268.0458 | 184.0906 | 211.9838 | 255.447 | 294.1545 | 338.7284 | 5.47%
9613 | 26-77 | -76.8979 | 26.1251 | 1282.2781 | 183.8293 | 211.6327 | 254.9438 | 293.5049 | 337.8994 | 5.441%
9614 | 26-77 | -77.1692 | 26.1251 | 1296.5889 | 183.5158 | 211.2224 | 254.3706 | 292.776 | 336.9807 | 5.404%
9615 | 26-77.5 | -77.4405 | 26.1251 | 1310.9755 | 183.2078 | 210.8376 | 253.8589 | 292.1449 | 336.2056 | 5.365%
9616 | 26-77.5 | -77.7119 | 26.1251 | 1325.4356 | 182.8624 | 210.4141 | 253.3073 | 291.4737 | 335.3912 | 5.32%
9617 | 26-78 | -77.9832 | 26.1251 | 1339.9666 | 182.4673 | 209.9332 | 252.6867 | 290.7232 | 334.4856 | 5.268%
9618 | 26-78.5 | -78.2545 | 26.1251 | 1354.5662 | 182.0807 | 209.4847 | 252.1407 | 290.0897 | 333.7505 | 5.214%
9619 | 26-78.5 | -78.5258 | 26.1251 | 1369.2323 | 181.4637 | 208.7521 | 251.2229 | 289.0025 | 332.464 | 5.131%
9620 | 26-79 | -78.7971 | 26.1251 | 1383.9626 | 180.4358 | 207.5445 | 249.6657 | 287.1217 | 330.1984 | 5%
9621 | 26-79 | -79.0685 | 26.1251 | 1398.755 | 178.8527 | 205.9551 | 247.6082 | 284.6309 | 327.1925 | 4.805%
9622 | 26-79.5 | -79.3398 | 26.1251 | 1413.6076 | 177.1256 | 204.2859 | 245.4368 | 281.9939 | 324.0015 | 4.602%
9623 | 26-79.5 | -79.6111 | 26.1251 | 1428.5185 | 175.5498 | 202.7505 | 243.431 | 279.5513 | 321.0383 | 4.422%
9624 | 26-80 | -79.8824 | 26.1251 | 1443.4858 | 174.1486 | 201.3921 | 241.6642 | 277.4059 | 318.4421 | 4.266%
9625 | 26-80 | -80.1537 | 26.1251 | 1458.5077 | 172.8083 | 200.0785 | 239.942 | 275.3033 | 315.8855 | 4.121%
9626 | 26-80.5 | -80.4251 | 26.1251 | 1473.5825 | 171.509 | 198.8113 | 238.2711 | 273.2559 | 313.3876 | 3.985%
9627 | 26-80.5 | -80.6964 | 26.1251 | 1488.7086 | 170.2954 | 197.6673 | 236.7714 | 271.4251 | 311.1614 | 3.861%
9628 | 26-81 | -80.9677 | 26.1251 | 1503.8843 | 169.3056 | 196.6926 | 235.4852 | 269.8477 | 309.2352 | 3.762%
9629 | 26-81 | -81.239 | 26.1251 | 1519.1082 | 168.6529 | 195.9777 | 234.5485 | 268.7039 | 307.8436 | 3.696%
9630 | 26-81.5 | -81.5104 | 26.1251 | 1534.3788 | 168.3227 | 195.591 | 234.0721 | 268.1464 | 307.1912 | 3.661%
9631 | 26-82 | -81.7817 | 26.1251 | 1549.6945 | 168.0486 | 195.2721 | 233.6826 | 267.6934 | 306.6645 | 3.632%
9632 | 26-82 | -82.053 | 26.1251 | 1565.0541 | 168.0142 | 195.2656 | 233.7276 | 267.7908 | 306.829 | 3.626%
9633 | 26-82.5 | -82.3243 | 26.1251 | 1580.4563 | 168.4408 | 195.8184 | 234.5553 | 268.8837 | 308.2472 | 3.662%
9634 | 26-82.5 | -82.5956 | 26.1251 | 1595.8997 | 169.4639 | 196.8151 | 235.9821 | 270.7208 | 310.5838 | 3.755%
9635 | 26-83 | -82.867 | 26.1251 | 1611.3831 | 170.659 | 197.9368 | 237.5976 | 272.8083 | 313.2466 | 3.863%
9636 | 26-83 | -83.1383 | 26.1251 | 1626.9053 | 171.7562 | 199.0099 | 239.1881 | 274.8967 | 315.9454 | 3.961%
9637 | 26-83.5 | -83.4096 | 26.1251 | 1642.4653 | 172.6865 | 199.9108 | 240.5392 | 276.682 | 318.2639 | 4.044%
9638 | 26-83.5 | -83.6809 | 26.1251 | 1658.0618 | 173.5567 | 200.7599 | 241.8246 | 278.389 | 320.4892 | 4.121%
9639 | 26-84 | -83.9522 | 26.1251 | 1673.6938 | 174.4357 | 201.6256 | 243.1438 | 280.1471 | 322.7875 | 4.199%
9640 | 26-84 | -84.2236 | 26.1251 | 1689.3603 | 175.2832 | 202.4307 | 244.3672 | 281.7755 | 324.9144 | 4.275%
9641 | 26-84.5 | -84.4949 | 26.1251 | 1705.0603 | 175.9608 | 203.1288 | 245.4529 | 283.2382 | 326.843 | 4.333%
9642 | 26-85 | -84.7662 | 26.1251 | 1720.7928 | 176.399 | 203.6976 | 246.3753 | 284.5073 | 328.5432 | 4.367%
9643 | 26-85 | -85.0375 | 26.1251 | 1736.5569 | 176.5527 | 203.9832 | 246.8932 | 285.2557 | 329.5809 | 4.372%
9644 | 26-85.5 | -85.3089 | 26.1251 | 1752.3516 | 176.6846 | 204.2368 | 247.3617 | 285.938 | 330.5317 | 4.376%
9645 | 26-85.5 | -85.5802 | 26.1251 | 1768.1762 | 176.8453 | 204.5227 | 247.8681 | 286.663 | 331.5309 | 4.384%
9646 | 26-86 | -85.8515 | 26.1251 | 1784.0297 | 176.9444 | 204.7014 | 248.1872 | 287.1216 | 332.1646 | 4.388%
9647 | 26-86 | -86.1228 | 26.1251 | 1799.9114 | 177.0577 | 204.8786 | 248.4759 | 287.5201 | 332.7002 | 4.396%
9648 | 26-86.5 | -86.3941 | 26.1251 | 1815.8204 | 177.1919 | 205.0605 | 248.7393 | 287.8626 | 333.1403 | 4.409%
9649 | 26-86.5 | -86.6655 | 26.1251 | 1831.7561 | 177.2526 | 205.1296 | 248.8217 | 287.9571 | 333.249 | 4.416%
9650 | 26-87 | -86.9368 | 26.1251 | 1847.7176 | 177.3157 | 205.2128 | 248.9394 | 288.1084 | 333.442 | 4.422%
9651 | 26-87 | -87.2081 | 26.1251 | 1863.7043 | 177.376 | 205.3038 | 249.0846 | 288.3073 | 333.7084 | 4.427%
9652 | 26-87.5 | -87.4794 | 26.1251 | 1879.7154 | 177.3376 | 205.2694 | 249.0593 | 288.2928 | 333.7092 | 4.421%
9653 | 26-88 | -87.7507 | 26.1251 | 1895.7503 | 177.2471 | 205.1857 | 248.9918 | 288.2448 | 333.6889 | 4.408%
9654 | 26-88 | -88.0221 | 26.1251 | 1911.8084 | 177.0892 | 205.0309 | 248.8492 | 288.1197 | 333.5906 | 4.386%
9655 | 26-88.5 | -88.2934 | 26.1251 | 1927.889 | 176.7942 | 204.7049 | 248.4788 | 287.7133 | 333.1465 | 4.35%
9656 | 26-88.5 | -88.5647 | 26.1251 | 1943.9915 | 176.4622 | 204.3557 | 248.1118 | 287.3388 | 332.7715 | 4.308%
9657 | 26-89 | -88.836 | 26.1251 | 1960.1153 | 176.0826 | 203.9666 | 247.7215 | 286.9591 | 332.4163 | 4.258%
9658 | 26-89 | -89.1074 | 26.1251 | 1976.2598 | 175.6045 | 203.4587 | 247.1789 | 286.3963 | 331.8408 | 4.199%
9659 | 26-89.5 | -89.3787 | 26.1251 | 1992.4246 | 175.1135 | 202.9591 | 246.6836 | 285.9208 | 331.4044 | 4.137%
9660 | 26-89.5 | -89.65 | 26.1251 | 2008.609 | 174.5917 | 202.4388 | 246.1875 | 285.4655 | 331.0157 | 4.071%
9661 | 26-90 | -89.9213 | 26.1251 | 2024.8125 | 174.0017 | 201.8356 | 245.5835 | 284.8788 | 330.467 | 4%
9662 | 26-90 | -90.1926 | 26.1251 | 2041.0347 | 173.4346 | 201.2575 | 245.0079 | 284.3227 | 329.9511 | 3.932%
9663 | 26-90.5 | -90.464 | 26.1251 | 2057.2749 | 172.8592 | 200.6617 | 244.394 | 283.7075 | 329.3494 | 3.866%
9664 | 26-90.5 | -90.7353 | 26.1251 | 2073.5329 | 172.2269 | 199.9836 | 243.6449 | 282.9046 | 328.4941 | 3.797%
9665 | 26-50 | -50.0371 | 26.3964 | 1020.2185 | 111.0204 | 145.2884 | 184.3848 | 208.9136 | 236.707 | 0.7357%
9666 | 26-50.5 | -50.3084 | 26.3964 | 1008.6156 | 112.6866 | 147.6489 | 185.8632 | 210.6605 | 238.7678 | 0.7737%
9667 | 26-50.5 | -50.5797 | 26.3964 | 997.1833 | 114.3562 | 150.002 | 187.3214 | 212.3719 | 240.774 | 0.8137%
9668 | 26-51 | -50.851 | 26.3964 | 985.9274 | 116.0353 | 152.34 | 188.7754 | 214.0878 | 242.7959 | 0.8562%
9669 | 26-51 | -51.1224 | 26.3964 | 974.8542 | 117.7532 | 154.6505 | 190.2705 | 215.8818 | 244.9421 | 0.902%
9670 | 26-51.5 | -51.3937 | 26.3964 | 963.97 | 119.4085 | 156.8142 | 191.6852 | 217.5805 | 246.9759 | 0.9482%
9671 | 26-51.5 | -51.665 | 26.3964 | 953.2813 | 121.0138 | 158.8458 | 193.0457 | 219.2271 | 248.9614 | 0.995%
9672 | 26-52 | -51.9363 | 26.3964 | 942.7947 | 122.5918 | 160.7581 | 194.3911 | 220.8783 | 250.9774 | 1.043%
9673 | 26-52 | -52.2077 | 26.3964 | 932.5172 | 124.0727 | 162.481 | 195.6141 | 222.3651 | 252.7778 | 1.09%
9674 | 26-52.5 | -52.479 | 26.3964 | 922.4557 | 125.4929 | 164.0563 | 196.7732 | 223.7794 | 254.496 | 1.136%
9675 | 26-53 | -52.7503 | 26.3964 | 912.6174 | 126.8775 | 165.4988 | 197.9125 | 225.189 | 256.2292 | 1.183%
9676 | 26-53 | -53.0216 | 26.3964 | 903.0096 | 128.1524 | 166.7343 | 198.9355 | 226.4497 | 257.7741 | 1.227%
9677 | 26-53.5 | -53.2929 | 26.3964 | 893.6398 | 129.3828 | 167.8423 | 199.9298 | 227.6866 | 259.302 | 1.27%
9678 | 26-53.5 | -53.5643 | 26.3964 | 884.5156 | 130.6008 | 168.8438 | 200.9369 | 228.9556 | 260.8865 | 1.314%
9679 | 26-54 | -53.8356 | 26.3964 | 875.6448 | 131.7333 | 169.6636 | 201.8663 | 230.1246 | 262.3438 | 1.355%
9680 | 26-54 | -54.1069 | 26.3964 | 867.035 | 132.8916 | 170.4494 | 202.85 | 231.3711 | 263.9076 | 1.398%
9681 | 26-54.5 | -54.3782 | 26.3964 | 858.6942 | 134.1139 | 171.2412 | 203.9292 | 232.7471 | 265.6429 | 1.444%
9682 | 26-54.5 | -54.6495 | 26.3964 | 850.6303 | 135.2956 | 171.9883 | 204.9569 | 234.0397 | 267.2552 | 1.49%
9683 | 26-55 | -54.9209 | 26.3964 | 842.8513 | 136.5574 | 172.8044 | 206.0787 | 235.45 | 269.0138 | 1.541%
9684 | 26-55 | -55.1922 | 26.3964 | 835.3651 | 137.9242 | 173.7074 | 207.3198 | 237.0104 | 270.9599 | 1.599%
9685 | 26-55.5 | -55.4635 | 26.3964 | 828.1798 | 139.2834 | 174.6069 | 208.5137 | 238.4799 | 272.7599 | 1.658%
9686 | 26-55.5 | -55.7348 | 26.3964 | 821.3032 | 140.7226 | 175.5645 | 209.79 | 240.0546 | 274.6926 | 1.722%
9687 | 26-56 | -56.0061 | 26.3964 | 814.7432 | 142.2494 | 176.5848 | 211.155 | 241.7428 | 276.7691 | 1.794%
9688 | 26-56.5 | -56.2775 | 26.3964 | 808.5076 | 143.7647 | 177.5894 | 212.4699 | 243.3466 | 278.7179 | 1.867%
9689 | 26-56.5 | -56.5488 | 26.3964 | 802.6038 | 145.3567 | 178.6387 | 213.8468 | 245.0287 | 280.7648 | 1.947%
9690 | 26-57 | -56.8201 | 26.3964 | 797.0392 | 147.0208 | 179.7276 | 215.2767 | 246.7764 | 282.8923 | 2.035%
9691 | 26-57 | -57.0914 | 26.3964 | 791.8212 | 148.6806 | 180.7991 | 216.6635 | 248.4556 | 284.9197 | 2.125%
9692 | 26-57.5 | -57.3628 | 26.3964 | 786.9565 | 150.4271 | 181.914 | 218.1094 | 250.2085 | 287.0385 | 2.224%
9693 | 26-57.5 | -57.6341 | 26.3964 | 782.4517 | 152.2341 | 183.052 | 219.579 | 251.9854 | 289.1809 | 2.331%
9694 | 26-58 | -57.9054 | 26.3964 | 778.3132 | 153.9886 | 184.1373 | 220.9545 | 253.6274 | 291.1377 | 2.44%
9695 | 26-58 | -58.1767 | 26.3964 | 774.5467 | 155.7748 | 185.2603 | 222.3884 | 255.3479 | 293.1978 | 2.556%
9696 | 26-58.5 | -58.448 | 26.3964 | 771.1579 | 157.5266 | 186.3825 | 223.8134 | 257.0515 | 295.2307 | 2.675%
9697 | 26-58.5 | -58.7194 | 26.3964 | 768.1516 | 159.1404 | 187.4105 | 225.08 | 258.5334 | 296.9636 | 2.791%
9698 | 26-59 | -58.9907 | 26.3964 | 765.5324 | 160.7193 | 188.4467 | 226.3677 | 260.0496 | 298.7472 | 2.909%
9699 | 26-59.5 | -59.262 | 26.3964 | 763.3043 | 162.2141 | 189.4524 | 227.6122 | 261.5103 | 300.4604 | 3.025%
9700 | 26-59.5 | -59.5333 | 26.3964 | 761.4707 | 163.564 | 190.3605 | 228.7069 | 262.7707 | 301.9111 | 3.136%
9701 | 26-60 | -59.8046 | 26.3964 | 760.0345 | 164.8596 | 191.2637 | 229.8102 | 264.0536 | 303.4023 | 3.246%
9702 | 26-60 | -60.076 | 26.3964 | 758.998 | 166.0598 | 192.1353 | 230.879 | 265.2999 | 304.8547 | 3.352%
9703 | 26-60.5 | -60.3473 | 26.3964 | 758.3627 | 167.1286 | 192.94 | 231.8547 | 266.4284 | 306.1594 | 3.45%
9704 | 26-60.5 | -60.6186 | 26.3964 | 758.1297 | 168.1295 | 193.7462 | 232.8491 | 267.5931 | 307.5228 | 3.544%
9705 | 26-61 | -60.8899 | 26.3964 | 758.2994 | 169.0137 | 194.5218 | 233.8133 | 268.7286 | 308.859 | 3.63%
9706 | 26-61 | -61.1613 | 26.3964 | 758.8715 | 169.7607 | 195.2495 | 234.7191 | 269.7967 | 310.1175 | 3.705%
9707 | 26-61.5 | -61.4326 | 26.3964 | 759.8451 | 170.4697 | 196.0158 | 235.6991 | 270.9741 | 311.5294 | 3.778%
9708 | 26-61.5 | -61.7039 | 26.3964 | 761.2186 | 171.1196 | 196.7732 | 236.6785 | 272.1599 | 312.9617 | 3.845%
9709 | 26-62 | -61.9752 | 26.3964 | 762.9899 | 171.7229 | 197.5115 | 237.6408 | 273.3315 | 314.3839 | 3.908%
9710 | 26-62 | -62.2465 | 26.3964 | 765.1563 | 172.3773 | 198.3394 | 238.7573 | 274.7209 | 316.1034 | 3.975%
9711 | 26-62.5 | -62.5179 | 26.3964 | 767.7142 | 173.041 | 199.1865 | 239.9102 | 276.1639 | 317.8984 | 4.043%
9712 | 26-63 | -62.7892 | 26.3964 | 770.66 | 173.7046 | 200.0347 | 241.0667 | 277.613 | 319.7025 | 4.111%
9713 | 26-63 | -63.0605 | 26.3964 | 773.989 | 174.4277 | 200.972 | 242.3633 | 279.2519 | 321.7581 | 4.184%
9714 | 26-63.5 | -63.3318 | 26.3964 | 777.6965 | 175.151 | 201.907 | 243.6528 | 280.8789 | 323.7956 | 4.258%
9715 | 26-63.5 | -63.6031 | 26.3964 | 781.7769 | 175.8573 | 202.8126 | 244.8915 | 282.4339 | 325.7344 | 4.332%
9716 | 26-64 | -63.8745 | 26.3964 | 786.2245 | 176.5871 | 203.7499 | 246.1756 | 284.0474 | 327.7479 | 4.409%
9717 | 26-64 | -64.1458 | 26.3964 | 791.0331 | 177.2831 | 204.6357 | 247.3775 | 285.5488 | 329.6119 | 4.483%
9718 | 26-64.5 | -64.4171 | 26.3964 | 796.196 | 177.9413 | 205.4651 | 248.4907 | 286.9299 | 331.3167 | 4.556%
9719 | 26-64.5 | -64.6884 | 26.3964 | 801.7066 | 178.5998 | 206.2916 | 249.5958 | 288.2978 | 333.0018 | 4.629%
9720 | 26-65 | -64.9598 | 26.3964 | 807.5575 | 179.2125 | 207.0459 | 250.5828 | 289.5025 | 334.468 | 4.699%
9721 | 26-65 | -65.2311 | 26.3964 | 813.7416 | 179.7956 | 207.7526 | 251.491 | 290.5979 | 335.7868 | 4.769%
9722 | 26-65.5 | -65.5024 | 26.3964 | 820.2511 | 180.3892 | 208.4712 | 252.4132 | 291.7094 | 337.1241 | 4.84%
9723 | 26-66 | -65.7737 | 26.3964 | 827.0784 | 180.9197 | 209.0915 | 253.1758 | 292.6008 | 338.1661 | 4.907%
9724 | 26-66 | -66.045 | 26.3964 | 834.2158 | 181.4091 | 209.6497 | 253.8396 | 293.3576 | 339.0287 | 4.973%
9725 | 26-66.5 | -66.3164 | 26.3964 | 841.6551 | 181.8984 | 210.2089 | 254.5068 | 294.12 | 339.8998 | 5.038%
9726 | 26-66.5 | -66.5877 | 26.3964 | 849.3887 | 182.305 | 210.6583 | 255.0182 | 294.6824 | 340.5167 | 5.095%
9727 | 26-67 | -66.859 | 26.3964 | 857.4083 | 182.6697 | 211.0601 | 255.4733 | 295.1808 | 341.061 | 5.148%
9728 | 26-67 | -67.1303 | 26.3964 | 865.7061 | 183.0348 | 211.4758 | 255.9666 | 295.7422 | 341.6996 | 5.198%
9729 | 26-67.5 | -67.4016 | 26.3964 | 874.2742 | 183.3374 | 211.8167 | 256.3652 | 296.1904 | 342.2033 | 5.241%
9730 | 26-67.5 | -67.673 | 26.3964 | 883.1045 | 183.6291 | 212.1548 | 256.776 | 296.6665 | 342.7551 | 5.281%
9731 | 26-68 | -67.9443 | 26.3964 | 892.1894 | 183.9435 | 212.5362 | 257.2667 | 297.2589 | 343.4689 | 5.321%
9732 | 26-68 | -68.2156 | 26.3964 | 901.5211 | 184.2014 | 212.8447 | 257.6569 | 297.7242 | 344.0233 | 5.356%
9733 | 26-68.5 | -68.4869 | 26.3964 | 911.0919 | 184.4438 | 213.1389 | 258.0356 | 298.1814 | 344.5741 | 5.387%
9734 | 26-69 | -68.7583 | 26.3964 | 920.8945 | 184.6926 | 213.4496 | 258.4489 | 298.6916 | 345.201 | 5.418%
9735 | 26-69 | -69.0296 | 26.3964 | 930.9214 | 184.8512 | 213.6414 | 258.6945 | 298.987 | 345.5558 | 5.439%
9736 | 26-69.5 | -69.3009 | 26.3964 | 941.1655 | 184.9908 | 213.8197 | 258.9376 | 299.2917 | 345.9352 | 5.455%
9737 | 26-69.5 | -69.5722 | 26.3964 | 951.6196 | 185.1391 | 214.0251 | 259.2407 | 299.6896 | 346.4502 | 5.47%
9738 | 26-70 | -69.8435 | 26.3964 | 962.277 | 185.1872 | 214.1017 | 259.3672 | 299.8653 | 346.6874 | 5.473%
9739 | 26-70 | -70.1149 | 26.3964 | 973.131 | 185.2205 | 214.162 | 259.475 | 300.0204 | 346.902 | 5.474%
9740 | 26-70.5 | -70.3862 | 26.3964 | 984.1749 | 185.2595 | 214.2319 | 259.5996 | 300.1993 | 347.1492 | 5.475%
9741 | 26-70.5 | -70.6575 | 26.3964 | 995.4025 | 185.2264 | 214.1954 | 259.5581 | 300.1539 | 347.0998 | 5.47%
9742 | 26-71 | -70.9288 | 26.3964 | 1006.8075 | 185.1879 | 214.145 | 259.4878 | 300.0645 | 346.9873 | 5.466%
9743 | 26-71 | -71.2001 | 26.3964 | 1018.3839 | 185.1524 | 214.0914 | 259.4031 | 299.9496 | 346.8349 | 5.463%
9744 | 26-71.5 | -71.4715 | 26.3964 | 1030.1261 | 185.0659 | 213.9586 | 259.19 | 299.6577 | 346.445 | 5.457%
9745 | 26-71.5 | -71.7428 | 26.3964 | 1042.0282 | 185.0067 | 213.8607 | 259.0245 | 299.4256 | 346.1298 | 5.453%
9746 | 26-72 | -72.0141 | 26.3964 | 1054.0849 | 184.9736 | 213.796 | 258.904 | 299.2495 | 345.8839 | 5.453%
9747 | 26-72.5 | -72.2854 | 26.3964 | 1066.2909 | 184.9047 | 213.6773 | 258.6978 | 298.9568 | 345.4828 | 5.451%
9748 | 26-72.5 | -72.5568 | 26.3964 | 1078.6411 | 184.8949 | 213.6374 | 258.6039 | 298.8086 | 345.266 | 5.454%
9749 | 26-73 | -72.8281 | 26.3964 | 1091.1305 | 184.9247 | 213.647 | 258.5761 | 298.7423 | 345.1499 | 5.463%
9750 | 26-73 | -73.0994 | 26.3964 | 1103.7544 | 184.9048 | 213.5746 | 258.4094 | 298.4806 | 344.7678 | 5.469%
9751 | 26-73.5 | -73.3707 | 26.3964 | 1116.5082 | 184.9435 | 213.5768 | 258.3441 | 298.3458 | 344.5437 | 5.482%
9752 | 26-73.5 | -73.642 | 26.3964 | 1129.3875 | 185.0127 | 213.6172 | 258.3297 | 298.2739 | 344.3967 | 5.499%
9753 | 26-74 | -73.9134 | 26.3964 | 1142.3879 | 185.0442 | 213.6002 | 258.2239 | 298.0772 | 344.0835 | 5.513%
9754 | 26-74 | -74.1847 | 26.3964 | 1155.5053 | 185.1164 | 213.6432 | 258.2113 | 298.0062 | 343.9364 | 5.531%
9755 | 26-74.5 | -74.456 | 26.3964 | 1168.7359 | 185.1973 | 213.6995 | 258.2203 | 297.965 | 343.8292 | 5.549%
9756 | 26-74.5 | -74.7273 | 26.3964 | 1182.0756 | 185.2285 | 213.6835 | 258.118 | 297.7746 | 343.526 | 5.564%
9757 | 26-75 | -74.9986 | 26.3964 | 1195.5209 | 185.2632 | 213.6702 | 258.0166 | 297.5833 | 343.2197 | 5.579%
9758 | 26-75.5 | -75.27 | 26.3964 | 1209.0681 | 185.2676 | 213.616 | 257.8566 | 297.3164 | 342.817 | 5.59%
9759 | 26-75.5 | -75.5413 | 26.3964 | 1222.7139 | 185.19 | 213.4568 | 257.5534 | 296.87 | 342.1907 | 5.592%
9760 | 26-76 | -75.8126 | 26.3964 | 1236.455 | 185.089 | 213.2766 | 257.2342 | 296.4132 | 341.5618 | 5.589%
9761 | 26-76 | -76.0839 | 26.3964 | 1250.2881 | 184.9298 | 213.0274 | 256.8286 | 295.8541 | 340.8113 | 5.579%
9762 | 26-76.5 | -76.3553 | 26.3964 | 1264.2102 | 184.6867 | 212.6741 | 256.2852 | 295.1254 | 339.8532 | 5.557%
9763 | 26-76.5 | -76.6266 | 26.3964 | 1278.2183 | 184.444 | 212.3426 | 255.8025 | 294.4967 | 339.0452 | 5.531%
9764 | 26-77 | -76.8979 | 26.3964 | 1292.3097 | 184.1613 | 211.973 | 255.2868 | 293.8415 | 338.2196 | 5.497%
9765 | 26-77 | -77.1692 | 26.3964 | 1306.4815 | 183.8166 | 211.5315 | 254.6836 | 293.0847 | 337.2764 | 5.455%
9766 | 26-77.5 | -77.4405 | 26.3964 | 1320.7312 | 183.4768 | 211.1152 | 254.142 | 292.4261 | 336.4779 | 5.41%
9767 | 26-77.5 | -77.7119 | 26.3964 | 1335.0562 | 183.0968 | 210.6559 | 253.554 | 291.7189 | 335.6288 | 5.359%
9768 | 26-78 | -77.9832 | 26.3964 | 1349.454 | 182.6629 | 210.133 | 252.8867 | 290.9182 | 334.6695 | 5.301%
9769 | 26-78.5 | -78.2545 | 26.3964 | 1363.9224 | 182.2354 | 209.6392 | 252.2893 | 290.2281 | 333.8724 | 5.24%
9770 | 26-78.5 | -78.5258 | 26.3964 | 1378.459 | 181.5565 | 208.8344 | 251.2831 | 289.038 | 332.4658 | 5.148%
9771 | 26-79 | -78.7971 | 26.3964 | 1393.0617 | 180.4247 | 207.5038 | 249.5676 | 286.9662 | 329.9704 | 5.003%
9772 | 26-79 | -79.0685 | 26.3964 | 1407.7284 | 178.6556 | 205.7303 | 247.2674 | 284.1779 | 326.6016 | 4.787%
9773 | 26-79.5 | -79.3398 | 26.3964 | 1422.457 | 176.6845 | 203.8321 | 244.7923 | 281.1675 | 322.9535 | 4.555%
9774 | 26-79.5 | -79.6111 | 26.3964 | 1437.2456 | 174.8328 | 202.0472 | 242.4552 | 278.3171 | 319.491 | 4.347%
9775 | 26-80 | -79.8824 | 26.3964 | 1452.0924 | 173.1432 | 200.4396 | 240.3576 | 275.7646 | 316.3964 | 4.162%
9776 | 26-80 | -80.1537 | 26.3964 | 1466.9954 | 171.5184 | 198.8897 | 238.3222 | 273.2774 | 313.3698 | 3.991%
9777 | 26-80.5 | -80.4251 | 26.3964 | 1481.9531 | 169.9405 | 197.3966 | 236.3536 | 270.8654 | 310.4276 | 3.831%
9778 | 26-80.5 | -80.6964 | 26.3964 | 1496.9636 | 168.448 | 196.0277 | 234.5593 | 268.6752 | 307.7649 | 3.683%
9779 | 26-81 | -80.9677 | 26.3964 | 1512.0254 | 167.2326 | 194.8672 | 233.0308 | 266.8031 | 305.4816 | 3.566%
9780 | 26-81 | -81.239 | 26.3964 | 1527.1369 | 166.4369 | 194.025 | 231.932 | 265.4652 | 303.8578 | 3.489%
9781 | 26-81.5 | -81.5104 | 26.3964 | 1542.2967 | 166.0484 | 193.5736 | 231.3815 | 264.8257 | 303.1149 | 3.449%
9782 | 26-82 | -81.7817 | 26.3964 | 1557.5031 | 165.729 | 193.2074 | 230.9428 | 264.3229 | 302.5385 | 3.416%
9783 | 26-82 | -82.053 | 26.3964 | 1572.7549 | 165.6705 | 193.1818 | 230.9783 | 264.4213 | 302.718 | 3.407%
9784 | 26-82.5 | -82.3243 | 26.3964 | 1588.0507 | 166.1101 | 193.7609 | 231.8607 | 265.5969 | 304.2542 | 3.443%
9785 | 26-82.5 | -82.5956 | 26.3964 | 1603.3892 | 167.2169 | 194.83 | 233.4052 | 267.5959 | 306.8075 | 3.539%
9786 | 26-83 | -82.867 | 26.3964 | 1618.7692 | 168.5425 | 196.0545 | 235.1795 | 269.8963 | 309.7497 | 3.654%
9787 | 26-83 | -83.1383 | 26.3964 | 1634.1893 | 169.8026 | 197.2515 | 236.9572 | 272.233 | 312.7715 | 3.762%
9788 | 26-83.5 | -83.4096 | 26.3964 | 1649.6485 | 170.9279 | 198.2982 | 238.5214 | 274.2958 | 315.4459 | 3.86%
9789 | 26-83.5 | -83.6809 | 26.3964 | 1665.1456 | 172.0086 | 199.3023 | 240.0278 | 276.2865 | 318.0311 | 3.954%
9790 | 26-84 | -83.9522 | 26.3964 | 1680.6795 | 173.1049 | 200.3263 | 241.5681 | 278.3253 | 320.6821 | 4.05%
9791 | 26-84 | -84.2236 | 26.3964 | 1696.2491 | 174.1747 | 201.2922 | 243.0109 | 280.2279 | 323.1492 | 4.146%
9792 | 26-84.5 | -84.4949 | 26.3964 | 1711.8535 | 175.0261 | 202.116 | 244.2656 | 281.9002 | 325.3362 | 4.221%
9793 | 26-85 | -84.7662 | 26.3964 | 1727.4916 | 175.5631 | 202.7606 | 245.2871 | 283.2902 | 327.1832 | 4.265%
9794 | 26-85 | -85.0375 | 26.3964 | 1743.1624 | 175.7405 | 203.0706 | 245.83 | 284.0635 | 328.2451 | 4.274%
9795 | 26-85.5 | -85.3089 | 26.3964 | 1758.8652 | 175.8929 | 203.3431 | 246.3137 | 284.7564 | 329.2003 | 4.281%
9796 | 26-85.5 | -85.5802 | 26.3964 | 1774.5989 | 176.082 | 203.6564 | 246.8446 | 285.5023 | 330.215 | 4.293%
9797 | 26-86 | -85.8515 | 26.3964 | 1790.3627 | 176.2181 | 203.8702 | 247.1937 | 285.9845 | 330.8634 | 4.302%
9798 | 26-86 | -86.1228 | 26.3964 | 1806.1557 | 176.3766 | 204.0897 | 247.5177 | 286.41 | 331.4141 | 4.317%
9799 | 26-86.5 | -86.3941 | 26.3964 | 1821.9772 | 176.5644 | 204.3214 | 247.8219 | 286.7827 | 331.8693 | 4.337%
9800 | 26-86.5 | -86.6655 | 26.3964 | 1837.8264 | 176.6854 | 204.4456 | 247.9478 | 286.9069 | 331.9887 | 4.353%
9801 | 26-87 | -86.9368 | 26.3964 | 1853.7025 | 176.8138 | 204.5889 | 248.1136 | 287.0922 | 332.196 | 4.368%
9802 | 26-87 | -87.2081 | 26.3964 | 1869.6047 | 176.9441 | 204.7448 | 248.3115 | 287.3296 | 332.4808 | 4.383%
9803 | 26-87.5 | -87.4794 | 26.3964 | 1885.5324 | 176.977 | 204.778 | 248.3445 | 287.3618 | 332.5116 | 4.387%
9804 | 26-88 | -87.7507 | 26.3964 | 1901.4849 | 176.9596 | 204.7657 | 248.3425 | 287.3711 | 332.5361 | 4.384%
9805 | 26-88 | -88.0221 | 26.3964 | 1917.4615 | 176.8751 | 204.6837 | 248.2686 | 287.3083 | 332.4902 | 4.372%
9806 | 26-88.5 | -88.2934 | 26.3964 | 1933.4615 | 176.6478 | 204.4242 | 247.9599 | 286.9566 | 332.09 | 4.345%
9807 | 26-88.5 | -88.5647 | 26.3964 | 1949.4843 | 176.3779 | 204.1361 | 247.6499 | 286.6329 | 331.7563 | 4.311%
9808 | 26-89 | -88.836 | 26.3964 | 1965.5294 | 176.0538 | 203.8018 | 247.3106 | 286.2988 | 331.438 | 4.269%
9809 | 26-89 | -89.1074 | 26.3964 | 1981.5961 | 175.6234 | 203.3416 | 246.8138 | 285.7784 | 330.8996 | 4.216%
9810 | 26-89.5 | -89.3787 | 26.3964 | 1997.6838 | 175.1717 | 202.8842 | 246.3644 | 285.3513 | 330.5136 | 4.158%
9811 | 26-89.5 | -89.65 | 26.3964 | 2013.7921 | 174.6808 | 202.4008 | 245.9149 | 284.9514 | 330.1909 | 4.095%
9812 | 26-90 | -89.9213 | 26.3964 | 2029.9203 | 174.1133 | 201.8297 | 245.3596 | 284.4295 | 329.7269 | 4.025%
9813 | 26-90 | -90.1926 | 26.3964 | 2046.0679 | 173.5626 | 201.281 | 244.8365 | 283.9491 | 329.3156 | 3.957%
9814 | 26-90.5 | -90.464 | 26.3964 | 2062.2345 | 172.9988 | 200.7105 | 244.2759 | 283.4153 | 328.8311 | 3.89%
9815 | 26-90.5 | -90.7353 | 26.3964 | 2078.4195 | 172.3761 | 200.0512 | 243.5743 | 282.6891 | 328.0897 | 3.82%
9816 | 27-50 | -50.0371 | 26.6677 | 1033.7608 | 110.9067 | 144.9611 | 184.0705 | 208.4427 | 236.0433 | 0.7306%
9817 | 27-50.5 | -50.3084 | 26.6677 | 1022.3354 | 112.5343 | 147.2721 | 185.5194 | 210.1567 | 238.0672 | 0.7676%
9818 | 27-50.5 | -50.5797 | 26.6677 | 1011.0816 | 114.1712 | 149.5881 | 186.9537 | 211.8407 | 240.042 | 0.8067%
9819 | 27-51 | -50.851 | 26.6677 | 1000.0053 | 115.8246 | 151.9031 | 188.39 | 213.536 | 242.0398 | 0.8483%
9820 | 27-51 | -51.1224 | 26.6677 | 989.1124 | 117.5248 | 154.2079 | 189.8751 | 215.3178 | 244.1711 | 0.8934%
9821 | 27-51.5 | -51.3937 | 26.6677 | 978.409 | 119.1696 | 156.376 | 191.2825 | 217.0041 | 246.186 | 0.939%
9822 | 27-51.5 | -51.665 | 26.6677 | 967.9016 | 120.7723 | 158.4219 | 192.638 | 218.6369 | 248.1463 | 0.9855%
9823 | 27-52 | -51.9363 | 26.6677 | 957.5966 | 122.3562 | 160.3599 | 193.9814 | 220.274 | 250.1324 | 1.033%
9824 | 27-52 | -52.2077 | 26.6677 | 947.5006 | 123.8495 | 162.1186 | 195.2058 | 221.7487 | 251.9035 | 1.08%
9825 | 27-52.5 | -52.479 | 26.6677 | 937.6204 | 125.284 | 163.732 | 196.3643 | 223.1476 | 253.5871 | 1.127%
9826 | 27-53 | -52.7503 | 26.6677 | 927.9629 | 126.6818 | 165.2098 | 197.4981 | 224.5354 | 255.2775 | 1.174%
9827 | 27-53 | -53.0216 | 26.6677 | 918.5352 | 127.97 | 166.4789 | 198.513 | 225.771 | 256.7756 | 1.218%
9828 | 27-53.5 | -53.2929 | 26.6677 | 909.3445 | 129.212 | 167.6163 | 199.4974 | 226.9827 | 258.2588 | 1.262%
9829 | 27-53.5 | -53.5643 | 26.6677 | 900.3981 | 130.4381 | 168.6411 | 200.492 | 228.226 | 259.8005 | 1.306%
9830 | 27-54 | -53.8356 | 26.6677 | 891.7033 | 131.5792 | 169.4802 | 201.4079 | 229.368 | 261.2137 | 1.347%
9831 | 27-54 | -54.1069 | 26.6677 | 883.2675 | 132.7458 | 170.2791 | 202.3767 | 230.5864 | 262.7325 | 1.39%
9832 | 27-54.5 | -54.3782 | 26.6677 | 875.0984 | 133.9752 | 171.0765 | 203.4396 | 231.933 | 264.4218 | 1.437%
9833 | 27-54.5 | -54.6495 | 26.6677 | 867.2034 | 135.16 | 171.8177 | 204.4466 | 233.1912 | 265.9823 | 1.483%
9834 | 27-55 | -54.9209 | 26.6677 | 859.5901 | 136.4215 | 172.6247 | 205.5491 | 234.5719 | 267.6982 | 1.534%
9835 | 27-55 | -55.1922 | 26.6677 | 852.2662 | 137.7852 | 173.5173 | 206.7738 | 236.1098 | 269.614 | 1.591%
9836 | 27-55.5 | -55.4635 | 26.6677 | 845.2391 | 139.1355 | 174.4035 | 207.9516 | 237.5603 | 271.3914 | 1.65%
9837 | 27-55.5 | -55.7348 | 26.6677 | 838.5164 | 140.5625 | 175.3473 | 209.2124 | 239.1181 | 273.3053 | 1.714%
9838 | 27-56 | -56.0061 | 26.6677 | 832.1054 | 142.0751 | 176.3541 | 210.5634 | 240.7916 | 275.3662 | 1.785%
9839 | 27-56.5 | -56.2775 | 26.6677 | 826.0134 | 143.5745 | 177.3461 | 211.8652 | 242.382 | 277.3012 | 1.858%
9840 | 27-56.5 | -56.5488 | 26.6677 | 820.2475 | 145.1486 | 178.3827 | 213.2294 | 244.0516 | 279.3358 | 1.937%
9841 | 27-57 | -56.8201 | 26.6677 | 814.8147 | 146.7941 | 179.4603 | 214.6489 | 245.79 | 281.4556 | 2.024%
9842 | 27-57 | -57.0914 | 26.6677 | 809.7218 | 148.4361 | 180.5223 | 216.0283 | 247.464 | 283.4806 | 2.113%
9843 | 27-57.5 | -57.3628 | 26.6677 | 804.975 | 150.1615 | 181.6267 | 217.4684 | 249.216 | 285.6049 | 2.211%
9844 | 27-57.5 | -57.6341 | 26.6677 | 800.5808 | 151.9453 | 182.754 | 218.9346 | 250.9972 | 287.7614 | 2.317%
9845 | 27-58 | -57.9054 | 26.6677 | 796.5448 | 153.6765 | 183.8289 | 220.309 | 252.6477 | 289.7393 | 2.424%
9846 | 27-58 | -58.1767 | 26.6677 | 792.8725 | 155.4477 | 184.9439 | 221.7467 | 254.384 | 291.8306 | 2.538%
9847 | 27-58.5 | -58.448 | 26.6677 | 789.5692 | 157.1944 | 186.0613 | 223.1814 | 256.1119 | 293.9066 | 2.657%
9848 | 27-58.5 | -58.7194 | 26.6677 | 786.6393 | 158.8088 | 187.09 | 224.4667 | 257.6311 | 295.7003 | 2.772%
9849 | 27-59 | -58.9907 | 26.6677 | 784.0871 | 160.3953 | 188.1345 | 225.7854 | 259.201 | 297.5663 | 2.889%
9850 | 27-59.5 | -59.262 | 26.6677 | 781.9164 | 161.9026 | 189.1531 | 227.0672 | 260.7235 | 299.3724 | 3.006%
9851 | 27-59.5 | -59.5333 | 26.6677 | 780.1302 | 163.2655 | 190.0717 | 228.1944 | 262.0386 | 300.9058 | 3.117%
9852 | 27-60 | -59.8046 | 26.6677 | 778.7313 | 164.5753 | 190.9837 | 229.3268 | 263.3711 | 302.4723 | 3.227%
9853 | 27-60 | -60.076 | 26.6677 | 777.7218 | 165.7893 | 191.8608 | 230.418 | 264.6567 | 303.9857 | 3.333%
9854 | 27-60.5 | -60.3473 | 26.6677 | 777.1031 | 166.8698 | 192.6654 | 231.4052 | 265.8083 | 305.3282 | 3.43%
9855 | 27-60.5 | -60.6186 | 26.6677 | 776.8762 | 167.8803 | 193.4664 | 232.4017 | 266.9825 | 306.7106 | 3.525%
9856 | 27-61 | -60.8899 | 26.6677 | 777.0415 | 168.7722 | 194.2325 | 233.3593 | 268.1147 | 308.0478 | 3.611%
9857 | 27-61 | -61.1613 | 26.6677 | 777.5986 | 169.5255 | 194.9469 | 234.2505 | 269.1667 | 309.2887 | 3.686%
9858 | 27-61.5 | -61.4326 | 26.6677 | 778.5468 | 170.2377 | 195.6963 | 235.2083 | 270.3172 | 310.6677 | 3.758%
9859 | 27-61.5 | -61.7039 | 26.6677 | 779.8847 | 170.884 | 196.4362 | 236.1637 | 271.4728 | 312.0621 | 3.825%
9860 | 27-62 | -61.9752 | 26.6677 | 781.6101 | 171.4778 | 197.1592 | 237.1048 | 272.6174 | 313.4502 | 3.887%
9861 | 27-62 | -62.2465 | 26.6677 | 783.7206 | 172.1216 | 197.9726 | 238.2001 | 273.979 | 315.1338 | 3.953%
9862 | 27-62.5 | -62.5179 | 26.6677 | 786.2131 | 172.7756 | 198.8057 | 239.3318 | 275.3936 | 316.8914 | 4.02%
9863 | 27-63 | -62.7892 | 26.6677 | 789.0839 | 173.4327 | 199.6444 | 240.4733 | 276.8225 | 318.6687 | 4.087%
9864 | 27-63 | -63.0605 | 26.6677 | 792.3288 | 174.1569 | 200.5835 | 241.7729 | 278.4655 | 320.7296 | 4.161%
9865 | 27-63.5 | -63.3318 | 26.6677 | 795.9434 | 174.887 | 201.5276 | 243.0753 | 280.1091 | 322.7882 | 4.235%
9866 | 27-63.5 | -63.6031 | 26.6677 | 799.9226 | 175.6046 | 202.4477 | 244.3337 | 281.6887 | 324.7576 | 4.31%
9867 | 27-64 | -63.8745 | 26.6677 | 804.2609 | 176.3511 | 203.4067 | 245.6479 | 283.3401 | 326.8183 | 4.389%
9868 | 27-64 | -64.1458 | 26.6677 | 808.9527 | 177.0674 | 204.3176 | 246.8826 | 284.8814 | 328.7308 | 4.465%
9869 | 27-64.5 | -64.4171 | 26.6677 | 813.9917 | 177.7476 | 205.1724 | 248.0266 | 286.298 | 330.4765 | 4.54%
9870 | 27-64.5 | -64.6884 | 26.6677 | 819.3715 | 178.4284 | 206.0238 | 249.1601 | 287.6971 | 332.1956 | 4.616%
9871 | 27-65 | -64.9598 | 26.6677 | 825.0854 | 179.0645 | 206.8042 | 250.1772 | 288.9353 | 333.6989 | 4.69%
9872 | 27-65 | -65.2311 | 26.6677 | 831.1267 | 179.6705 | 207.5365 | 251.1149 | 290.0634 | 335.0538 | 4.763%
9873 | 27-65.5 | -65.5024 | 26.6677 | 837.488 | 180.2842 | 208.277 | 252.0613 | 291.2007 | 336.4184 | 4.837%
9874 | 27-66 | -65.7737 | 26.6677 | 844.1622 | 180.8346 | 208.9192 | 252.8489 | 292.1197 | 337.4907 | 4.907%
9875 | 27-66 | -66.045 | 26.6677 | 851.142 | 181.3446 | 209.501 | 253.5412 | 292.9091 | 338.3909 | 4.975%
9876 | 27-66.5 | -66.3164 | 26.6677 | 858.4198 | 181.8551 | 210.0853 | 254.2396 | 293.7085 | 339.3056 | 5.044%
9877 | 27-66.5 | -66.5877 | 26.6677 | 865.988 | 182.2808 | 210.5562 | 254.7761 | 294.299 | 339.954 | 5.104%
9878 | 27-67 | -66.859 | 26.6677 | 873.8392 | 182.6643 | 210.9792 | 255.2559 | 294.8252 | 340.5294 | 5.159%
9879 | 27-67 | -67.1303 | 26.6677 | 881.9658 | 183.0497 | 211.4189 | 255.779 | 295.4218 | 341.2096 | 5.212%
9880 | 27-67.5 | -67.4016 | 26.6677 | 890.3601 | 183.3721 | 211.7832 | 256.2068 | 295.9046 | 341.7542 | 5.258%
9881 | 27-67.5 | -67.673 | 26.6677 | 899.0148 | 183.6847 | 212.1471 | 256.6517 | 296.4224 | 342.3569 | 5.301%
9882 | 27-68 | -67.9443 | 26.6677 | 907.9222 | 184.0227 | 212.5591 | 257.1848 | 297.0685 | 343.1383 | 5.344%
9883 | 27-68 | -68.2156 | 26.6677 | 917.075 | 184.3072 | 212.9037 | 257.6273 | 297.6017 | 343.7797 | 5.381%
9884 | 27-68.5 | -68.4869 | 26.6677 | 926.4659 | 184.579 | 213.238 | 258.0641 | 298.1347 | 344.4279 | 5.416%
9885 | 27-69 | -68.7583 | 26.6677 | 936.0877 | 184.8596 | 213.5917 | 258.5394 | 298.7248 | 345.1572 | 5.45%
9886 | 27-69 | -69.0296 | 26.6677 | 945.9333 | 185.0504 | 213.8264 | 258.8463 | 299.0994 | 345.613 | 5.475%
9887 | 27-69.5 | -69.3009 | 26.6677 | 955.9959 | 185.2203 | 214.0443 | 259.1444 | 299.4739 | 346.0804 | 5.495%
9888 | 27-69.5 | -69.5722 | 26.6677 | 966.2685 | 185.3964 | 214.2845 | 259.4942 | 299.9296 | 346.6666 | 5.514%
9889 | 27-70 | -69.8435 | 26.6677 | 976.7445 | 185.4661 | 214.3859 | 259.6505 | 300.1395 | 346.9431 | 5.52%
9890 | 27-70 | -70.1149 | 26.6677 | 987.4175 | 185.5173 | 214.4655 | 259.7795 | 300.3173 | 347.1817 | 5.523%
9891 | 27-70.5 | -70.3862 | 26.6677 | 998.281 | 185.5712 | 214.5504 | 259.9185 | 300.5097 | 347.4409 | 5.527%
9892 | 27-70.5 | -70.6575 | 26.6677 | 1009.329 | 185.5468 | 214.5199 | 259.878 | 300.4597 | 347.3795 | 5.524%
9893 | 27-71 | -70.9288 | 26.6677 | 1020.5553 | 185.5131 | 214.47 | 259.8001 | 300.3547 | 347.2409 | 5.521%
9894 | 27-71 | -71.2001 | 26.6677 | 1031.9541 | 185.4785 | 214.4117 | 259.7006 | 300.2144 | 347.0499 | 5.519%
9895 | 27-71.5 | -71.4715 | 26.6677 | 1043.5198 | 185.39 | 214.271 | 259.4689 | 299.8933 | 346.6172 | 5.514%
9896 | 27-71.5 | -71.7428 | 26.6677 | 1055.2467 | 185.3259 | 214.1617 | 259.2805 | 299.6267 | 346.253 | 5.511%
9897 | 27-72 | -72.0141 | 26.6677 | 1067.1296 | 185.2848 | 214.0818 | 259.1319 | 299.41 | 345.9506 | 5.511%
9898 | 27-72.5 | -72.2854 | 26.6677 | 1079.1633 | 185.2025 | 213.9406 | 258.8876 | 299.0637 | 345.4767 | 5.507%
9899 | 27-72.5 | -72.5568 | 26.6677 | 1091.3427 | 185.1759 | 213.8735 | 258.7486 | 298.8527 | 345.1749 | 5.51%
9900 | 27-73 | -72.8281 | 26.6677 | 1103.663 | 185.1865 | 213.8529 | 258.6713 | 298.7179 | 344.9668 | 5.517%
9901 | 27-73 | -73.0994 | 26.6677 | 1116.1195 | 185.1501 | 213.7545 | 258.4619 | 298.3974 | 344.5057 | 5.522%
9902 | 27-73.5 | -73.3707 | 26.6677 | 1128.7077 | 185.1784 | 213.7402 | 258.3696 | 298.2251 | 344.2311 | 5.535%
9903 | 27-73.5 | -73.642 | 26.6677 | 1141.423 | 185.2415 | 213.771 | 258.3397 | 298.132 | 344.0559 | 5.552%
9904 | 27-74 | -73.9134 | 26.6677 | 1154.2614 | 185.2654 | 213.7438 | 258.2191 | 297.9162 | 343.7183 | 5.566%
9905 | 27-74 | -74.1847 | 26.6677 | 1167.2187 | 185.3313 | 213.7796 | 258.1983 | 297.8361 | 343.5612 | 5.583%
9906 | 27-74.5 | -74.456 | 26.6677 | 1180.291 | 185.4066 | 213.8316 | 258.2053 | 297.7954 | 343.4581 | 5.6%
9907 | 27-74.5 | -74.7273 | 26.6677 | 1193.4743 | 185.4319 | 213.8124 | 258.105 | 297.6126 | 343.1697 | 5.613%
9908 | 27-75 | -74.9986 | 26.6677 | 1206.7652 | 185.4595 | 213.7949 | 258.0052 | 297.4288 | 342.8787 | 5.627%
9909 | 27-75.5 | -75.27 | 26.6677 | 1220.1599 | 185.4563 | 213.7363 | 257.8468 | 297.17 | 342.4925 | 5.637%
9910 | 27-75.5 | -75.5413 | 26.6677 | 1233.6551 | 185.3724 | 213.575 | 257.5494 | 296.7375 | 341.8907 | 5.637%
9911 | 27-76 | -75.8126 | 26.6677 | 1247.2475 | 185.2687 | 213.3981 | 257.2443 | 296.306 | 341.3011 | 5.633%
9912 | 27-76 | -76.0839 | 26.6677 | 1260.9339 | 185.1073 | 213.1538 | 256.8566 | 295.7779 | 340.5987 | 5.62%
9913 | 27-76.5 | -76.3553 | 26.6677 | 1274.7113 | 184.8558 | 212.7992 | 256.325 | 295.0746 | 339.6836 | 5.595%
9914 | 27-76.5 | -76.6266 | 26.6677 | 1288.5766 | 184.5937 | 212.4528 | 255.8364 | 294.4497 | 338.8919 | 5.565%
9915 | 27-77 | -76.8979 | 26.6677 | 1302.527 | 184.2827 | 212.0572 | 255.2998 | 293.7793 | 338.0594 | 5.526%
9916 | 27-77 | -77.1692 | 26.6677 | 1316.5598 | 183.9051 | 211.5838 | 254.6676 | 292.9975 | 337.0969 | 5.477%
9917 | 27-77.5 | -77.4405 | 26.6677 | 1330.6723 | 183.5334 | 211.1372 | 254.1001 | 292.3183 | 336.2852 | 5.426%
9918 | 27-77.5 | -77.7119 | 26.6677 | 1344.8619 | 183.12 | 210.6456 | 253.4828 | 291.5858 | 335.4167 | 5.369%
9919 | 27-78 | -77.9832 | 26.6677 | 1359.1263 | 182.6499 | 210.0852 | 252.7771 | 290.7468 | 334.4201 | 5.305%
9920 | 27-78.5 | -78.2545 | 26.6677 | 1373.4631 | 182.1842 | 209.5501 | 252.1339 | 290.0075 | 333.5705 | 5.238%
9921 | 27-78.5 | -78.5258 | 26.6677 | 1387.8698 | 181.4517 | 208.6829 | 251.0516 | 288.7289 | 332.0612 | 5.138%
9922 | 27-79 | -78.7971 | 26.6677 | 1402.3445 | 180.2394 | 207.2546 | 249.2105 | 286.5056 | 329.3835 | 4.983%
9923 | 27-79 | -79.0685 | 26.6677 | 1416.8849 | 178.3408 | 205.346 | 246.7325 | 283.4998 | 325.7493 | 4.752%
9924 | 27-79.5 | -79.3398 | 26.6677 | 1431.4889 | 176.1911 | 203.281 | 244.0367 | 280.2182 | 321.7697 | 4.502%
9925 | 27-79.5 | -79.6111 | 26.6677 | 1446.1547 | 174.1195 | 201.3043 | 241.4455 | 277.0555 | 317.9251 | 4.271%
9926 | 27-80 | -79.8824 | 26.6677 | 1460.8803 | 172.177 | 199.4854 | 239.0671 | 274.1573 | 314.4072 | 4.062%
9927 | 27-80 | -80.1537 | 26.6677 | 1475.6638 | 170.2867 | 197.7198 | 236.7454 | 271.3179 | 310.9496 | 3.868%
9928 | 27-80.5 | -80.4251 | 26.6677 | 1490.5036 | 168.4381 | 196.0109 | 234.4914 | 268.5556 | 307.5797 | 3.685%
9929 | 27-80.5 | -80.6964 | 26.6677 | 1505.3978 | 166.6685 | 194.4188 | 232.4074 | 266.0112 | 304.4856 | 3.516%
9930 | 27-81 | -80.9677 | 26.6677 | 1520.3449 | 165.2254 | 193.0748 | 230.6385 | 263.8457 | 301.8456 | 3.382%
9931 | 27-81 | -81.239 | 26.6677 | 1535.3432 | 164.2812 | 192.1063 | 229.3777 | 262.3128 | 299.9877 | 3.295%
9932 | 27-81.5 | -81.5104 | 26.6677 | 1550.3913 | 163.8329 | 191.5898 | 228.7516 | 261.5887 | 299.1502 | 3.25%
9933 | 27-82 | -81.7817 | 26.6677 | 1565.4876 | 163.4676 | 191.1755 | 228.2624 | 261.0341 | 298.5218 | 3.214%
9934 | 27-82 | -82.053 | 26.6677 | 1580.6308 | 163.3787 | 191.1229 | 228.2782 | 261.121 | 298.7006 | 3.203%
9935 | 27-82.5 | -82.3243 | 26.6677 | 1595.8194 | 163.8134 | 191.7091 | 229.1893 | 262.3473 | 300.3154 | 3.236%
9936 | 27-82.5 | -82.5956 | 26.6677 | 1611.052 | 164.9629 | 192.8204 | 230.8109 | 264.4579 | 303.0232 | 3.331%
9937 | 27-83 | -82.867 | 26.6677 | 1626.3276 | 166.3794 | 194.1172 | 232.7024 | 266.9191 | 306.1803 | 3.448%
9938 | 27-83 | -83.1383 | 26.6677 | 1641.6446 | 167.7738 | 195.4136 | 234.6329 | 269.4602 | 309.4699 | 3.564%
9939 | 27-83.5 | -83.4096 | 26.6677 | 1657.0021 | 169.0761 | 196.5887 | 236.3849 | 271.7676 | 312.4583 | 3.673%
9940 | 27-83.5 | -83.6809 | 26.6677 | 1672.3988 | 170.3562 | 197.7346 | 238.0924 | 274.0158 | 315.3692 | 3.782%
9941 | 27-84 | -83.9522 | 26.6677 | 1687.8335 | 171.664 | 198.9069 | 239.8376 | 276.3127 | 318.3427 | 3.896%
9942 | 27-84 | -84.2236 | 26.6677 | 1703.3053 | 172.9551 | 200.0304 | 241.4889 | 278.4743 | 321.1294 | 4.01%
9943 | 27-84.5 | -84.4949 | 26.6677 | 1718.8131 | 173.9816 | 200.9743 | 242.9031 | 280.343 | 323.5566 | 4.101%
9944 | 27-85 | -84.7662 | 26.6677 | 1734.3558 | 174.6204 | 201.6886 | 244.0138 | 281.84 | 325.5319 | 4.154%
9945 | 27-85 | -85.0375 | 26.6677 | 1749.9325 | 174.8197 | 202.0177 | 244.5729 | 282.6261 | 326.6016 | 4.166%
9946 | 27-85.5 | -85.3089 | 26.6677 | 1765.5422 | 174.9891 | 202.3034 | 245.0625 | 283.3172 | 327.5447 | 4.176%
9947 | 27-85.5 | -85.5802 | 26.6677 | 1781.184 | 175.2029 | 202.6385 | 245.6089 | 284.0714 | 328.558 | 4.192%
9948 | 27-86 | -85.8515 | 26.6677 | 1796.857 | 175.3729 | 202.8826 | 245.9805 | 284.5673 | 329.2077 | 4.206%
9949 | 27-86 | -86.1228 | 26.6677 | 1812.5604 | 175.5733 | 203.1401 | 246.3339 | 285.012 | 329.7637 | 4.226%
9950 | 27-86.5 | -86.3941 | 26.6677 | 1828.2933 | 175.8115 | 203.4179 | 246.6745 | 285.4097 | 330.2282 | 4.253%
9951 | 27-86.5 | -86.6655 | 26.6677 | 1844.0549 | 175.9903 | 203.5952 | 246.8424 | 285.5631 | 330.3589 | 4.277%
9952 | 27-87 | -86.9368 | 26.6677 | 1859.8445 | 176.1816 | 203.7967 | 247.0556 | 285.7829 | 330.5826 | 4.301%
9953 | 27-87 | -87.2081 | 26.6677 | 1875.6613 | 176.3794 | 204.0158 | 247.3062 | 286.0602 | 330.8894 | 4.325%
9954 | 27-87.5 | -87.4794 | 26.6677 | 1891.5045 | 176.481 | 204.1152 | 247.3983 | 286.1423 | 330.9565 | 4.339%
9955 | 27-88 | -87.7507 | 26.6677 | 1907.3735 | 176.5344 | 204.1725 | 247.4608 | 286.2091 | 331.0276 | 4.346%
9956 | 27-88 | -88.0221 | 26.6677 | 1923.2675 | 176.5209 | 204.1608 | 247.4534 | 286.2065 | 331.0321 | 4.344%
9957 | 27-88.5 | -88.2934 | 26.6677 | 1939.1859 | 176.3603 | 203.9674 | 247.207 | 285.9113 | 330.6791 | 4.326%
9958 | 27-88.5 | -88.5647 | 26.6677 | 1955.1281 | 176.1522 | 203.7409 | 246.9557 | 285.6416 | 330.3917 | 4.3%
9959 | 27-89 | -88.836 | 26.6677 | 1971.0933 | 175.8835 | 203.4619 | 246.6691 | 285.3558 | 330.1147 | 4.265%
9960 | 27-89 | -89.1074 | 26.6677 | 1987.0811 | 175.5002 | 203.0488 | 246.2176 | 284.8773 | 329.6124 | 4.218%
9961 | 27-89.5 | -89.3787 | 26.6677 | 2003.0908 | 175.0869 | 202.6313 | 245.8097 | 284.4921 | 329.2677 | 4.164%
9962 | 27-89.5 | -89.65 | 26.6677 | 2019.1219 | 174.6251 | 202.1811 | 245.3991 | 284.1362 | 328.9945 | 4.104%
9963 | 27-90 | -89.9213 | 26.6677 | 2035.1737 | 174.0779 | 201.6371 | 244.8825 | 283.664 | 328.5937 | 4.035%
9964 | 27-90 | -90.1926 | 26.6677 | 2051.2458 | 173.5404 | 201.1113 | 244.3993 | 283.2404 | 328.2603 | 3.968%
9965 | 27-90.5 | -90.464 | 26.6677 | 2067.3376 | 172.9822 | 200.5588 | 243.8785 | 282.7684 | 327.8655 | 3.9%
9966 | 27-90.5 | -90.7353 | 26.6677 | 2083.4486 | 172.3537 | 199.9115 | 243.2132 | 282.1032 | 327.2166 | 3.828%
9967 | 27-50 | -50.0371 | 26.939 | 1047.46 | 110.8851 | 144.7586 | 183.8367 | 208.0709 | 235.501 | 0.7275%
9968 | 27-50.5 | -50.3084 | 26.939 | 1036.2093 | 112.4668 | 147.0107 | 185.2517 | 209.7475 | 237.4837 | 0.7635%
9969 | 27-50.5 | -50.5797 | 26.939 | 1025.1311 | 114.0636 | 149.2779 | 186.6575 | 211.4002 | 239.424 | 0.8015%
9970 | 27-51 | -50.851 | 26.939 | 1014.2311 | 115.6832 | 151.5574 | 188.0709 | 213.07 | 241.3932 | 0.8422%
9971 | 27-51 | -51.1224 | 26.939 | 1003.5151 | 117.3566 | 153.8427 | 189.5391 | 214.8322 | 243.5018 | 0.8865%
9972 | 27-51.5 | -51.3937 | 26.939 | 992.9891 | 118.9827 | 156.0034 | 190.9328 | 216.4993 | 245.4906 | 0.9314%
9973 | 27-51.5 | -51.665 | 26.939 | 982.6593 | 120.5761 | 158.0531 | 192.2787 | 218.1136 | 247.4211 | 0.9774%
9974 | 27-52 | -51.9363 | 26.939 | 972.5319 | 122.161 | 160.0075 | 193.6174 | 219.7345 | 249.376 | 1.025%
9975 | 27-52 | -52.2077 | 26.939 | 962.6133 | 123.6636 | 161.7941 | 194.8422 | 221.1976 | 251.1198 | 1.072%
9976 | 27-52.5 | -52.479 | 26.939 | 952.9102 | 125.1116 | 163.4399 | 196.0011 | 222.5832 | 252.7725 | 1.119%
9977 | 27-53 | -52.7503 | 26.939 | 943.4291 | 126.5243 | 164.9504 | 197.1324 | 223.9531 | 254.4254 | 1.166%
9978 | 27-53 | -53.0216 | 26.939 | 934.177 | 127.83 | 166.2528 | 198.1437 | 225.1693 | 255.8837 | 1.211%
9979 | 27-53.5 | -53.2929 | 26.939 | 925.1606 | 129.0898 | 167.4218 | 199.1241 | 226.3623 | 257.3295 | 1.255%
9980 | 27-53.5 | -53.5643 | 26.939 | 916.3869 | 130.3325 | 168.4746 | 200.1132 | 227.5871 | 258.836 | 1.3%
9981 | 27-54 | -53.8356 | 26.939 | 907.8631 | 131.4928 | 169.3401 | 201.0233 | 228.7099 | 260.2128 | 1.342%
9982 | 27-54 | -54.1069 | 26.939 | 899.5962 | 132.6797 | 170.162 | 201.9857 | 229.9084 | 261.6946 | 1.386%
9983 | 27-54.5 | -54.3782 | 26.939 | 891.5934 | 133.9292 | 170.9757 | 203.0409 | 231.2341 | 263.3457 | 1.433%
9984 | 27-54.5 | -54.6495 | 26.939 | 883.862 | 135.1302 | 171.7217 | 204.0362 | 232.4669 | 264.8633 | 1.48%
9985 | 27-55 | -54.9209 | 26.939 | 876.409 | 136.403 | 172.5268 | 205.1261 | 233.8241 | 266.5416 | 1.532%
9986 | 27-55 | -55.1922 | 26.939 | 869.2418 | 137.773 | 173.4141 | 206.3381 | 235.3417 | 268.4274 | 1.589%
9987 | 27-55.5 | -55.4635 | 26.939 | 862.3675 | 139.1217 | 174.2907 | 207.5019 | 236.7737 | 270.1805 | 1.648%
9988 | 27-55.5 | -55.7348 | 26.939 | 855.793 | 140.5421 | 175.223 | 208.7482 | 238.3138 | 272.0726 | 1.713%
9989 | 27-56 | -56.0061 | 26.939 | 849.5255 | 142.0441 | 176.2171 | 210.0842 | 239.9702 | 274.1136 | 1.783%
9990 | 27-56.5 | -56.2775 | 26.939 | 843.5718 | 143.5283 | 177.195 | 211.37 | 241.5427 | 276.0284 | 1.856%
9991 | 27-56.5 | -56.5488 | 26.939 | 837.9385 | 145.0823 | 178.2159 | 212.7168 | 243.1931 | 278.0417 | 1.935%
9992 | 27-57 | -56.8201 | 26.939 | 832.6323 | 146.7047 | 179.2773 | 214.1187 | 244.9127 | 280.1414 | 2.02%
9993 | 27-57 | -57.0914 | 26.939 | 827.6593 | 148.322 | 180.3235 | 215.4812 | 246.5688 | 282.1475 | 2.109%
9994 | 27-57.5 | -57.3628 | 26.939 | 823.0257 | 150.0174 | 181.4098 | 216.904 | 248.3048 | 284.2574 | 2.206%
9995 | 27-57.5 | -57.6341 | 26.939 | 818.7373 | 151.7671 | 182.5176 | 218.3541 | 250.0735 | 286.4066 | 2.309%
9996 | 27-58 | -57.9054 | 26.939 | 814.7994 | 153.463 | 183.5734 | 219.7151 | 251.7169 | 288.3856 | 2.414%
9997 | 27-58 | -58.1767 | 26.939 | 811.2173 | 155.2074 | 184.6719 | 221.1449 | 253.4545 | 290.4901 | 2.527%
9998 | 27-58.5 | -58.448 | 26.939 | 807.9957 | 156.9369 | 185.7766 | 222.5786 | 255.1936 | 292.593 | 2.644%
9999 | 27-58.5 | -58.7194 | 26.939 | 805.1388 | 158.5406 | 186.7983 | 223.8728 | 256.7379 | 294.4325 | 2.758%
10000 | 27-59 | -58.9907 | 26.939 | 802.6506 | 160.1235 | 187.8435 | 225.2119 | 258.3481 | 296.3643 | 2.875%
10001 | 27-59.5 | -59.262 | 26.939 | 800.5346 | 161.6328 | 188.8676 | 226.5208 | 259.9196 | 298.2469 | 2.991%
10002 | 27-59.5 | -59.5333 | 26.939 | 798.7937 | 162.9999 | 189.7916 | 227.6734 | 261.2802 | 299.8514 | 3.101%
10003 | 27-60 | -59.8046 | 26.939 | 797.4304 | 164.3176 | 190.7097 | 228.8311 | 262.6573 | 301.487 | 3.211%
10004 | 27-60 | -60.076 | 26.939 | 796.4466 | 165.5416 | 191.5918 | 229.944 | 263.9815 | 303.0602 | 3.316%
10005 | 27-60.5 | -60.3473 | 26.939 | 795.8437 | 166.6324 | 192.3979 | 230.945 | 265.1592 | 304.4446 | 3.414%
10006 | 27-60.5 | -60.6186 | 26.939 | 795.6227 | 167.6527 | 193.1971 | 231.949 | 266.3503 | 305.8558 | 3.509%
10007 | 27-61 | -60.8899 | 26.939 | 795.7837 | 168.5538 | 193.9583 | 232.9074 | 267.4892 | 307.2072 | 3.595%
10008 | 27-61 | -61.1613 | 26.939 | 796.3266 | 169.3153 | 194.664 | 233.7912 | 268.5356 | 308.4446 | 3.67%
10009 | 27-61.5 | -61.4326 | 26.939 | 797.2506 | 170.0324 | 195.4 | 234.7332 | 269.6678 | 309.8027 | 3.743%
10010 | 27-61.5 | -61.7039 | 26.939 | 798.5544 | 170.6767 | 196.1253 | 235.6697 | 270.8004 | 311.169 | 3.809%
10011 | 27-62 | -61.9752 | 26.939 | 800.2361 | 171.263 | 196.8356 | 236.594 | 271.924 | 312.5311 | 3.87%
10012 | 27-62 | -62.2465 | 26.939 | 802.2934 | 171.8974 | 197.6368 | 237.6721 | 273.2636 | 314.1867 | 3.935%
10013 | 27-62.5 | -62.5179 | 26.939 | 804.7232 | 172.5426 | 198.4577 | 238.7856 | 274.6542 | 315.9129 | 4.001%
10014 | 27-63 | -62.7892 | 26.939 | 807.5224 | 173.1931 | 199.2867 | 239.9122 | 276.0629 | 317.6635 | 4.068%
10015 | 27-63 | -63.0605 | 26.939 | 810.687 | 173.9164 | 200.2244 | 241.2094 | 277.7026 | 319.7199 | 4.141%
10016 | 27-63.5 | -63.3318 | 26.939 | 814.2128 | 174.6499 | 201.1727 | 242.5171 | 279.3525 | 321.7859 | 4.216%
10017 | 27-63.5 | -63.6031 | 26.939 | 818.095 | 175.3748 | 202.1018 | 243.7874 | 280.9466 | 323.7727 | 4.292%
10018 | 27-64 | -63.8745 | 26.939 | 822.3287 | 176.1336 | 203.0769 | 245.1238 | 282.626 | 325.8686 | 4.372%
10019 | 27-64 | -64.1458 | 26.939 | 826.9085 | 176.8656 | 204.0072 | 246.3839 | 284.1982 | 327.8185 | 4.45%
10020 | 27-64.5 | -64.4171 | 26.939 | 831.8285 | 177.5634 | 204.8823 | 247.5525 | 285.6432 | 329.5966 | 4.527%
10021 | 27-64.5 | -64.6884 | 26.939 | 837.0828 | 178.2635 | 205.7552 | 248.7106 | 287.0694 | 331.3457 | 4.606%
10022 | 27-65 | -64.9598 | 26.939 | 842.6651 | 178.9202 | 206.5587 | 249.7543 | 288.337 | 332.8812 | 4.683%
10023 | 27-65 | -65.2311 | 26.939 | 848.5689 | 179.5461 | 207.3128 | 250.7164 | 289.4915 | 334.2644 | 4.758%
10024 | 27-65.5 | -65.5024 | 26.939 | 854.7875 | 180.1767 | 208.0705 | 251.6799 | 290.6453 | 335.6443 | 4.835%
10025 | 27-66 | -65.7737 | 26.939 | 861.3142 | 180.7431 | 208.7294 | 252.4848 | 291.5816 | 336.7335 | 4.908%
10026 | 27-66 | -66.045 | 26.939 | 868.1419 | 181.2696 | 209.3296 | 253.1982 | 292.3946 | 337.6598 | 4.978%
10027 | 27-66.5 | -66.3164 | 26.939 | 875.2635 | 181.7972 | 209.9344 | 253.9224 | 293.2245 | 338.6109 | 5.049%
10028 | 27-66.5 | -66.5877 | 26.939 | 882.672 | 182.2394 | 210.4245 | 254.4825 | 293.8427 | 339.2916 | 5.111%
10029 | 27-67 | -66.859 | 26.939 | 890.3602 | 182.6401 | 210.8677 | 254.9874 | 294.3985 | 339.9019 | 5.169%
10030 | 27-67 | -67.1303 | 26.939 | 898.3208 | 183.0447 | 211.3307 | 255.5407 | 295.0316 | 340.6261 | 5.225%
10031 | 27-67.5 | -67.4016 | 26.939 | 906.5467 | 183.3846 | 211.7158 | 255.9946 | 295.5453 | 341.2073 | 5.273%
10032 | 27-67.5 | -67.673 | 26.939 | 915.0306 | 183.7144 | 212.1005 | 256.4661 | 296.0952 | 341.8487 | 5.319%
10033 | 27-68 | -67.9443 | 26.939 | 923.7654 | 184.0703 | 212.5354 | 257.0302 | 296.7799 | 342.6779 | 5.364%
10034 | 27-68 | -68.2156 | 26.939 | 932.7442 | 184.3754 | 212.9075 | 257.5119 | 297.3638 | 343.3839 | 5.404%
10035 | 27-68.5 | -68.4869 | 26.939 | 941.9597 | 184.6707 | 213.2737 | 257.9951 | 297.9569 | 344.1093 | 5.441%
10036 | 27-69 | -68.7583 | 26.939 | 951.4053 | 184.9781 | 213.6635 | 258.5223 | 298.6144 | 344.925 | 5.479%
10037 | 27-69 | -69.0296 | 26.939 | 961.0739 | 185.197 | 213.9364 | 258.8844 | 299.0605 | 345.4724 | 5.506%
10038 | 27-69.5 | -69.3009 | 26.939 | 970.9591 | 185.3946 | 214.1906 | 259.2337 | 299.5004 | 346.0226 | 5.53%
10039 | 27-69.5 | -69.5722 | 26.939 | 981.0541 | 185.597 | 214.4642 | 259.6284 | 300.012 | 346.678 | 5.552%
10040 | 27-70 | -69.8435 | 26.939 | 991.3525 | 185.6884 | 214.5909 | 259.8156 | 300.258 | 346.9966 | 5.561%
10041 | 27-70 | -70.1149 | 26.939 | 1001.8481 | 185.7579 | 214.6907 | 259.9677 | 300.4612 | 347.2631 | 5.567%
10042 | 27-70.5 | -70.3862 | 26.939 | 1012.5346 | 185.8265 | 214.791 | 260.1227 | 300.6696 | 347.538 | 5.573%
10043 | 27-70.5 | -70.6575 | 26.939 | 1023.4061 | 185.8113 | 214.7678 | 260.0859 | 300.6197 | 347.4716 | 5.572%
10044 | 27-71 | -70.9288 | 26.939 | 1034.4567 | 185.7844 | 214.7223 | 260.008 | 300.5098 | 347.3218 | 5.571%
10045 | 27-71 | -71.2001 | 26.939 | 1045.6807 | 185.7548 | 214.6664 | 259.9057 | 300.3614 | 347.1157 | 5.571%
10046 | 27-71.5 | -71.4715 | 26.939 | 1057.0724 | 185.6693 | 214.5261 | 259.6696 | 300.0309 | 346.6675 | 5.566%
10047 | 27-71.5 | -71.7428 | 26.939 | 1068.6267 | 185.6048 | 214.4131 | 259.4716 | 299.7489 | 346.2802 | 5.564%
10048 | 27-72 | -72.0141 | 26.939 | 1080.3381 | 185.5601 | 214.3254 | 259.3079 | 299.5095 | 345.9459 | 5.564%
10049 | 27-72.5 | -72.2854 | 26.939 | 1092.2015 | 185.4701 | 214.1705 | 259.0394 | 299.1287 | 345.4246 | 5.56%
10050 | 27-72.5 | -72.5568 | 26.939 | 1104.2122 | 185.4328 | 214.0852 | 258.8687 | 298.8728 | 345.0614 | 5.562%
10051 | 27-73 | -72.8281 | 26.939 | 1116.3652 | 185.4304 | 214.0426 | 258.7539 | 298.6852 | 344.7813 | 5.569%
10052 | 27-73 | -73.0994 | 26.939 | 1128.6559 | 185.3806 | 213.9226 | 258.509 | 298.3155 | 344.2541 | 5.574%
10053 | 27-73.5 | -73.3707 | 26.939 | 1141.0799 | 185.3981 | 213.8918 | 258.3903 | 298.1072 | 343.9315 | 5.586%
10054 | 27-73.5 | -73.642 | 26.939 | 1153.6328 | 185.4519 | 213.9094 | 258.3404 | 297.9875 | 343.7218 | 5.602%
10055 | 27-74 | -73.9134 | 26.939 | 1166.3103 | 185.4644 | 213.867 | 258.1984 | 297.7444 | 343.3498 | 5.615%
10056 | 27-74 | -74.1847 | 26.939 | 1179.1086 | 185.5188 | 213.8887 | 258.1591 | 297.6419 | 343.1656 | 5.631%
10057 | 27-74.5 | -74.456 | 26.939 | 1192.0235 | 185.5822 | 213.9274 | 258.1508 | 297.5844 | 343.0438 | 5.647%
10058 | 27-74.5 | -74.7273 | 26.939 | 1205.0514 | 185.5945 | 213.8956 | 258.0391 | 297.3916 | 342.7479 | 5.657%
10059 | 27-75 | -74.9986 | 26.939 | 1218.1885 | 185.6084 | 213.8656 | 257.9297 | 297.2017 | 342.4555 | 5.668%
10060 | 27-75.5 | -75.27 | 26.939 | 1231.4313 | 185.5897 | 213.7932 | 257.7614 | 296.9372 | 342.0694 | 5.676%
10061 | 27-75.5 | -75.5413 | 26.939 | 1244.7765 | 185.4874 | 213.6154 | 257.4511 | 296.4964 | 341.4655 | 5.672%
10062 | 27-76 | -75.8126 | 26.939 | 1258.2207 | 185.3637 | 213.4209 | 257.1337 | 296.0583 | 340.8774 | 5.664%
10063 | 27-76 | -76.0839 | 26.939 | 1271.7607 | 185.1807 | 213.1586 | 256.7355 | 295.5279 | 340.1835 | 5.646%
10064 | 27-76.5 | -76.3553 | 26.939 | 1285.3935 | 184.9056 | 212.7853 | 256.1951 | 294.8263 | 339.2841 | 5.616%
10065 | 27-76.5 | -76.6266 | 26.939 | 1299.1161 | 184.6158 | 212.415 | 255.6904 | 294.194 | 338.4969 | 5.58%
10066 | 27-77 | -76.8979 | 26.939 | 1312.9256 | 184.2732 | 211.9904 | 255.1305 | 293.5071 | 337.657 | 5.535%
10067 | 27-77 | -77.1692 | 26.939 | 1326.8194 | 183.8624 | 211.4856 | 254.4715 | 292.704 | 336.6812 | 5.48%
10068 | 27-77.5 | -77.4405 | 26.939 | 1340.7947 | 183.4592 | 211.0106 | 253.8819 | 292.0101 | 335.8648 | 5.423%
10069 | 27-77.5 | -77.7119 | 26.939 | 1354.8489 | 183.0141 | 210.4898 | 253.2413 | 291.261 | 334.989 | 5.36%
10070 | 27-78 | -77.9832 | 26.939 | 1368.9796 | 182.5101 | 209.8961 | 252.5047 | 290.3942 | 333.9696 | 5.289%
10071 | 27-78.5 | -78.2545 | 26.939 | 1383.1845 | 182.0093 | 209.3241 | 251.8227 | 289.6154 | 333.0801 | 5.217%
10072 | 27-78.5 | -78.5258 | 26.939 | 1397.4611 | 181.2353 | 208.4102 | 250.6856 | 288.2749 | 331.5011 | 5.112%
10073 | 27-79 | -78.7971 | 26.939 | 1411.8073 | 179.972 | 206.9214 | 248.7689 | 285.9622 | 328.7177 | 4.951%
10074 | 27-79 | -79.0685 | 26.939 | 1426.221 | 178.014 | 204.9406 | 246.1977 | 282.8439 | 324.948 | 4.713%
10075 | 27-79.5 | -79.3398 | 26.939 | 1440.7 | 175.7596 | 202.7766 | 243.3727 | 279.405 | 320.7775 | 4.452%
10076 | 27-79.5 | -79.6111 | 26.939 | 1455.2424 | 173.5277 | 200.6643 | 240.6032 | 276.0241 | 316.6672 | 4.206%
10077 | 27-80 | -79.8824 | 26.939 | 1469.8462 | 171.3733 | 198.6724 | 237.9961 | 272.8452 | 312.8064 | 3.978%
10078 | 27-80 | -80.1537 | 26.939 | 1484.5097 | 169.2428 | 196.7152 | 235.4213 | 269.6953 | 308.9697 | 3.763%
10079 | 27-80.5 | -80.4251 | 26.939 | 1499.2309 | 167.1365 | 194.8043 | 232.9011 | 266.6073 | 305.2028 | 3.56%
10080 | 27-80.5 | -80.6964 | 26.939 | 1514.0082 | 165.0924 | 192.99 | 230.5363 | 263.7201 | 301.6922 | 3.37%
10081 | 27-81 | -80.9677 | 26.939 | 1528.8399 | 163.4193 | 191.4651 | 228.531 | 261.2667 | 298.7029 | 3.221%
10082 | 27-81 | -81.239 | 26.939 | 1543.7243 | 162.3211 | 190.3712 | 227.1095 | 259.5407 | 296.6133 | 3.123%
10083 | 27-81.5 | -81.5104 | 26.939 | 1558.66 | 161.8039 | 189.7887 | 226.4063 | 258.7297 | 295.6779 | 3.075%
10084 | 27-82 | -81.7817 | 26.939 | 1573.6454 | 161.3881 | 189.3242 | 225.863 | 258.1185 | 294.9907 | 3.035%
10085 | 27-82 | -82.053 | 26.939 | 1588.6791 | 161.2527 | 189.2305 | 225.8389 | 258.1679 | 295.1362 | 3.02%
10086 | 27-82.5 | -82.3243 | 26.939 | 1603.7596 | 161.6501 | 189.7888 | 226.7306 | 259.384 | 296.7532 | 3.049%
10087 | 27-82.5 | -82.5956 | 26.939 | 1618.8856 | 162.7717 | 190.887 | 228.353 | 261.5099 | 299.4955 | 3.137%
10088 | 27-83 | -82.867 | 26.939 | 1634.0558 | 164.2079 | 192.2002 | 230.2842 | 264.0343 | 302.7451 | 3.251%
10089 | 27-83 | -83.1383 | 26.939 | 1649.269 | 165.6814 | 193.5518 | 232.3052 | 266.7002 | 306.202 | 3.368%
10090 | 27-83.5 | -83.4096 | 26.939 | 1664.5238 | 167.1201 | 194.8234 | 234.1991 | 269.1929 | 309.4288 | 3.484%
10091 | 27-83.5 | -83.6809 | 26.939 | 1679.8192 | 168.5718 | 196.0883 | 236.0739 | 271.6543 | 312.6085 | 3.604%
10092 | 27-84 | -83.9522 | 26.939 | 1695.1539 | 170.0766 | 197.3929 | 237.9999 | 274.1775 | 315.8628 | 3.732%
10093 | 27-84 | -84.2236 | 26.939 | 1710.5269 | 171.5852 | 198.6702 | 239.845 | 276.5778 | 318.9416 | 3.864%
10094 | 27-84.5 | -84.4949 | 26.939 | 1725.9371 | 172.7873 | 199.7276 | 241.4071 | 278.6257 | 321.5856 | 3.969%
10095 | 27-85 | -84.7662 | 26.939 | 1741.3835 | 173.5304 | 200.5053 | 242.5956 | 280.2136 | 323.6666 | 4.032%
10096 | 27-85 | -85.0375 | 26.939 | 1756.865 | 173.7568 | 200.8476 | 243.1612 | 280.9989 | 324.7259 | 4.047%
10097 | 27-85.5 | -85.3089 | 26.939 | 1772.3807 | 173.943 | 201.1412 | 243.6481 | 281.6761 | 325.6406 | 4.06%
10098 | 27-85.5 | -85.5802 | 26.939 | 1787.9296 | 174.1837 | 201.493 | 244.2018 | 282.4275 | 326.6377 | 4.079%
10099 | 27-86 | -85.8515 | 26.939 | 1803.5109 | 174.3899 | 201.7627 | 244.5888 | 282.9276 | 327.2765 | 4.098%
10100 | 27-86 | -86.1228 | 26.939 | 1819.1236 | 174.6363 | 202.0541 | 244.9657 | 283.3842 | 327.8286 | 4.124%
10101 | 27-86.5 | -86.3941 | 26.939 | 1834.7669 | 174.9296 | 202.3745 | 245.3386 | 283.8023 | 328.2971 | 4.158%
10102 | 27-86.5 | -86.6655 | 26.939 | 1850.44 | 175.1702 | 202.6027 | 245.547 | 283.984 | 328.4391 | 4.189%
10103 | 27-87 | -86.9368 | 26.939 | 1866.1421 | 175.4283 | 202.8606 | 245.8066 | 284.2383 | 328.6806 | 4.222%
10104 | 27-87 | -87.2081 | 26.939 | 1881.8724 | 175.6961 | 203.1413 | 246.1094 | 284.5564 | 329.0118 | 4.255%
10105 | 27-87.5 | -87.4794 | 26.939 | 1897.6302 | 175.8656 | 203.3058 | 246.2607 | 284.6898 | 329.1185 | 4.278%
10106 | 27-88 | -87.7507 | 26.939 | 1913.4146 | 175.9876 | 203.4312 | 246.3881 | 284.816 | 329.2402 | 4.294%
10107 | 27-88 | -88.0221 | 26.939 | 1929.2251 | 176.0431 | 203.4888 | 246.4477 | 284.8763 | 329.3002 | 4.301%
10108 | 27-88.5 | -88.2934 | 26.939 | 1945.0609 | 175.948 | 203.3615 | 246.2659 | 284.6422 | 329.0022 | 4.292%
10109 | 27-88.5 | -88.5647 | 26.939 | 1960.9213 | 175.8007 | 203.1967 | 246.0755 | 284.4305 | 328.7677 | 4.274%
10110 | 27-89 | -88.836 | 26.939 | 1976.8058 | 175.5871 | 202.9731 | 245.8429 | 284.1956 | 328.5359 | 4.247%
10111 | 27-89 | -89.1074 | 26.939 | 1992.7137 | 175.2505 | 202.6066 | 245.4357 | 283.7576 | 328.0681 | 4.206%
10112 | 27-89.5 | -89.3787 | 26.939 | 2008.6443 | 174.875 | 202.2276 | 245.0656 | 283.4083 | 327.7559 | 4.157%
10113 | 27-89.5 | -89.65 | 26.939 | 2024.5971 | 174.4419 | 201.8078 | 244.6876 | 283.0862 | 327.517 | 4.1%
10114 | 27-90 | -89.9213 | 26.939 | 2040.5716 | 173.9139 | 201.2877 | 244.2018 | 282.6512 | 327.161 | 4.032%
10115 | 27-90 | -90.1926 | 26.939 | 2056.5671 | 173.384 | 200.7802 | 243.7489 | 282.2696 | 326.8842 | 3.965%
10116 | 27-90.5 | -90.464 | 26.939 | 2072.5832 | 172.8224 | 200.2404 | 243.2577 | 281.8441 | 326.5573 | 3.896%
10117 | 27-90.5 | -90.7353 | 26.939 | 2088.6192 | 172.1785 | 199.6 | 242.6192 | 281.226 | 325.9815 | 3.821%
10118 | 27-50 | -50.0371 | 27.2104 | 1061.3099 | 110.9878 | 144.7346 | 183.7309 | 207.8723 | 235.1869 | 0.7274%
10119 | 27-50.5 | -50.3084 | 27.2104 | 1050.2311 | 112.5172 | 146.9187 | 185.108 | 209.5072 | 237.1237 | 0.7623%
10120 | 27-50.5 | -50.5797 | 27.2104 | 1039.3255 | 114.0668 | 149.1268 | 186.4811 | 211.1245 | 239.0257 | 0.7994%
10121 | 27-51 | -50.851 | 27.2104 | 1028.5986 | 115.645 | 151.358 | 187.8666 | 212.7636 | 240.9611 | 0.8391%
10122 | 27-51 | -51.1224 | 27.2104 | 1018.0562 | 117.283 | 153.6101 | 189.3119 | 214.5 | 243.0405 | 0.8825%
10123 | 27-51.5 | -51.3937 | 27.2104 | 1007.7041 | 118.8823 | 155.7503 | 190.6865 | 216.1424 | 244.9977 | 0.9266%
10124 | 27-51.5 | -51.665 | 27.2104 | 997.5482 | 120.4589 | 157.7903 | 192.0185 | 217.735 | 246.8967 | 0.972%
10125 | 27-52 | -51.9363 | 27.2104 | 987.5946 | 122.038 | 159.7477 | 193.3502 | 219.3397 | 248.824 | 1.019%
10126 | 27-52 | -52.2077 | 27.2104 | 977.8495 | 123.5441 | 161.5486 | 194.5737 | 220.7923 | 250.5452 | 1.066%
10127 | 27-52.5 | -52.479 | 27.2104 | 968.3192 | 125.0022 | 163.2158 | 195.734 | 222.169 | 252.176 | 1.113%
10128 | 27-53 | -52.7503 | 27.2104 | 959.0102 | 126.4297 | 164.7516 | 196.8671 | 223.5296 | 253.805 | 1.161%
10129 | 27-53 | -53.0216 | 27.2104 | 949.929 | 127.7554 | 166.0836 | 197.8811 | 224.7361 | 255.2378 | 1.206%
10130 | 27-53.5 | -53.2929 | 27.2104 | 941.0823 | 129.0387 | 167.2841 | 198.865 | 225.9207 | 256.6595 | 1.251%
10131 | 27-53.5 | -53.5643 | 27.2104 | 932.4766 | 130.3068 | 168.3681 | 199.8579 | 227.1379 | 258.1439 | 1.297%
10132 | 27-54 | -53.8356 | 27.2104 | 924.1189 | 131.497 | 169.2658 | 200.7711 | 228.2508 | 259.4942 | 1.34%
10133 | 27-54 | -54.1069 | 27.2104 | 916.0159 | 132.7162 | 170.1182 | 201.7366 | 229.4394 | 260.9491 | 1.386%
10134 | 27-54.5 | -54.3782 | 27.2104 | 908.1744 | 133.9988 | 170.9579 | 202.7945 | 230.7551 | 262.5739 | 1.435%
10135 | 27-54.5 | -54.6495 | 27.2104 | 900.6013 | 135.2297 | 171.7193 | 203.7883 | 231.9729 | 264.0589 | 1.483%
10136 | 27-55 | -54.9209 | 27.2104 | 893.3035 | 136.527 | 172.5314 | 204.874 | 233.3142 | 265.7063 | 1.536%
10137 | 27-55 | -55.1922 | 27.2104 | 886.2877 | 137.9155 | 173.4214 | 206.0797 | 234.816 | 267.5638 | 1.594%
10138 | 27-55.5 | -55.4635 | 27.2104 | 879.5608 | 139.274 | 174.2956 | 207.2343 | 236.2318 | 269.2917 | 1.654%
10139 | 27-55.5 | -55.7348 | 27.2104 | 873.1294 | 140.6979 | 175.2226 | 208.4705 | 237.7569 | 271.1625 | 1.719%
10140 | 27-56 | -56.0061 | 27.2104 | 867.0001 | 142.1982 | 176.2092 | 209.7959 | 239.3994 | 273.1852 | 1.79%
10141 | 27-56.5 | -56.2775 | 27.2104 | 861.1795 | 143.6729 | 177.1757 | 211.0665 | 240.9527 | 275.0759 | 1.863%
10142 | 27-56.5 | -56.5488 | 27.2104 | 855.6738 | 145.2096 | 178.1814 | 212.3942 | 242.5804 | 277.0617 | 1.942%
10143 | 27-57 | -56.8201 | 27.2104 | 850.4891 | 146.8085 | 179.2249 | 213.7745 | 244.2747 | 279.1314 | 2.027%
10144 | 27-57 | -57.0914 | 27.2104 | 845.6314 | 148.3968 | 180.2505 | 215.1111 | 245.9 | 281.1008 | 2.115%
10145 | 27-57.5 | -57.3628 | 27.2104 | 841.1064 | 150.0551 | 181.312 | 216.5052 | 247.6038 | 283.1743 | 2.21%
10146 | 27-57.5 | -57.6341 | 27.2104 | 836.9194 | 151.7615 | 182.3924 | 217.926 | 249.3416 | 285.2911 | 2.312%
10147 | 27-58 | -57.9054 | 27.2104 | 833.0756 | 153.4117 | 183.4207 | 219.2601 | 250.9594 | 287.2466 | 2.415%
10148 | 27-58 | -58.1767 | 27.2104 | 829.5798 | 155.1177 | 184.4945 | 220.6699 | 252.6823 | 289.3437 | 2.526%
10149 | 27-58.5 | -58.448 | 27.2104 | 826.4363 | 156.8177 | 185.5782 | 222.0915 | 254.4186 | 291.4559 | 2.641%
10150 | 27-58.5 | -58.7194 | 27.2104 | 823.6493 | 158.3966 | 186.5844 | 223.3828 | 255.9731 | 293.3227 | 2.752%
10151 | 27-59 | -58.9907 | 27.2104 | 821.2224 | 159.9615 | 187.6212 | 224.7294 | 257.6071 | 295.2991 | 2.868%
10152 | 27-59.5 | -59.262 | 27.2104 | 819.1587 | 161.4583 | 188.642 | 226.0523 | 259.2101 | 297.2357 | 2.983%
10153 | 27-59.5 | -59.5333 | 27.2104 | 817.461 | 162.8164 | 189.5641 | 227.2187 | 260.6006 | 298.8906 | 3.092%
10154 | 27-60 | -59.8046 | 27.2104 | 816.1317 | 164.1316 | 190.4843 | 228.3952 | 262.0134 | 300.5832 | 3.201%
10155 | 27-60 | -60.076 | 27.2104 | 815.1724 | 165.358 | 191.3701 | 229.5274 | 263.3727 | 302.2114 | 3.306%
10156 | 27-60.5 | -60.3473 | 27.2104 | 814.5847 | 166.4535 | 192.1784 | 230.5431 | 264.5777 | 303.6393 | 3.404%
10157 | 27-60.5 | -60.6186 | 27.2104 | 814.3691 | 167.4809 | 192.9794 | 231.5603 | 265.7936 | 305.0898 | 3.498%
10158 | 27-61 | -60.8899 | 27.2104 | 814.5261 | 168.391 | 193.7411 | 232.5287 | 266.9519 | 306.4726 | 3.584%
10159 | 27-61 | -61.1613 | 27.2104 | 815.0554 | 169.162 | 194.4446 | 233.4158 | 268.0072 | 307.726 | 3.66%
10160 | 27-61.5 | -61.4326 | 27.2104 | 815.9564 | 169.8859 | 195.1738 | 234.3524 | 269.1355 | 309.0822 | 3.733%
10161 | 27-61.5 | -61.7039 | 27.2104 | 817.2276 | 170.5302 | 195.8903 | 235.279 | 270.2572 | 310.4366 | 3.799%
10162 | 27-62 | -61.9752 | 27.2104 | 818.8676 | 171.111 | 196.5927 | 236.1937 | 271.3698 | 311.7857 | 3.86%
10163 | 27-62 | -62.2465 | 27.2104 | 820.8739 | 171.739 | 197.3864 | 237.2622 | 272.6978 | 313.4273 | 3.924%
10164 | 27-62.5 | -62.5179 | 27.2104 | 823.244 | 172.3779 | 198.1989 | 238.3637 | 274.073 | 315.1338 | 3.989%
10165 | 27-63 | -62.7892 | 27.2104 | 825.9746 | 173.0229 | 199.02 | 239.4782 | 275.4652 | 316.8626 | 4.056%
10166 | 27-63 | -63.0605 | 27.2104 | 829.0623 | 173.7444 | 199.9551 | 240.7712 | 277.0991 | 318.911 | 4.129%
10167 | 27-63.5 | -63.3318 | 27.2104 | 832.5031 | 174.4789 | 200.9039 | 242.0789 | 278.7482 | 320.9751 | 4.204%
10168 | 27-63.5 | -63.6031 | 27.2104 | 836.2925 | 175.2075 | 201.8373 | 243.3541 | 280.3477 | 322.968 | 4.28%
10169 | 27-64 | -63.8745 | 27.2104 | 840.4258 | 175.9748 | 202.8234 | 244.7057 | 282.0464 | 325.0879 | 4.361%
10170 | 27-64 | -64.1458 | 27.2104 | 844.8981 | 176.7184 | 203.7679 | 245.9841 | 283.6406 | 327.0642 | 4.441%
10171 | 27-64.5 | -64.4171 | 27.2104 | 849.7039 | 177.4305 | 204.6593 | 247.172 | 285.1076 | 328.8674 | 4.52%
10172 | 27-64.5 | -64.6884 | 27.2104 | 854.8375 | 178.1475 | 205.5515 | 248.3532 | 286.5601 | 330.6462 | 4.601%
10173 | 27-65 | -64.9598 | 27.2104 | 860.2932 | 178.8228 | 206.3761 | 249.4214 | 287.8551 | 332.2123 | 4.68%
10174 | 27-65 | -65.2311 | 27.2104 | 866.0648 | 179.4665 | 207.1494 | 250.4046 | 289.032 | 333.6191 | 4.757%
10175 | 27-65.5 | -65.5024 | 27.2104 | 872.1459 | 180.1118 | 207.9216 | 251.3818 | 290.198 | 335.0089 | 4.837%
10176 | 27-66 | -65.7737 | 27.2104 | 878.5303 | 180.6917 | 208.5938 | 252.1987 | 291.1449 | 336.1064 | 4.912%
10177 | 27-66 | -66.045 | 27.2104 | 885.2112 | 181.2316 | 209.2083 | 252.9277 | 291.9743 | 337.0498 | 4.985%
10178 | 27-66.5 | -66.3164 | 27.2104 | 892.182 | 181.773 | 209.8296 | 253.6731 | 292.8296 | 338.0313 | 5.057%
10179 | 27-66.5 | -66.5877 | 27.2104 | 899.436 | 182.229 | 210.3364 | 254.2545 | 293.4734 | 338.7428 | 5.122%
10180 | 27-67 | -66.859 | 27.2104 | 906.9663 | 182.6452 | 210.7986 | 254.784 | 294.0591 | 339.3893 | 5.182%
10181 | 27-67 | -67.1303 | 27.2104 | 914.766 | 183.0679 | 211.2845 | 255.3681 | 294.7304 | 340.1609 | 5.241%
10182 | 27-67.5 | -67.4016 | 27.2104 | 922.8284 | 183.4231 | 211.6879 | 255.8453 | 295.272 | 340.7753 | 5.291%
10183 | 27-67.5 | -67.673 | 27.2104 | 931.1466 | 183.7661 | 212.0884 | 256.3365 | 295.8452 | 341.4442 | 5.338%
10184 | 27-68 | -67.9443 | 27.2104 | 939.7137 | 184.1344 | 212.5383 | 256.9202 | 296.5537 | 342.3023 | 5.386%
10185 | 27-68 | -68.2156 | 27.2104 | 948.523 | 184.4529 | 212.9276 | 257.4254 | 297.167 | 343.0449 | 5.427%
10186 | 27-68.5 | -68.4869 | 27.2104 | 957.5678 | 184.7645 | 213.3152 | 257.9386 | 297.7985 | 343.8189 | 5.466%
10187 | 27-69 | -68.7583 | 27.2104 | 966.8414 | 185.0915 | 213.7313 | 258.5032 | 298.5041 | 344.6956 | 5.506%
10188 | 27-69 | -69.0296 | 27.2104 | 976.3373 | 185.3321 | 214.0329 | 258.9062 | 299.0028 | 345.31 | 5.537%
10189 | 27-69.5 | -69.3009 | 27.2104 | 986.0491 | 185.5515 | 214.3152 | 259.2941 | 299.4913 | 345.9211 | 5.563%
10190 | 27-69.5 | -69.5722 | 27.2104 | 995.9703 | 185.7756 | 214.6153 | 259.7231 | 300.0444 | 346.6266 | 5.588%
10191 | 27-70 | -69.8435 | 27.2104 | 1006.0949 | 185.8862 | 214.763 | 259.934 | 300.3163 | 346.9733 | 5.6%
10192 | 27-70 | -70.1149 | 27.2104 | 1016.4166 | 185.9721 | 214.88 | 260.104 | 300.5375 | 347.2576 | 5.609%
10193 | 27-70.5 | -70.3862 | 27.2104 | 1026.9294 | 186.0542 | 214.9935 | 260.2712 | 300.7569 | 347.5413 | 5.617%
10194 | 27-70.5 | -70.6575 | 27.2104 | 1037.6277 | 186.0471 | 214.9765 | 260.2365 | 300.7045 | 347.4668 | 5.618%
10195 | 27-71 | -70.9288 | 27.2104 | 1048.5056 | 186.0287 | 214.9382 | 260.1632 | 300.5963 | 347.3147 | 5.618%
10196 | 27-71 | -71.2001 | 27.2104 | 1059.5575 | 186.0084 | 214.8913 | 260.069 | 300.4549 | 347.1139 | 5.62%
10197 | 27-71.5 | -71.4715 | 27.2104 | 1070.7781 | 185.9305 | 214.7585 | 259.84 | 300.131 | 346.6712 | 5.616%
10198 | 27-71.5 | -71.7428 | 27.2104 | 1082.1621 | 185.8703 | 214.6492 | 259.6445 | 299.8499 | 346.2831 | 5.615%
10199 | 27-72 | -72.0141 | 27.2104 | 1093.7043 | 185.8266 | 214.561 | 259.4774 | 299.6046 | 345.9392 | 5.616%
10200 | 27-72.5 | -72.2854 | 27.2104 | 1105.3998 | 185.732 | 214.3975 | 259.1932 | 299.2009 | 345.3862 | 5.612%
10201 | 27-72.5 | -72.5568 | 27.2104 | 1117.2437 | 185.6865 | 214.2976 | 258.9969 | 298.9086 | 344.9732 | 5.614%
10202 | 27-73 | -72.8281 | 27.2104 | 1129.2312 | 185.6725 | 214.2355 | 258.8488 | 298.6741 | 344.6292 | 5.621%
10203 | 27-73 | -73.0994 | 27.2104 | 1141.3579 | 185.6101 | 214.0959 | 258.5721 | 298.2606 | 344.0434 | 5.625%
10204 | 27-73.5 | -73.3707 | 27.2104 | 1153.6193 | 185.6165 | 214.0489 | 258.4286 | 298.0193 | 343.6778 | 5.636%
10205 | 27-73.5 | -73.642 | 27.2104 | 1166.0111 | 185.6591 | 214.0518 | 258.3582 | 297.8735 | 343.435 | 5.651%
10206 | 27-74 | -73.9134 | 27.2104 | 1178.5292 | 185.6574 | 213.9913 | 258.1917 | 297.6 | 343.0255 | 5.662%
10207 | 27-74 | -74.1847 | 27.2104 | 1191.1696 | 185.6965 | 213.9942 | 258.128 | 297.4678 | 342.8055 | 5.676%
10208 | 27-74.5 | -74.456 | 27.2104 | 1203.9283 | 185.7428 | 214.0129 | 258.0951 | 297.3817 | 342.6505 | 5.69%
10209 | 27-74.5 | -74.7273 | 27.2104 | 1216.8015 | 185.735 | 213.9592 | 257.9591 | 297.1628 | 342.3267 | 5.698%
10210 | 27-75 | -74.9986 | 27.2104 | 1229.7858 | 185.7283 | 213.9088 | 257.8302 | 296.955 | 342.0191 | 5.705%
10211 | 27-75.5 | -75.27 | 27.2104 | 1242.8775 | 185.6879 | 213.8159 | 257.6445 | 296.6769 | 341.6248 | 5.708%
10212 | 27-75.5 | -75.5413 | 27.2104 | 1256.0732 | 185.5622 | 213.6163 | 257.3164 | 296.2228 | 341.0139 | 5.7%
10213 | 27-76 | -75.8126 | 27.2104 | 1269.3697 | 185.4155 | 213.4024 | 256.9871 | 295.7811 | 340.4333 | 5.687%
10214 | 27-76 | -76.0839 | 27.2104 | 1282.7638 | 185.2094 | 213.1228 | 256.5827 | 295.2564 | 339.761 | 5.664%
10215 | 27-76.5 | -76.3553 | 27.2104 | 1296.2524 | 184.9098 | 212.732 | 256.0381 | 294.565 | 338.8904 | 5.628%
10216 | 27-76.5 | -76.6266 | 27.2104 | 1309.8326 | 184.5915 | 212.3385 | 255.5209 | 293.9316 | 338.1174 | 5.586%
10217 | 27-77 | -76.8979 | 27.2104 | 1323.5014 | 184.2172 | 211.8857 | 254.9403 | 293.2325 | 337.2769 | 5.534%
10218 | 27-77 | -77.1692 | 27.2104 | 1337.2562 | 183.7731 | 211.3503 | 254.2566 | 292.4116 | 336.2927 | 5.473%
10219 | 27-77.5 | -77.4405 | 27.2104 | 1351.0943 | 183.3391 | 210.848 | 253.6474 | 291.7065 | 335.4767 | 5.41%
10220 | 27-77.5 | -77.7119 | 27.2104 | 1365.013 | 182.8631 | 210.2997 | 252.9863 | 290.9449 | 334.5992 | 5.341%
10221 | 27-78 | -77.9832 | 27.2104 | 1379.01 | 182.3266 | 209.6751 | 252.2229 | 290.0564 | 333.5652 | 5.265%
10222 | 27-78.5 | -78.2545 | 27.2104 | 1393.0828 | 181.793 | 209.0701 | 251.5087 | 289.247 | 332.6482 | 5.187%
10223 | 27-78.5 | -78.5258 | 27.2104 | 1407.229 | 180.9922 | 208.1287 | 250.3438 | 287.8792 | 331.0429 | 5.078%
10224 | 27-79 | -78.7971 | 27.2104 | 1421.4465 | 179.7137 | 206.6252 | 248.4138 | 285.555 | 328.2506 | 4.915%
10225 | 27-79 | -79.0685 | 27.2104 | 1435.7332 | 177.7526 | 204.6441 | 245.8478 | 282.4471 | 324.4984 | 4.678%
10226 | 27-79.5 | -79.3398 | 27.2104 | 1450.0868 | 175.4704 | 202.4504 | 242.9876 | 278.9684 | 320.2827 | 4.415%
10227 | 27-79.5 | -79.6111 | 27.2104 | 1464.5054 | 173.134 | 200.2519 | 240.1071 | 275.4536 | 316.0113 | 4.16%
10228 | 27-80 | -79.8824 | 27.2104 | 1478.987 | 170.8041 | 198.1185 | 237.3155 | 272.0504 | 311.8785 | 3.916%
10229 | 27-80 | -80.1537 | 27.2104 | 1493.5298 | 168.4565 | 195.9904 | 234.5176 | 268.6289 | 307.7123 | 3.683%
10230 | 27-80.5 | -80.4251 | 27.2104 | 1508.132 | 166.1052 | 193.8905 | 231.7512 | 265.2414 | 303.5827 | 3.461%
10231 | 27-80.5 | -80.6964 | 27.2104 | 1522.7917 | 163.7893 | 191.8563 | 229.1145 | 262.0246 | 299.6738 | 3.251%
10232 | 27-81 | -80.9677 | 27.2104 | 1537.5074 | 161.8842 | 190.1524 | 226.8778 | 259.2911 | 296.3465 | 3.086%
10233 | 27-81 | -81.239 | 27.2104 | 1552.2773 | 160.6274 | 188.9338 | 225.2982 | 257.3762 | 294.0313 | 2.979%
10234 | 27-81.5 | -81.5104 | 27.2104 | 1567.0999 | 160.0341 | 188.285 | 224.5173 | 256.4778 | 292.9979 | 2.926%
10235 | 27-82 | -81.7817 | 27.2104 | 1581.9737 | 159.5589 | 187.7678 | 223.9156 | 255.8037 | 292.2432 | 2.883%
10236 | 27-82 | -82.053 | 27.2104 | 1596.8972 | 159.3553 | 187.6142 | 223.8245 | 255.7804 | 292.3102 | 2.863%
10237 | 27-82.5 | -82.3243 | 27.2104 | 1611.8689 | 159.6721 | 188.0985 | 224.6322 | 256.9044 | 293.8264 | 2.885%
10238 | 27-82.5 | -82.5956 | 27.2104 | 1626.8875 | 160.7006 | 189.1093 | 226.1524 | 258.9155 | 296.4395 | 2.961%
10239 | 27-83 | -82.867 | 27.2104 | 1641.9516 | 162.0693 | 190.3655 | 228.0213 | 261.3734 | 299.619 | 3.064%
10240 | 27-83 | -83.1383 | 27.2104 | 1657.06 | 163.5549 | 191.7174 | 230.055 | 264.0648 | 303.1176 | 3.177%
10241 | 27-83.5 | -83.4096 | 27.2104 | 1672.2114 | 165.0823 | 193.0494 | 232.0382 | 266.6747 | 306.4955 | 3.296%
10242 | 27-83.5 | -83.6809 | 27.2104 | 1687.4047 | 166.6712 | 194.4088 | 234.0443 | 269.3021 | 309.8832 | 3.423%
10243 | 27-84 | -83.9522 | 27.2104 | 1702.6385 | 168.3489 | 195.8299 | 236.1274 | 272.0205 | 313.3786 | 3.56%
10244 | 27-84 | -84.2236 | 27.2104 | 1717.9118 | 170.0612 | 197.2554 | 238.1526 | 274.64 | 316.7233 | 3.707%
10245 | 27-84.5 | -84.4949 | 27.2104 | 1733.2236 | 171.4328 | 198.4203 | 239.851 | 276.8508 | 319.5612 | 3.825%
10246 | 27-85 | -84.7662 | 27.2104 | 1748.5727 | 172.2817 | 199.2552 | 241.1062 | 278.5132 | 321.7255 | 3.896%
10247 | 27-85 | -85.0375 | 27.2104 | 1763.9581 | 172.5384 | 199.6049 | 241.6681 | 279.2833 | 322.7545 | 3.916%
10248 | 27-85.5 | -85.3089 | 27.2104 | 1779.3789 | 172.7459 | 199.9013 | 242.1437 | 279.9346 | 323.6246 | 3.931%
10249 | 27-85.5 | -85.5802 | 27.2104 | 1794.834 | 173.0183 | 200.2653 | 242.6979 | 280.6742 | 324.5936 | 3.954%
10250 | 27-86 | -85.8515 | 27.2104 | 1810.3226 | 173.2655 | 200.5565 | 243.0942 | 281.1704 | 325.2112 | 3.978%
10251 | 27-86 | -86.1228 | 27.2104 | 1825.8437 | 173.5632 | 200.8783 | 243.4904 | 281.6341 | 325.7539 | 4.01%
10252 | 27-86.5 | -86.3941 | 27.2104 | 1841.3965 | 173.9174 | 201.239 | 243.8939 | 282.0716 | 326.2263 | 4.05%
10253 | 27-86.5 | -86.6655 | 27.2104 | 1856.9802 | 174.2266 | 201.5168 | 244.143 | 282.2834 | 326.3834 | 4.09%
10254 | 27-87 | -86.9368 | 27.2104 | 1872.5938 | 174.5586 | 201.8304 | 244.4499 | 282.5748 | 326.6475 | 4.131%
10255 | 27-87 | -87.2081 | 27.2104 | 1888.2366 | 174.9038 | 202.1721 | 244.806 | 282.9364 | 327.0082 | 4.174%
10256 | 27-87.5 | -87.4794 | 27.2104 | 1903.9079 | 175.1488 | 202.4007 | 245.0166 | 283.1222 | 327.1568 | 4.206%
10257 | 27-88 | -87.7507 | 27.2104 | 1919.6069 | 175.3465 | 202.594 | 245.2104 | 283.3114 | 327.3355 | 4.231%
10258 | 27-88 | -88.0221 | 27.2104 | 1935.3328 | 175.4748 | 202.721 | 245.3403 | 283.4409 | 327.4616 | 4.247%
10259 | 27-88.5 | -88.2934 | 27.2104 | 1951.085 | 175.4437 | 202.6598 | 245.2259 | 283.2737 | 327.228 | 4.247%
10260 | 27-88.5 | -88.5647 | 27.2104 | 1966.8628 | 175.3562 | 202.5567 | 245.0983 | 283.1241 | 327.0529 | 4.237%
10261 | 27-89 | -88.836 | 27.2104 | 1982.6655 | 175.1967 | 202.3881 | 244.9199 | 282.9409 | 326.8682 | 4.216%
10262 | 27-89 | -89.1074 | 27.2104 | 1998.4925 | 174.9064 | 202.067 | 244.5547 | 282.54 | 326.4298 | 4.181%
10263 | 27-89.5 | -89.3787 | 27.2104 | 2014.3431 | 174.5689 | 201.7252 | 244.2188 | 282.2205 | 326.1406 | 4.138%
10264 | 27-89.5 | -89.65 | 27.2104 | 2030.2167 | 174.1647 | 201.3342 | 243.8679 | 281.9229 | 325.9221 | 4.084%
10265 | 27-90 | -89.9213 | 27.2104 | 2046.1129 | 173.6503 | 200.8349 | 243.4053 | 281.5127 | 325.5924 | 4.018%
10266 | 27-90 | -90.1926 | 27.2104 | 2062.0309 | 173.1215 | 200.342 | 242.9743 | 281.16 | 325.3531 | 3.951%
10267 | 27-90.5 | -90.464 | 27.2104 | 2077.9702 | 172.549 | 199.8104 | 242.5036 | 280.7674 | 325.0748 | 3.88%
10268 | 27-90.5 | -90.7353 | 27.2104 | 2093.9303 | 171.8813 | 199.1714 | 241.8819 | 280.1819 | 324.5518 | 3.803%
10269 | 27-50 | -50.0371 | 27.4817 | 1075.3047 | 111.1526 | 144.8033 | 183.6791 | 207.7326 | 234.937 | 0.7286%
10270 | 27-50.5 | -50.3084 | 27.4817 | 1064.395 | 112.6228 | 146.908 | 185.0107 | 209.3163 | 236.816 | 0.7624%
10271 | 27-50.5 | -50.5797 | 27.4817 | 1053.659 | 114.1184 | 149.0449 | 186.3433 | 210.8886 | 238.6681 | 0.7983%
10272 | 27-51 | -50.851 | 27.4817 | 1043.1021 | 115.6483 | 151.217 | 187.6931 | 212.4872 | 240.5575 | 0.837%
10273 | 27-51 | -51.1224 | 27.4817 | 1032.73 | 117.244 | 153.4253 | 189.1069 | 214.1867 | 242.5935 | 0.8793%
10274 | 27-51.5 | -51.3937 | 27.4817 | 1022.5482 | 118.8103 | 155.5359 | 190.4554 | 215.796 | 244.5091 | 0.9226%
10275 | 27-51.5 | -51.665 | 27.4817 | 1012.5626 | 120.3644 | 157.5576 | 191.7679 | 217.3607 | 246.37 | 0.9672%
10276 | 27-52 | -51.9363 | 27.4817 | 1002.7789 | 121.9324 | 159.5085 | 193.0874 | 218.9445 | 248.2652 | 1.014%
10277 | 27-52 | -52.2077 | 27.4817 | 993.2033 | 123.4375 | 161.3141 | 194.3058 | 220.3835 | 249.9622 | 1.061%
10278 | 27-52.5 | -52.479 | 27.4817 | 983.8418 | 124.903 | 162.9949 | 195.4657 | 221.7511 | 251.5726 | 1.108%
10279 | 27-53 | -52.7503 | 27.4817 | 974.7006 | 126.345 | 164.5515 | 196.6014 | 223.1046 | 253.1821 | 1.156%
10280 | 27-53 | -53.0216 | 27.4817 | 965.786 | 127.6929 | 165.9117 | 197.6218 | 224.3074 | 254.5982 | 1.202%
10281 | 27-53.5 | -53.2929 | 27.4817 | 957.1044 | 129.0047 | 167.1459 | 198.6153 | 225.4919 | 256.0072 | 1.248%
10282 | 27-53.5 | -53.5643 | 27.4817 | 948.6622 | 130.3057 | 168.2673 | 199.6201 | 226.7117 | 257.4821 | 1.295%
10283 | 27-54 | -53.8356 | 27.4817 | 940.4658 | 131.5351 | 169.2061 | 200.5457 | 227.8257 | 258.8187 | 1.34%
10284 | 27-54 | -54.1069 | 27.4817 | 932.5218 | 132.7954 | 170.0983 | 201.5224 | 229.0136 | 260.2573 | 1.387%
10285 | 27-54.5 | -54.3782 | 27.4817 | 924.8367 | 134.1192 | 170.9714 | 202.5895 | 230.3263 | 261.8631 | 1.438%
10286 | 27-54.5 | -54.6495 | 27.4817 | 917.417 | 135.3886 | 171.7551 | 203.5891 | 231.5376 | 263.3256 | 1.488%
10287 | 27-55 | -54.9209 | 27.4817 | 910.2692 | 136.7183 | 172.5798 | 204.6764 | 232.869 | 264.948 | 1.542%
10288 | 27-55 | -55.1922 | 27.4817 | 903.3998 | 138.1324 | 173.4769 | 205.8789 | 234.3569 | 266.7776 | 1.603%
10289 | 27-55.5 | -55.4635 | 27.4817 | 896.8153 | 139.5068 | 174.3523 | 207.0269 | 235.7577 | 268.4797 | 1.664%
10290 | 27-55.5 | -55.7348 | 27.4817 | 890.522 | 140.939 | 175.2763 | 208.2539 | 237.2671 | 270.3263 | 1.73%
10291 | 27-56 | -56.0061 | 27.4817 | 884.526 | 142.4405 | 176.2564 | 209.5678 | 238.893 | 272.3258 | 1.802%
10292 | 27-56.5 | -56.2775 | 27.4817 | 878.8336 | 143.9074 | 177.2112 | 210.8211 | 240.4234 | 274.1864 | 1.875%
10293 | 27-56.5 | -56.5488 | 27.4817 | 873.4506 | 145.4274 | 178.2 | 212.1254 | 242.0211 | 276.1341 | 1.954%
10294 | 27-57 | -56.8201 | 27.4817 | 868.3829 | 147.0013 | 179.222 | 213.4764 | 243.6786 | 278.1576 | 2.039%
10295 | 27-57 | -57.0914 | 27.4817 | 863.636 | 148.5552 | 180.2207 | 214.7761 | 245.2571 | 280.0678 | 2.126%
10296 | 27-57.5 | -57.3628 | 27.4817 | 859.2152 | 150.1684 | 181.2494 | 216.1274 | 246.9086 | 282.0775 | 2.22%
10297 | 27-57.5 | -57.6341 | 27.4817 | 855.1256 | 151.8214 | 182.2932 | 217.5033 | 248.5938 | 284.1324 | 2.319%
10298 | 27-58 | -57.9054 | 27.4817 | 851.372 | 153.4175 | 183.2857 | 218.7971 | 250.1676 | 286.0398 | 2.42%
10299 | 27-58 | -58.1767 | 27.4817 | 847.9588 | 155.0758 | 184.3259 | 220.1732 | 251.8573 | 288.1049 | 2.528%
10300 | 27-58.5 | -58.448 | 27.4817 | 844.8903 | 156.7362 | 185.38 | 221.5697 | 253.5737 | 290.2045 | 2.64%
10301 | 27-58.5 | -58.7194 | 27.4817 | 842.1701 | 158.2821 | 186.3634 | 222.8481 | 255.1257 | 292.0824 | 2.75%
10302 | 27-59 | -58.9907 | 27.4817 | 839.8017 | 159.8214 | 187.3857 | 224.1933 | 256.7721 | 294.0889 | 2.864%
10303 | 27-59.5 | -59.262 | 27.4817 | 837.7881 | 161.2991 | 188.3986 | 225.5237 | 258.3983 | 296.0688 | 2.977%
10304 | 27-59.5 | -59.5333 | 27.4817 | 836.1318 | 162.6429 | 189.3162 | 226.7009 | 259.8151 | 297.7698 | 3.085%
10305 | 27-60 | -59.8046 | 27.4817 | 834.8349 | 163.9517 | 190.2376 | 227.8957 | 261.2635 | 299.52 | 3.193%
10306 | 27-60 | -60.076 | 27.4817 | 833.8992 | 165.177 | 191.1276 | 229.0494 | 262.6615 | 301.2088 | 3.297%
10307 | 27-60.5 | -60.3473 | 27.4817 | 833.3258 | 166.2746 | 191.9395 | 230.0836 | 263.9002 | 302.6893 | 3.395%
10308 | 27-60.5 | -60.6186 | 27.4817 | 833.1156 | 167.3091 | 192.7451 | 231.1196 | 265.1492 | 304.1911 | 3.489%
10309 | 27-61 | -60.8899 | 27.4817 | 833.2687 | 168.231 | 193.5122 | 232.1064 | 266.339 | 305.6218 | 3.575%
10310 | 27-61 | -61.1613 | 27.4817 | 833.7851 | 169.0173 | 194.2209 | 233.0094 | 267.4208 | 306.9153 | 3.652%
10311 | 27-61.5 | -61.4326 | 27.4817 | 834.6639 | 169.7534 | 194.9511 | 233.9536 | 268.5633 | 308.2939 | 3.726%
10312 | 27-61.5 | -61.7039 | 27.4817 | 835.9041 | 170.4032 | 195.6666 | 234.8827 | 269.6911 | 309.6588 | 3.792%
10313 | 27-62 | -61.9752 | 27.4817 | 837.504 | 170.9835 | 196.3673 | 235.7975 | 270.8055 | 311.0121 | 3.853%
10314 | 27-62 | -62.2465 | 27.4817 | 839.4617 | 171.6073 | 197.1564 | 236.8608 | 272.1278 | 312.6472 | 3.916%
10315 | 27-62.5 | -62.5179 | 27.4817 | 841.7745 | 172.2403 | 197.9611 | 237.9513 | 273.4887 | 314.3353 | 3.981%
10316 | 27-63 | -62.7892 | 27.4817 | 844.4396 | 172.8791 | 198.7732 | 239.0516 | 274.8618 | 316.0387 | 4.047%
10317 | 27-63 | -63.0605 | 27.4817 | 847.4537 | 173.5964 | 199.7017 | 240.3339 | 276.4808 | 318.067 | 4.12%
10318 | 27-63.5 | -63.3318 | 27.4817 | 850.8129 | 174.3279 | 200.6454 | 241.6326 | 278.117 | 320.1134 | 4.195%
10319 | 27-63.5 | -63.6031 | 27.4817 | 854.5133 | 175.0557 | 201.5767 | 242.9034 | 279.7098 | 322.0966 | 4.272%
10320 | 27-64 | -63.8745 | 27.4817 | 858.5504 | 175.8268 | 202.5676 | 244.2616 | 281.4167 | 324.2264 | 4.353%
10321 | 27-64 | -64.1458 | 27.4817 | 862.9195 | 176.578 | 203.5213 | 245.5518 | 283.025 | 326.2196 | 4.434%
10322 | 27-64.5 | -64.4171 | 27.4817 | 867.6155 | 177.3002 | 204.4243 | 246.7534 | 284.5074 | 328.0401 | 4.514%
10323 | 27-64.5 | -64.6884 | 27.4817 | 872.6332 | 178.0298 | 205.3305 | 247.9506 | 285.9774 | 329.838 | 4.597%
10324 | 27-65 | -64.9598 | 27.4817 | 877.967 | 178.7191 | 206.1705 | 249.0364 | 287.2917 | 331.4251 | 4.678%
10325 | 27-65 | -65.2311 | 27.4817 | 883.6112 | 179.3762 | 206.9582 | 250.035 | 288.4847 | 332.8484 | 4.758%
10326 | 27-65.5 | -65.5024 | 27.4817 | 889.5598 | 180.0326 | 207.7411 | 251.0215 | 289.6584 | 334.2436 | 4.839%
10327 | 27-66 | -65.7737 | 27.4817 | 895.8068 | 180.6226 | 208.423 | 251.8473 | 290.6128 | 335.3465 | 4.916%
10328 | 27-66 | -66.045 | 27.4817 | 902.346 | 181.1724 | 209.048 | 252.5872 | 291.4534 | 336.3012 | 4.991%
10329 | 27-66.5 | -66.3164 | 27.4817 | 909.171 | 181.7232 | 209.6804 | 253.3464 | 292.325 | 337.3018 | 5.065%
10330 | 27-66.5 | -66.5877 | 27.4817 | 916.2754 | 182.1894 | 210.1998 | 253.9442 | 292.9886 | 338.0374 | 5.131%
10331 | 27-67 | -66.859 | 27.4817 | 923.6528 | 182.6179 | 210.6775 | 254.4946 | 293.6004 | 338.7162 | 5.193%
10332 | 27-67 | -67.1303 | 27.4817 | 931.2967 | 183.0555 | 211.1828 | 255.1056 | 294.3056 | 339.5302 | 5.253%
10333 | 27-67.5 | -67.4016 | 27.4817 | 939.2004 | 183.4231 | 211.6012 | 255.6019 | 294.8702 | 340.1724 | 5.306%
10334 | 27-67.5 | -67.673 | 27.4817 | 947.3576 | 183.7761 | 212.0134 | 256.1078 | 295.4607 | 340.8615 | 5.355%
10335 | 27-68 | -67.9443 | 27.4817 | 955.7616 | 184.1528 | 212.4735 | 256.7045 | 296.1849 | 341.7383 | 5.403%
10336 | 27-68 | -68.2156 | 27.4817 | 964.4061 | 184.4798 | 212.8737 | 257.2245 | 296.8167 | 342.504 | 5.446%
10337 | 27-68.5 | -68.4869 | 27.4817 | 973.2844 | 184.8015 | 213.2743 | 257.7557 | 297.4708 | 343.3062 | 5.487%
10338 | 27-69 | -68.7583 | 27.4817 | 982.3904 | 185.141 | 213.7064 | 258.3421 | 298.2037 | 344.2168 | 5.528%
10339 | 27-69 | -69.0296 | 27.4817 | 991.7177 | 185.3964 | 214.0272 | 258.7717 | 298.7359 | 344.8733 | 5.56%
10340 | 27-69.5 | -69.3009 | 27.4817 | 1001.2601 | 185.6314 | 214.3291 | 259.1855 | 299.2563 | 345.5233 | 5.589%
10341 | 27-69.5 | -69.5722 | 27.4817 | 1011.0115 | 185.8716 | 214.6478 | 259.6372 | 299.8359 | 346.2596 | 5.616%
10342 | 27-70 | -69.8435 | 27.4817 | 1020.9658 | 185.9979 | 214.8122 | 259.8658 | 300.1259 | 346.6246 | 5.631%
10343 | 27-70 | -70.1149 | 27.4817 | 1031.1171 | 186.0978 | 214.9428 | 260.0482 | 300.3579 | 346.9172 | 5.643%
10344 | 27-70.5 | -70.3862 | 27.4817 | 1041.4597 | 186.1915 | 215.0664 | 260.2222 | 300.5804 | 347.199 | 5.653%
10345 | 27-70.5 | -70.6575 | 27.4817 | 1051.9879 | 186.1919 | 215.0541 | 260.187 | 300.522 | 347.1111 | 5.656%
10346 | 27-71 | -70.9288 | 27.4817 | 1062.6961 | 186.182 | 215.023 | 260.118 | 300.4149 | 346.9561 | 5.658%
10347 | 27-71 | -71.2001 | 27.4817 | 1073.5789 | 186.1718 | 214.9863 | 260.0338 | 300.2831 | 346.7639 | 5.661%
10348 | 27-71.5 | -71.4715 | 27.4817 | 1084.631 | 186.103 | 214.8632 | 259.8154 | 299.9703 | 346.3329 | 5.659%
10349 | 27-71.5 | -71.7428 | 27.4817 | 1095.8473 | 186.0498 | 214.7614 | 259.6279 | 299.6978 | 345.9537 | 5.659%
10350 | 27-72 | -72.0141 | 27.4817 | 1107.2227 | 186.0106 | 214.6777 | 259.4654 | 299.4568 | 345.614 | 5.661%
10351 | 27-72.5 | -72.2854 | 27.4817 | 1118.7524 | 185.9156 | 214.5118 | 259.1752 | 299.0437 | 345.0472 | 5.658%
10352 | 27-72.5 | -72.5568 | 27.4817 | 1130.4316 | 185.8649 | 214.4021 | 258.9613 | 298.7259 | 344.5988 | 5.66%
10353 | 27-73 | -72.8281 | 27.4817 | 1142.2557 | 185.8416 | 214.3243 | 258.7861 | 298.4532 | 344.2029 | 5.666%
10354 | 27-73 | -73.0994 | 27.4817 | 1154.2201 | 185.7685 | 214.1686 | 258.484 | 298.0054 | 343.5717 | 5.669%
10355 | 27-73.5 | -73.3707 | 27.4817 | 1166.3206 | 185.7635 | 214.1062 | 258.3184 | 297.7356 | 343.1697 | 5.68%
10356 | 27-73.5 | -73.642 | 27.4817 | 1178.5529 | 185.7933 | 214.0933 | 258.2275 | 297.5651 | 342.8974 | 5.693%
10357 | 27-74 | -73.9134 | 27.4817 | 1190.9129 | 185.7755 | 214.0142 | 258.0385 | 297.2655 | 342.458 | 5.702%
10358 | 27-74 | -74.1847 | 27.4817 | 1203.3966 | 185.7966 | 213.9966 | 257.9504 | 297.1058 | 342.2068 | 5.714%
10359 | 27-74.5 | -74.456 | 27.4817 | 1216.0002 | 185.8223 | 213.9924 | 257.8915 | 296.9911 | 342.0208 | 5.724%
10360 | 27-74.5 | -74.7273 | 27.4817 | 1228.7199 | 185.7905 | 213.9136 | 257.7294 | 296.746 | 341.6711 | 5.728%
10361 | 27-75 | -74.9986 | 27.4817 | 1241.5523 | 185.7588 | 213.8392 | 257.5795 | 296.5208 | 341.3514 | 5.731%
10362 | 27-75.5 | -75.27 | 27.4817 | 1254.4936 | 185.692 | 213.7225 | 257.3754 | 296.2306 | 340.9536 | 5.728%
10363 | 27-75.5 | -75.5413 | 27.4817 | 1267.5406 | 185.5391 | 213.4986 | 257.0295 | 295.7659 | 340.3421 | 5.715%
10364 | 27-76 | -75.8126 | 27.4817 | 1280.6901 | 185.3666 | 213.2639 | 256.6893 | 295.3241 | 339.7757 | 5.696%
10365 | 27-76 | -76.0839 | 27.4817 | 1293.9387 | 185.1355 | 212.9664 | 256.2804 | 294.8093 | 339.132 | 5.667%
10366 | 27-76.5 | -76.3553 | 27.4817 | 1307.2836 | 184.8108 | 212.5585 | 255.7345 | 294.133 | 338.2983 | 5.625%
10367 | 27-76.5 | -76.6266 | 27.4817 | 1320.7217 | 184.4642 | 212.1431 | 255.2077 | 293.5035 | 337.5468 | 5.576%
10368 | 27-77 | -76.8979 | 27.4817 | 1334.2501 | 184.0593 | 211.6644 | 254.6111 | 292.799 | 336.7151 | 5.518%
10369 | 27-77 | -77.1692 | 27.4817 | 1347.8661 | 183.5839 | 211.1017 | 253.9084 | 291.9682 | 335.7337 | 5.451%
10370 | 27-77.5 | -77.4405 | 27.4817 | 1361.5671 | 183.12 | 210.5736 | 253.2818 | 291.2551 | 334.922 | 5.382%
10371 | 27-77.5 | -77.7119 | 27.4817 | 1375.3504 | 182.614 | 209.9987 | 252.6012 | 290.482 | 334.0439 | 5.307%
10372 | 27-78 | -77.9832 | 27.4817 | 1389.2136 | 182.0462 | 209.3445 | 251.8122 | 289.5728 | 332.9962 | 5.226%
10373 | 27-78.5 | -78.2545 | 27.4817 | 1403.1543 | 181.4808 | 208.7072 | 251.0661 | 288.7326 | 332.0504 | 5.144%
10374 | 27-78.5 | -78.5258 | 27.4817 | 1417.17 | 180.6619 | 207.7486 | 249.8862 | 287.3527 | 330.437 | 5.033%
10375 | 27-79 | -78.7971 | 27.4817 | 1431.2586 | 179.3896 | 206.2569 | 247.9778 | 285.0597 | 327.688 | 4.871%
10376 | 27-79 | -79.0685 | 27.4817 | 1445.418 | 177.4592 | 204.3179 | 245.473 | 282.0314 | 324.0378 | 4.638%
10377 | 27-79.5 | -79.3398 | 27.4817 | 1459.6459 | 175.1871 | 202.1404 | 242.6396 | 278.5897 | 319.8718 | 4.378%
10378 | 27-79.5 | -79.6111 | 27.4817 | 1473.9403 | 172.7887 | 199.8982 | 239.7062 | 275.014 | 315.5301 | 4.117%
10379 | 27-80 | -79.8824 | 27.4817 | 1488.2994 | 170.3279 | 197.6619 | 236.7836 | 271.4538 | 311.2097 | 3.863%
10380 | 27-80 | -80.1537 | 27.4817 | 1502.7211 | 167.7966 | 195.3922 | 233.8036 | 267.8127 | 306.7794 | 3.615%
10381 | 27-80.5 | -80.4251 | 27.4817 | 1517.2038 | 165.2175 | 193.1206 | 230.8153 | 264.1569 | 302.3262 | 3.376%
10382 | 27-80.5 | -80.6964 | 27.4817 | 1531.7455 | 162.632 | 190.8672 | 227.9139 | 260.6194 | 298.0301 | 3.147%
10383 | 27-81 | -80.9677 | 27.4817 | 1546.3446 | 160.4828 | 188.9793 | 225.4395 | 257.5987 | 294.3567 | 2.967%
10384 | 27-81 | -81.239 | 27.4817 | 1560.9994 | 159.0388 | 187.6207 | 223.6815 | 255.47 | 291.7858 | 2.848%
10385 | 27-81.5 | -81.5104 | 27.4817 | 1575.7084 | 158.3215 | 186.8781 | 222.7856 | 254.4373 | 290.5956 | 2.787%
10386 | 27-82 | -81.7817 | 27.4817 | 1590.4699 | 157.7462 | 186.2861 | 222.0947 | 253.6613 | 289.7246 | 2.739%
10387 | 27-82 | -82.053 | 27.4817 | 1605.2825 | 157.4415 | 186.0508 | 221.9058 | 253.526 | 289.6632 | 2.712%
10388 | 27-82.5 | -82.3243 | 27.4817 | 1620.1447 | 157.6468 | 186.4326 | 222.5888 | 254.5054 | 291.012 | 2.725%
10389 | 27-82.5 | -82.5956 | 27.4817 | 1635.0552 | 158.541 | 187.3126 | 223.9461 | 256.3243 | 293.3986 | 2.787%
10390 | 27-83 | -82.867 | 27.4817 | 1650.0125 | 159.7962 | 188.464 | 225.6845 | 258.6285 | 296.397 | 2.877%
10391 | 27-83 | -83.1383 | 27.4817 | 1665.0154 | 161.2426 | 189.7707 | 227.6648 | 261.2593 | 299.8268 | 2.982%
10392 | 27-83.5 | -83.4096 | 27.4817 | 1680.0626 | 162.8044 | 191.1213 | 229.6763 | 263.9067 | 303.2537 | 3.098%
10393 | 27-83.5 | -83.6809 | 27.4817 | 1695.1529 | 164.4868 | 192.5426 | 231.7655 | 266.6371 | 306.7682 | 3.227%
10394 | 27-84 | -83.9522 | 27.4817 | 1710.285 | 166.3085 | 194.0589 | 233.9735 | 269.5079 | 310.4487 | 3.371%
10395 | 27-84 | -84.2236 | 27.4817 | 1725.4579 | 168.21 | 195.6275 | 236.1639 | 272.3264 | 314.0323 | 3.528%
10396 | 27-84.5 | -84.4949 | 27.4817 | 1740.6704 | 169.7498 | 196.9004 | 237.9969 | 274.696 | 317.0571 | 3.657%
10397 | 27-85 | -84.7662 | 27.4817 | 1755.9214 | 170.7188 | 197.8024 | 239.3295 | 276.4444 | 319.3166 | 3.739%
10398 | 27-85 | -85.0375 | 27.4817 | 1771.2099 | 171.0401 | 198.1812 | 239.9159 | 277.2334 | 320.3566 | 3.764%
10399 | 27-85.5 | -85.3089 | 27.4817 | 1786.5348 | 171.299 | 198.497 | 240.4023 | 277.8862 | 321.2156 | 3.785%
10400 | 27-85.5 | -85.5802 | 27.4817 | 1801.8953 | 171.6235 | 198.88 | 240.9661 | 278.6252 | 322.1705 | 3.813%
10401 | 27-86 | -85.8515 | 27.4817 | 1817.2903 | 171.9182 | 199.1891 | 241.3679 | 279.1135 | 322.7625 | 3.842%
10402 | 27-86 | -86.1228 | 27.4817 | 1832.719 | 172.2701 | 199.5356 | 241.7771 | 279.5776 | 323.2887 | 3.879%
10403 | 27-86.5 | -86.3941 | 27.4817 | 1848.1803 | 172.6874 | 199.9303 | 242.2053 | 280.0291 | 323.7607 | 3.925%
10404 | 27-86.5 | -86.6655 | 27.4817 | 1863.6736 | 173.0671 | 200.2524 | 242.492 | 280.2703 | 323.9355 | 3.971%
10405 | 27-87 | -86.9368 | 27.4817 | 1879.1979 | 173.4749 | 200.6159 | 242.8432 | 280.5988 | 324.2262 | 4.021%
10406 | 27-87 | -87.2081 | 27.4817 | 1894.7523 | 173.8994 | 201.0127 | 243.2495 | 281.004 | 324.6205 | 4.072%
10407 | 27-87.5 | -87.4794 | 27.4817 | 1910.3362 | 174.2231 | 201.3002 | 243.5167 | 281.2425 | 324.8154 | 4.112%
10408 | 27-88 | -87.7507 | 27.4817 | 1925.9488 | 174.5005 | 201.5561 | 243.7739 | 281.4942 | 325.0538 | 4.147%
10409 | 27-88 | -88.0221 | 27.4817 | 1941.5893 | 174.7052 | 201.7461 | 243.9691 | 281.6895 | 325.2447 | 4.172%
10410 | 27-88.5 | -88.2934 | 27.4817 | 1957.257 | 174.7355 | 201.7357 | 243.904 | 281.5686 | 325.0525 | 4.179%
10411 | 27-88.5 | -88.5647 | 27.4817 | 1972.9511 | 174.6896 | 201.6678 | 243.8038 | 281.4372 | 324.883 | 4.175%
10412 | 27-89 | -88.836 | 27.4817 | 1988.6711 | 174.5456 | 201.5179 | 243.6291 | 281.2416 | 324.6645 | 4.158%
10413 | 27-89 | -89.1074 | 27.4817 | 2004.4163 | 174.2437 | 201.2011 | 243.2475 | 280.8028 | 324.1604 | 4.124%
10414 | 27-89.5 | -89.3787 | 27.4817 | 2020.1859 | 173.8738 | 200.8504 | 242.8791 | 280.4266 | 323.7835 | 4.079%
10415 | 27-89.5 | -89.65 | 27.4817 | 2035.9795 | 173.426 | 200.4429 | 242.4888 | 280.0664 | 323.4727 | 4.023%
10416 | 27-90 | -89.9213 | 27.4817 | 2051.7963 | 172.8763 | 199.9349 | 242.004 | 279.6203 | 323.0894 | 3.956%
10417 | 27-90 | -90.1926 | 27.4817 | 2067.6358 | 172.3226 | 199.4416 | 241.5686 | 279.259 | 322.8361 | 3.887%
10418 | 27-90.5 | -90.464 | 27.4817 | 2083.4975 | 171.724 | 198.9101 | 241.1012 | 278.8729 | 322.5681 | 3.815%
10419 | 27-90.5 | -90.7353 | 27.4817 | 2099.3807 | 171.0044 | 198.2562 | 240.4685 | 278.2807 | 322.0445 | 3.733%
10420 | 28-50 | -50.0371 | 27.753 | 1089.4389 | 111.4 | 144.9982 | 183.7199 | 207.7164 | 234.8482 | 0.7319%
10421 | 28-50.5 | -50.3084 | 27.753 | 1078.6953 | 112.8086 | 147.0182 | 185.004 | 209.2477 | 236.6694 | 0.7646%
10422 | 28-50.5 | -50.5797 | 27.753 | 1068.1259 | 114.2469 | 149.0774 | 186.2932 | 210.7726 | 238.4697 | 0.7994%
10423 | 28-51 | -50.851 | 27.753 | 1057.736 | 115.7248 | 151.182 | 187.6032 | 212.3267 | 240.3091 | 0.8369%
10424 | 28-51 | -51.1224 | 27.753 | 1047.5308 | 117.2739 | 153.338 | 188.9808 | 213.9837 | 242.2955 | 0.8782%
10425 | 28-51.5 | -51.3937 | 27.753 | 1037.5159 | 118.8028 | 155.41 | 190.2986 | 215.5547 | 244.1634 | 0.9205%
10426 | 28-51.5 | -51.665 | 27.753 | 1027.6969 | 120.3304 | 157.4039 | 191.5873 | 217.0869 | 245.9811 | 0.9644%
10427 | 28-52 | -51.9363 | 27.753 | 1018.0795 | 121.8836 | 159.3388 | 192.8909 | 218.6458 | 247.8402 | 1.011%
10428 | 28-52 | -52.2077 | 27.753 | 1008.6695 | 123.3843 | 161.1393 | 194.1007 | 220.0677 | 249.5095 | 1.057%
10429 | 28-52.5 | -52.479 | 27.753 | 999.4727 | 124.8548 | 162.8247 | 195.2577 | 221.4238 | 251.0973 | 1.104%
10430 | 28-53 | -52.7503 | 27.753 | 990.4952 | 126.3103 | 164.3949 | 196.395 | 222.7693 | 252.6868 | 1.153%
10431 | 28-53 | -53.0216 | 27.753 | 981.7429 | 127.6809 | 165.7782 | 197.4228 | 223.9702 | 254.0889 | 1.199%
10432 | 28-53.5 | -53.2929 | 27.753 | 973.222 | 129.0235 | 167.0439 | 198.4292 | 225.159 | 255.4909 | 1.246%
10433 | 28-53.5 | -53.5643 | 27.753 | 964.9387 | 130.362 | 168.2039 | 199.4516 | 226.3884 | 256.965 | 1.295%
10434 | 28-54 | -53.8356 | 27.753 | 956.8991 | 131.6366 | 169.1882 | 200.3969 | 227.5123 | 258.2985 | 1.341%
10435 | 28-54 | -54.1069 | 27.753 | 949.1094 | 132.9446 | 170.1253 | 201.3929 | 228.7096 | 259.7333 | 1.391%
10436 | 28-54.5 | -54.3782 | 27.753 | 941.5759 | 134.3162 | 171.038 | 202.4776 | 230.03 | 261.334 | 1.444%
10437 | 28-54.5 | -54.6495 | 27.753 | 934.3048 | 135.6309 | 171.85 | 203.4919 | 231.2464 | 262.7888 | 1.496%
10438 | 28-55 | -54.9209 | 27.753 | 927.3023 | 136.9992 | 172.6926 | 204.5888 | 232.5783 | 264.3998 | 1.553%
10439 | 28-55 | -55.1922 | 27.753 | 920.5746 | 138.4441 | 173.6015 | 205.7948 | 234.0609 | 266.2125 | 1.616%
10440 | 28-55.5 | -55.4635 | 27.753 | 914.1276 | 139.8389 | 174.4819 | 206.9408 | 235.4525 | 267.8959 | 1.678%
10441 | 28-55.5 | -55.7348 | 27.753 | 907.9676 | 141.2828 | 175.4055 | 208.1616 | 236.9496 | 269.7223 | 1.746%
10442 | 28-56 | -56.0061 | 27.753 | 902.1002 | 142.7879 | 176.3804 | 209.4654 | 238.5603 | 271.7 | 1.819%
10443 | 28-56.5 | -56.2775 | 27.753 | 896.5314 | 144.2492 | 177.3247 | 210.703 | 240.0698 | 273.533 | 1.893%
10444 | 28-56.5 | -56.5488 | 27.753 | 891.2666 | 145.7545 | 178.2977 | 211.985 | 241.6388 | 275.4439 | 1.972%
10445 | 28-57 | -56.8201 | 27.753 | 886.3114 | 147.3051 | 179.2985 | 213.3066 | 243.2587 | 277.4197 | 2.057%
10446 | 28-57 | -57.0914 | 27.753 | 881.671 | 148.8239 | 180.2688 | 214.5657 | 244.785 | 279.2633 | 2.143%
10447 | 28-57.5 | -57.3628 | 27.753 | 877.3504 | 150.389 | 181.2616 | 215.8682 | 246.3752 | 281.1964 | 2.235%
10448 | 28-57.5 | -57.6341 | 27.753 | 873.3543 | 151.9841 | 182.2645 | 217.1908 | 247.9955 | 283.1722 | 2.333%
10449 | 28-58 | -57.9054 | 27.753 | 869.6872 | 153.5197 | 183.2161 | 218.4349 | 249.5113 | 285.0119 | 2.43%
10450 | 28-58 | -58.1767 | 27.753 | 866.3534 | 155.1226 | 184.2169 | 219.7666 | 251.1523 | 287.0235 | 2.536%
10451 | 28-58.5 | -58.448 | 27.753 | 863.3567 | 156.7356 | 185.2353 | 221.127 | 252.8329 | 289.0882 | 2.646%
10452 | 28-58.5 | -58.7194 | 27.753 | 860.7006 | 158.2411 | 186.1907 | 222.3826 | 254.3681 | 290.9575 | 2.753%
10453 | 28-59 | -58.9907 | 27.753 | 858.3883 | 159.748 | 187.1939 | 223.7184 | 256.0152 | 292.9778 | 2.864%
10454 | 28-59.5 | -59.262 | 27.753 | 856.4225 | 161.2005 | 188.1958 | 225.0508 | 257.6568 | 294.9901 | 2.976%
10455 | 28-59.5 | -59.5333 | 27.753 | 854.8058 | 162.5253 | 189.1078 | 226.2366 | 259.0969 | 296.7331 | 3.082%
10456 | 28-60 | -59.8046 | 27.753 | 853.54 | 163.8227 | 190.0302 | 227.4493 | 260.58 | 298.5395 | 3.189%
10457 | 28-60 | -60.076 | 27.753 | 852.6268 | 165.0424 | 190.9248 | 228.6249 | 262.0173 | 300.2895 | 3.292%
10458 | 28-60.5 | -60.3473 | 27.753 | 852.0672 | 166.1375 | 191.741 | 229.6786 | 263.2908 | 301.8242 | 3.389%
10459 | 28-60.5 | -60.6186 | 27.753 | 851.8621 | 167.1766 | 192.5533 | 230.7366 | 264.5769 | 303.3821 | 3.483%
10460 | 28-61 | -60.8899 | 27.753 | 852.0115 | 168.1102 | 193.3296 | 231.7472 | 265.805 | 304.8694 | 3.57%
10461 | 28-61 | -61.1613 | 27.753 | 852.5154 | 168.9138 | 194.0486 | 232.6734 | 266.9227 | 306.2147 | 3.648%
10462 | 28-61.5 | -61.4326 | 27.753 | 853.3731 | 169.666 | 194.7862 | 233.6338 | 268.0903 | 307.6294 | 3.723%
10463 | 28-61.5 | -61.7039 | 27.753 | 854.5836 | 170.3263 | 195.5068 | 234.5736 | 269.2343 | 309.0172 | 3.79%
10464 | 28-62 | -61.9752 | 27.753 | 856.1453 | 170.9103 | 196.2106 | 235.4939 | 270.3566 | 310.3813 | 3.851%
10465 | 28-62 | -62.2465 | 27.753 | 858.0563 | 171.5324 | 196.9973 | 236.5536 | 271.6739 | 312.0097 | 3.915%
10466 | 28-62.5 | -62.5179 | 27.753 | 860.3143 | 172.1609 | 197.7948 | 237.6319 | 273.0175 | 313.6743 | 3.98%
10467 | 28-63 | -62.7892 | 27.753 | 862.9166 | 172.7934 | 198.5962 | 238.7141 | 274.3652 | 315.3429 | 4.045%
10468 | 28-63 | -63.0605 | 27.753 | 865.86 | 173.5044 | 199.5141 | 239.978 | 275.9581 | 317.3355 | 4.118%
10469 | 28-63.5 | -63.3318 | 27.753 | 869.1411 | 174.2294 | 200.4464 | 241.2568 | 277.5661 | 319.3432 | 4.193%
10470 | 28-63.5 | -63.6031 | 27.753 | 872.7561 | 174.9518 | 201.3682 | 242.5109 | 279.1349 | 321.2932 | 4.269%
10471 | 28-64 | -63.8745 | 27.753 | 876.7007 | 175.7216 | 202.3561 | 243.8629 | 280.8323 | 323.4096 | 4.351%
10472 | 28-64 | -64.1458 | 27.753 | 880.9707 | 176.4751 | 203.3112 | 245.1526 | 282.4384 | 325.3979 | 4.432%
10473 | 28-64.5 | -64.4171 | 27.753 | 885.5611 | 177.2024 | 204.2184 | 246.3568 | 283.9214 | 327.2166 | 4.514%
10474 | 28-64.5 | -64.6884 | 27.753 | 890.4672 | 177.939 | 205.1313 | 247.5596 | 285.3958 | 329.0168 | 4.598%
10475 | 28-65 | -64.9598 | 27.753 | 895.6837 | 178.6369 | 205.98 | 248.6541 | 286.7184 | 330.6115 | 4.68%
10476 | 28-65 | -65.2311 | 27.753 | 901.2051 | 179.3025 | 206.7766 | 249.6619 | 287.9205 | 332.0437 | 4.762%
10477 | 28-65.5 | -65.5024 | 27.753 | 907.0259 | 179.9662 | 207.5669 | 250.6556 | 289.1009 | 333.4445 | 4.845%
10478 | 28-66 | -65.7737 | 27.753 | 913.1404 | 180.5632 | 208.2561 | 251.4888 | 290.0628 | 334.5549 | 4.923%
10479 | 28-66 | -66.045 | 27.753 | 919.5426 | 181.1196 | 208.8884 | 252.2374 | 290.9131 | 335.5204 | 4.999%
10480 | 28-66.5 | -66.3164 | 27.753 | 926.2266 | 181.6765 | 209.5284 | 253.0063 | 291.7964 | 336.5352 | 5.074%
10481 | 28-66.5 | -66.5877 | 27.753 | 933.1863 | 182.1497 | 210.0567 | 253.6164 | 292.4756 | 337.2901 | 5.142%
10482 | 28-67 | -66.859 | 27.753 | 940.4156 | 182.5871 | 210.5465 | 254.1841 | 293.1096 | 337.9972 | 5.204%
10483 | 28-67 | -67.1303 | 27.753 | 947.9083 | 183.0362 | 211.0674 | 254.8177 | 293.8441 | 338.8488 | 5.266%
10484 | 28-67.5 | -67.4016 | 27.753 | 955.6581 | 183.4133 | 211.4979 | 255.3305 | 294.4293 | 339.5164 | 5.32%
10485 | 28-67.5 | -67.673 | 27.753 | 963.6589 | 183.7739 | 211.9196 | 255.8491 | 295.0356 | 340.225 | 5.37%
10486 | 28-68 | -67.9443 | 27.753 | 971.9043 | 184.1568 | 212.388 | 256.4575 | 295.7746 | 341.1204 | 5.42%
10487 | 28-68 | -68.2156 | 27.753 | 980.3883 | 184.4891 | 212.7956 | 256.9883 | 296.4206 | 341.9044 | 5.463%
10488 | 28-68.5 | -68.4869 | 27.753 | 989.1046 | 184.8165 | 213.2038 | 257.5302 | 297.0883 | 342.7238 | 5.505%
10489 | 28-69 | -68.7583 | 27.753 | 998.0471 | 185.1632 | 213.6449 | 258.1286 | 297.8359 | 343.6523 | 5.548%
10490 | 28-69 | -69.0296 | 27.753 | 1007.2099 | 185.4276 | 213.9772 | 258.5736 | 298.3873 | 344.3323 | 5.581%
10491 | 28-69.5 | -69.3009 | 27.753 | 1016.5868 | 185.673 | 214.2915 | 259.0034 | 298.927 | 345.0055 | 5.611%
10492 | 28-69.5 | -69.5722 | 27.753 | 1026.172 | 185.9243 | 214.6229 | 259.47 | 299.5231 | 345.7603 | 5.64%
10493 | 28-70 | -69.8435 | 27.753 | 1035.9597 | 186.0629 | 214.8002 | 259.712 | 299.8268 | 346.1388 | 5.657%
10494 | 28-70 | -70.1149 | 27.753 | 1045.9441 | 186.1748 | 214.9425 | 259.9051 | 300.0681 | 346.4386 | 5.671%
10495 | 28-70.5 | -70.3862 | 27.753 | 1056.1198 | 186.2792 | 215.0756 | 260.0862 | 300.2948 | 346.7207 | 5.684%
10496 | 28-70.5 | -70.6575 | 27.753 | 1066.481 | 186.2872 | 215.0688 | 260.0522 | 300.233 | 346.6234 | 5.688%
10497 | 28-71 | -70.9288 | 27.753 | 1077.0226 | 186.286 | 215.0454 | 259.9888 | 300.1292 | 346.4683 | 5.692%
10498 | 28-71 | -71.2001 | 27.753 | 1087.7391 | 186.2861 | 215.0192 | 259.9155 | 300.0081 | 346.2867 | 5.697%
10499 | 28-71.5 | -71.4715 | 27.753 | 1098.6255 | 186.2265 | 214.906 | 259.7076 | 299.7064 | 345.8671 | 5.697%
10500 | 28-71.5 | -71.7428 | 27.753 | 1109.6766 | 186.1818 | 214.8135 | 259.5305 | 299.4452 | 345.5003 | 5.698%
10501 | 28-72 | -72.0141 | 27.753 | 1120.8877 | 186.1501 | 214.7379 | 259.377 | 299.214 | 345.1712 | 5.701%
10502 | 28-72.5 | -72.2854 | 27.753 | 1132.2539 | 186.058 | 214.5739 | 259.0869 | 298.7993 | 344.6004 | 5.699%
10503 | 28-72.5 | -72.5568 | 27.753 | 1143.7705 | 186.0053 | 214.459 | 258.862 | 298.4647 | 344.1281 | 5.701%
10504 | 28-73 | -72.8281 | 27.753 | 1155.4331 | 185.9758 | 214.3699 | 258.6668 | 298.1634 | 343.6928 | 5.708%
10505 | 28-73 | -73.0994 | 27.753 | 1167.2372 | 185.8944 | 214.2015 | 258.3447 | 297.6883 | 343.0256 | 5.71%
10506 | 28-73.5 | -73.3707 | 27.753 | 1179.1785 | 185.8785 | 214.1246 | 258.1583 | 297.392 | 342.5901 | 5.719%
10507 | 28-73.5 | -73.642 | 27.753 | 1191.2528 | 185.8947 | 214.095 | 258.0457 | 297.195 | 342.2859 | 5.731%
10508 | 28-74 | -73.9134 | 27.753 | 1203.4562 | 185.8597 | 213.9958 | 257.8322 | 296.8674 | 341.8143 | 5.738%
10509 | 28-74 | -74.1847 | 27.753 | 1215.7846 | 185.861 | 213.9559 | 257.7182 | 296.6786 | 341.5307 | 5.746%
10510 | 28-74.5 | -74.456 | 27.753 | 1228.2344 | 185.8638 | 213.9267 | 257.6314 | 296.5338 | 341.3122 | 5.753%
10511 | 28-74.5 | -74.7273 | 27.753 | 1240.8017 | 185.8058 | 213.8207 | 257.4414 | 296.2608 | 340.9355 | 5.752%
10512 | 28-75 | -74.9986 | 27.753 | 1253.4831 | 185.7467 | 213.7203 | 257.269 | 296.0175 | 340.6039 | 5.75%
10513 | 28-75.5 | -75.27 | 27.753 | 1266.275 | 185.6507 | 213.5773 | 257.0449 | 295.7144 | 340.2031 | 5.742%
10514 | 28-75.5 | -75.5413 | 27.753 | 1279.1741 | 185.4672 | 213.3261 | 256.6787 | 295.2375 | 339.5902 | 5.722%
10515 | 28-76 | -75.8126 | 27.753 | 1292.1772 | 185.2656 | 213.0674 | 256.3246 | 294.7928 | 339.0356 | 5.697%
10516 | 28-76 | -76.0839 | 27.753 | 1305.2811 | 185.0069 | 212.7487 | 255.9075 | 294.2837 | 338.416 | 5.661%
10517 | 28-76.5 | -76.3553 | 27.753 | 1318.4827 | 184.6549 | 212.3213 | 255.357 | 293.6187 | 337.6143 | 5.613%
10518 | 28-76.5 | -76.6266 | 27.753 | 1331.7791 | 184.2796 | 211.8837 | 254.8209 | 292.9936 | 336.8854 | 5.558%
10519 | 28-77 | -76.8979 | 27.753 | 1345.1675 | 183.8448 | 211.3809 | 254.2113 | 292.2881 | 336.069 | 5.493%
10520 | 28-77 | -77.1692 | 27.753 | 1358.6451 | 183.339 | 210.7927 | 253.4932 | 291.453 | 335.0977 | 5.42%
10521 | 28-77.5 | -77.4405 | 27.753 | 1372.2092 | 182.8454 | 210.2394 | 252.8503 | 290.7333 | 334.2926 | 5.345%
10522 | 28-77.5 | -77.7119 | 27.753 | 1385.8572 | 182.3098 | 209.6381 | 252.1503 | 289.9485 | 333.4134 | 5.266%
10523 | 28-78 | -77.9832 | 27.753 | 1399.5867 | 181.7112 | 208.9546 | 251.3358 | 289.0185 | 332.3514 | 5.179%
10524 | 28-78.5 | -78.2545 | 27.753 | 1413.3952 | 181.1147 | 208.2853 | 250.5573 | 288.1464 | 331.375 | 5.093%
10525 | 28-78.5 | -78.5258 | 27.753 | 1427.2804 | 180.2807 | 207.313 | 249.3668 | 286.7593 | 329.7592 | 4.98%
10526 | 28-79 | -78.7971 | 27.753 | 1441.2401 | 179.0221 | 205.8427 | 247.4929 | 284.5136 | 327.0732 | 4.82%
10527 | 28-79 | -79.0685 | 27.753 | 1455.2719 | 177.1437 | 203.9613 | 245.0707 | 281.5918 | 323.5586 | 4.595%
10528 | 28-79.5 | -79.3398 | 27.753 | 1469.3739 | 174.9113 | 201.8272 | 242.3016 | 278.2345 | 319.5015 | 4.341%
10529 | 28-79.5 | -79.6111 | 27.753 | 1483.544 | 172.4926 | 199.5836 | 239.3742 | 274.6721 | 315.1826 | 4.079%
10530 | 28-80 | -79.8824 | 27.753 | 1497.7802 | 169.9618 | 197.3014 | 236.3996 | 271.0549 | 310.7999 | 3.819%
10531 | 28-80 | -80.1537 | 27.753 | 1512.0805 | 167.2959 | 194.9373 | 233.3031 | 267.2775 | 306.21 | 3.561%
10532 | 28-80.5 | -80.4251 | 27.753 | 1526.4432 | 164.5141 | 192.52 | 230.1295 | 263.4001 | 301.4923 | 3.307%
10533 | 28-80.5 | -80.6964 | 27.753 | 1540.8665 | 161.6627 | 190.0508 | 226.9732 | 259.5549 | 296.8259 | 3.06%
10534 | 28-81 | -80.9677 | 27.753 | 1555.3486 | 159.2561 | 187.9596 | 224.253 | 256.2378 | 292.7957 | 2.864%
10535 | 28-81 | -81.239 | 27.753 | 1569.8878 | 157.5936 | 186.4417 | 222.2917 | 253.8649 | 289.9326 | 2.733%
10536 | 28-81.5 | -81.5104 | 27.753 | 1584.4825 | 156.7006 | 185.5728 | 221.2372 | 252.6443 | 288.5198 | 2.661%
10537 | 28-82 | -81.7817 | 27.753 | 1599.1313 | 155.981 | 184.8795 | 220.4214 | 251.7221 | 287.4777 | 2.604%
10538 | 28-82 | -82.053 | 27.753 | 1613.8324 | 155.5448 | 184.5442 | 220.1096 | 251.443 | 287.2482 | 2.569%
10539 | 28-82.5 | -82.3243 | 27.753 | 1628.5846 | 155.6205 | 184.8108 | 220.6497 | 252.2544 | 288.3994 | 2.572%
10540 | 28-82.5 | -82.5956 | 27.753 | 1643.3862 | 156.3518 | 185.5439 | 221.8202 | 253.8499 | 290.5194 | 2.621%
10541 | 28-83 | -82.867 | 27.753 | 1658.2361 | 157.4569 | 186.5625 | 223.3878 | 255.9483 | 293.2705 | 2.696%
10542 | 28-83 | -83.1383 | 27.753 | 1673.1328 | 158.8146 | 187.7805 | 225.2528 | 258.4388 | 296.5304 | 2.789%
10543 | 28-83.5 | -83.4096 | 27.753 | 1688.0751 | 160.3411 | 189.0907 | 227.2093 | 261.0175 | 299.8718 | 2.897%
10544 | 28-83.5 | -83.6809 | 27.753 | 1703.0617 | 162.0573 | 190.5236 | 229.3105 | 263.7599 | 303.3979 | 3.022%
10545 | 28-84 | -83.9522 | 27.753 | 1718.0914 | 163.9866 | 192.1052 | 231.6004 | 266.7278 | 307.1931 | 3.167%
10546 | 28-84 | -84.2236 | 27.753 | 1733.163 | 166.0619 | 193.8101 | 233.9406 | 269.7245 | 310.9883 | 3.333%
10547 | 28-84.5 | -84.4949 | 27.753 | 1748.2755 | 167.7712 | 195.2072 | 235.9118 | 272.2558 | 314.2021 | 3.472%
10548 | 28-85 | -84.7662 | 27.753 | 1763.4276 | 168.8783 | 196.1917 | 237.341 | 274.113 | 316.5838 | 3.563%
10549 | 28-85 | -85.0375 | 27.753 | 1778.6184 | 169.3025 | 196.628 | 237.9898 | 274.9675 | 317.6919 | 3.597%
10550 | 28-85.5 | -85.3089 | 27.753 | 1793.8467 | 169.6435 | 196.9856 | 238.5171 | 275.6592 | 318.586 | 3.626%
10551 | 28-85.5 | -85.5802 | 27.753 | 1809.1117 | 170.0341 | 197.3979 | 239.1049 | 276.4158 | 319.5497 | 3.659%
10552 | 28-86 | -85.8515 | 27.753 | 1824.4123 | 170.3736 | 197.723 | 239.5107 | 276.8955 | 320.1165 | 3.692%
10553 | 28-86 | -86.1228 | 27.753 | 1839.7476 | 170.778 | 198.0895 | 239.9294 | 277.3575 | 320.6252 | 3.733%
10554 | 28-86.5 | -86.3941 | 27.753 | 1855.1167 | 171.26 | 198.5134 | 240.3793 | 277.8223 | 321.0989 | 3.785%
10555 | 28-86.5 | -86.6655 | 27.753 | 1870.5187 | 171.7111 | 198.8741 | 240.7001 | 278.092 | 321.294 | 3.837%
10556 | 28-87 | -86.9368 | 27.753 | 1885.9527 | 172.1952 | 199.281 | 241.0914 | 278.4559 | 321.6129 | 3.893%
10557 | 28-87 | -87.2081 | 27.753 | 1901.418 | 172.6993 | 199.7256 | 241.5426 | 278.9017 | 322.0411 | 3.951%
10558 | 28-87.5 | -87.4794 | 27.753 | 1916.9137 | 173.1024 | 200.0641 | 241.8598 | 279.1877 | 322.279 | 4%
10559 | 28-88 | -87.7507 | 27.753 | 1932.4389 | 173.4609 | 200.3746 | 242.1729 | 279.495 | 322.5714 | 4.042%
10560 | 28-88 | -88.0221 | 27.753 | 1947.9931 | 173.7427 | 200.6179 | 242.4228 | 279.7451 | 322.8159 | 4.076%
10561 | 28-88.5 | -88.2934 | 27.753 | 1963.5753 | 173.8089 | 200.6383 | 242.382 | 279.6409 | 322.6299 | 4.087%
10562 | 28-88.5 | -88.5647 | 27.753 | 1979.185 | 173.758 | 200.5743 | 242.2674 | 279.4763 | 322.403 | 4.084%
10563 | 28-89 | -88.836 | 27.753 | 1994.8214 | 173.57 | 200.4022 | 242.0404 | 279.1982 | 322.0639 | 4.065%
10564 | 28-89 | -89.1074 | 27.753 | 2010.4838 | 173.1906 | 200.0433 | 241.5783 | 278.6407 | 321.393 | 4.026%
10565 | 28-89.5 | -89.3787 | 27.753 | 2026.1716 | 172.7154 | 199.6319 | 241.1044 | 278.115 | 320.8113 | 3.974%
10566 | 28-89.5 | -89.65 | 27.753 | 2041.8841 | 172.1488 | 199.1568 | 240.6014 | 277.5974 | 320.2877 | 3.91%
10567 | 28-90 | -89.9213 | 27.753 | 2057.6207 | 171.5089 | 198.606 | 240.043 | 277.0472 | 319.7621 | 3.837%
10568 | 28-90 | -90.1926 | 27.753 | 2073.3809 | 170.9017 | 198.0958 | 239.5754 | 276.6384 | 319.4417 | 3.766%
10569 | 28-90.5 | -90.464 | 27.753 | 2089.164 | 170.2612 | 197.5566 | 239.0947 | 276.2333 | 319.1476 | 3.692%
10570 | 28-90.5 | -90.7353 | 27.753 | 2104.9695 | 169.4597 | 196.8708 | 238.422 | 275.5937 | 318.5677 | 3.606%
10571 | 28-50 | -50.0371 | 28.0243 | 1103.707 | 111.7513 | 145.3509 | 183.8863 | 207.8778 | 235.0003 | 0.738%
10572 | 28-50.5 | -50.3084 | 28.0243 | 1093.1268 | 113.0987 | 147.2856 | 185.1247 | 209.3612 | 236.7718 | 0.7697%
10573 | 28-50.5 | -50.5797 | 28.0243 | 1082.721 | 114.479 | 149.2641 | 186.3703 | 210.8403 | 238.524 | 0.8035%
10574 | 28-51 | -50.851 | 28.0243 | 1072.4948 | 115.9033 | 151.2955 | 187.6393 | 212.349 | 240.3136 | 0.8399%
10575 | 28-51 | -51.1224 | 28.0243 | 1062.4533 | 117.4031 | 153.3924 | 188.978 | 213.9611 | 242.2478 | 0.8802%
10576 | 28-51.5 | -51.3937 | 28.0243 | 1052.6019 | 118.8914 | 155.4161 | 190.2616 | 215.4894 | 244.0631 | 0.9215%
10577 | 28-51.5 | -51.665 | 28.0243 | 1042.946 | 120.3894 | 157.3723 | 191.5232 | 216.9853 | 245.833 | 0.9646%
10578 | 28-52 | -51.9363 | 28.0243 | 1033.4912 | 121.9249 | 159.2815 | 192.8087 | 218.517 | 247.6538 | 1.011%
10579 | 28-52 | -52.2077 | 28.0243 | 1024.2429 | 123.4181 | 161.0663 | 194.007 | 219.9185 | 249.2914 | 1.057%
10580 | 28-52.5 | -52.479 | 28.0243 | 1015.2069 | 124.8911 | 162.7463 | 195.1585 | 221.2599 | 250.8532 | 1.104%
10581 | 28-53 | -52.7503 | 28.0243 | 1006.389 | 126.3589 | 164.3212 | 196.296 | 222.5959 | 252.4205 | 1.152%
10582 | 28-53 | -53.0216 | 28.0243 | 997.7948 | 127.7515 | 165.7197 | 197.3307 | 223.7942 | 253.8077 | 1.2%
10583 | 28-53.5 | -53.2929 | 28.0243 | 989.4304 | 129.1254 | 167.0113 | 198.3516 | 224.9889 | 255.2048 | 1.248%
10584 | 28-53.5 | -53.5643 | 28.0243 | 981.3016 | 130.5036 | 168.2072 | 199.3954 | 226.233 | 256.6842 | 1.298%
10585 | 28-54 | -53.8356 | 28.0243 | 973.4143 | 131.8273 | 169.2372 | 200.366 | 227.3736 | 258.0232 | 1.347%
10586 | 28-54 | -54.1069 | 28.0243 | 965.7745 | 133.188 | 170.221 | 201.389 | 228.5901 | 259.467 | 1.399%
10587 | 28-54.5 | -54.3782 | 28.0243 | 958.3881 | 134.6134 | 171.1778 | 202.5007 | 229.9314 | 261.0797 | 1.455%
10588 | 28-54.5 | -54.6495 | 28.0243 | 951.261 | 135.9792 | 172.0219 | 203.5394 | 231.166 | 262.5445 | 1.51%
10589 | 28-55 | -54.9209 | 28.0243 | 944.3992 | 137.3916 | 172.888 | 204.6549 | 232.5111 | 264.1612 | 1.569%
10590 | 28-55 | -55.1922 | 28.0243 | 937.8084 | 138.8719 | 173.8137 | 205.8728 | 234.0002 | 265.9732 | 1.634%
10591 | 28-55.5 | -55.4635 | 28.0243 | 931.4945 | 140.291 | 174.7028 | 207.0227 | 235.3905 | 267.6484 | 1.699%
10592 | 28-55.5 | -55.7348 | 28.0243 | 925.4631 | 141.7498 | 175.6291 | 208.2419 | 236.8815 | 269.4627 | 1.768%
10593 | 28-56 | -56.0061 | 28.0243 | 919.7199 | 143.2613 | 176.6013 | 209.5393 | 238.4818 | 271.4249 | 1.843%
10594 | 28-56.5 | -56.2775 | 28.0243 | 914.2702 | 144.7202 | 177.5377 | 210.7655 | 239.9764 | 273.2386 | 1.918%
10595 | 28-56.5 | -56.5488 | 28.0243 | 909.1194 | 146.2149 | 178.4978 | 212.0302 | 241.5238 | 275.1226 | 1.998%
10596 | 28-57 | -56.8201 | 28.0243 | 904.2725 | 147.7464 | 179.4807 | 213.3276 | 243.1134 | 277.0605 | 2.083%
10597 | 28-57 | -57.0914 | 28.0243 | 899.7346 | 149.2326 | 180.4242 | 214.5484 | 244.5903 | 278.8412 | 2.169%
10598 | 28-57.5 | -57.3628 | 28.0243 | 895.5103 | 150.7511 | 181.3818 | 215.8023 | 246.119 | 280.697 | 2.26%
10599 | 28-57.5 | -57.6341 | 28.0243 | 891.6041 | 152.2878 | 182.3433 | 217.0694 | 247.6705 | 282.5877 | 2.355%
10600 | 28-58 | -57.9054 | 28.0243 | 888.0202 | 153.7592 | 183.2516 | 218.2577 | 249.1187 | 284.3458 | 2.45%
10601 | 28-58 | -58.1767 | 28.0243 | 884.7625 | 155.3015 | 184.2098 | 219.5376 | 250.6994 | 286.287 | 2.552%
10602 | 28-58.5 | -58.448 | 28.0243 | 881.8347 | 156.861 | 185.1888 | 220.8533 | 252.3309 | 288.2977 | 2.659%
10603 | 28-58.5 | -58.7194 | 28.0243 | 879.24 | 158.3189 | 186.1122 | 222.0768 | 253.8347 | 290.137 | 2.763%
10604 | 28-59 | -58.9907 | 28.0243 | 876.9815 | 159.7864 | 187.093 | 223.3956 | 255.4706 | 292.1538 | 2.872%
10605 | 28-59.5 | -59.262 | 28.0243 | 875.0617 | 161.2071 | 188.0813 | 224.7244 | 257.1189 | 294.1861 | 2.982%
10606 | 28-59.5 | -59.5333 | 28.0243 | 873.4829 | 162.5068 | 188.9865 | 225.9159 | 258.5774 | 295.9638 | 3.086%
10607 | 28-60 | -59.8046 | 28.0243 | 872.2469 | 163.787 | 189.9094 | 227.1446 | 260.0921 | 297.8213 | 3.191%
10608 | 28-60 | -60.076 | 28.0243 | 871.3552 | 164.9947 | 190.8086 | 228.3407 | 261.5659 | 299.6281 | 3.294%
10609 | 28-60.5 | -60.3473 | 28.0243 | 870.8089 | 166.0811 | 191.6291 | 229.4125 | 262.8712 | 301.2119 | 3.39%
10610 | 28-60.5 | -60.6186 | 28.0243 | 870.6085 | 167.1203 | 192.45 | 230.4939 | 264.1955 | 302.8265 | 3.484%
10611 | 28-61 | -60.8899 | 28.0243 | 870.7544 | 168.0626 | 193.2385 | 231.5315 | 265.4653 | 304.3738 | 3.571%
10612 | 28-61 | -61.1613 | 28.0243 | 871.2464 | 168.8818 | 193.9716 | 232.4846 | 266.6226 | 305.7745 | 3.65%
10613 | 28-61.5 | -61.4326 | 28.0243 | 872.0839 | 169.6512 | 194.7215 | 233.4671 | 267.8218 | 307.2326 | 3.726%
10614 | 28-61.5 | -61.7039 | 28.0243 | 873.2659 | 170.3247 | 195.4522 | 234.4232 | 268.9879 | 308.6497 | 3.795%
10615 | 28-62 | -61.9752 | 28.0243 | 874.7909 | 170.9149 | 196.1628 | 235.3521 | 270.1204 | 310.0259 | 3.857%
10616 | 28-62 | -62.2465 | 28.0243 | 876.6573 | 171.5385 | 196.9495 | 236.4091 | 271.4321 | 311.6447 | 3.921%
10617 | 28-62.5 | -62.5179 | 28.0243 | 878.8627 | 172.1644 | 197.7404 | 237.4737 | 272.7549 | 313.2796 | 3.986%
10618 | 28-63 | -62.7892 | 28.0243 | 881.4048 | 172.791 | 198.5302 | 238.5339 | 274.0704 | 314.9032 | 4.052%
10619 | 28-63 | -63.0605 | 28.0243 | 884.2804 | 173.4943 | 199.4337 | 239.7722 | 275.6264 | 316.8448 | 4.124%
10620 | 28-63.5 | -63.3318 | 28.0243 | 887.4865 | 174.2095 | 200.3488 | 241.0204 | 277.1907 | 318.7922 | 4.199%
10621 | 28-63.5 | -63.6031 | 28.0243 | 891.0194 | 174.9222 | 201.2534 | 242.244 | 278.716 | 320.6825 | 4.275%
10622 | 28-64 | -63.8745 | 28.0243 | 894.8752 | 175.6856 | 202.2296 | 243.5751 | 280.3833 | 322.7573 | 4.356%
10623 | 28-64 | -64.1458 | 28.0243 | 899.0498 | 176.4357 | 203.1769 | 244.8494 | 281.9661 | 324.7126 | 4.438%
10624 | 28-64.5 | -64.4171 | 28.0243 | 903.5388 | 177.1621 | 204.0796 | 246.0424 | 283.4313 | 326.5048 | 4.52%
10625 | 28-64.5 | -64.6884 | 28.0243 | 908.3374 | 177.9002 | 204.9916 | 247.24 | 284.896 | 328.2897 | 4.605%
10626 | 28-65 | -64.9598 | 28.0243 | 913.4408 | 178.6011 | 205.8421 | 248.334 | 286.2156 | 329.8782 | 4.689%
10627 | 28-65 | -65.2311 | 28.0243 | 918.8438 | 179.2705 | 206.6425 | 249.3451 | 287.4206 | 331.3123 | 4.771%
10628 | 28-65.5 | -65.5024 | 28.0243 | 924.5413 | 179.9383 | 207.4377 | 250.3453 | 288.6088 | 332.7226 | 4.855%
10629 | 28-66 | -65.7737 | 28.0243 | 930.5278 | 180.5392 | 208.1322 | 251.1861 | 289.5803 | 333.8451 | 4.934%
10630 | 28-66 | -66.045 | 28.0243 | 936.7976 | 181.0994 | 208.7698 | 251.9423 | 290.4405 | 334.8234 | 5.011%
10631 | 28-66.5 | -66.3164 | 28.0243 | 943.3453 | 181.6598 | 209.4148 | 252.719 | 291.3344 | 335.852 | 5.087%
10632 | 28-66.5 | -66.5877 | 28.0243 | 950.1649 | 182.1373 | 209.9493 | 253.3386 | 292.0262 | 336.6234 | 5.155%
10633 | 28-67 | -66.859 | 28.0243 | 957.2507 | 182.5806 | 210.4478 | 253.9199 | 292.6785 | 337.3547 | 5.219%
10634 | 28-67 | -67.1303 | 28.0243 | 964.5967 | 183.0376 | 210.9807 | 254.5723 | 293.4386 | 338.24 | 5.282%
10635 | 28-67.5 | -67.4016 | 28.0243 | 972.1971 | 183.4215 | 211.4208 | 255.0995 | 294.0428 | 338.9323 | 5.336%
10636 | 28-67.5 | -67.673 | 28.0243 | 980.0459 | 183.7877 | 211.8505 | 255.6301 | 294.6649 | 339.6615 | 5.387%
10637 | 28-68 | -67.9443 | 28.0243 | 988.1371 | 184.1754 | 212.3263 | 256.2503 | 295.42 | 340.5782 | 5.438%
10638 | 28-68 | -68.2156 | 28.0243 | 996.4649 | 184.5107 | 212.7386 | 256.7889 | 296.0767 | 341.3765 | 5.481%
10639 | 28-68.5 | -68.4869 | 28.0243 | 1005.0233 | 184.8404 | 213.1504 | 257.3364 | 296.7519 | 342.2057 | 5.523%
10640 | 28-69 | -68.7583 | 28.0243 | 1013.8065 | 185.1902 | 213.5954 | 257.9403 | 297.5063 | 343.1427 | 5.567%
10641 | 28-69 | -69.0296 | 28.0243 | 1022.8086 | 185.4587 | 213.9326 | 258.3913 | 298.0649 | 343.8311 | 5.601%
10642 | 28-69.5 | -69.3009 | 28.0243 | 1032.0239 | 185.7096 | 214.2534 | 258.8289 | 298.6135 | 344.5145 | 5.632%
10643 | 28-69.5 | -69.5722 | 28.0243 | 1041.4467 | 185.9679 | 214.5925 | 259.3044 | 299.2194 | 345.2798 | 5.662%
10644 | 28-70 | -69.8435 | 28.0243 | 1051.0713 | 186.1157 | 214.7796 | 259.5569 | 299.534 | 345.6696 | 5.68%
10645 | 28-70 | -70.1149 | 28.0243 | 1060.8924 | 186.2378 | 214.9328 | 259.7617 | 299.7874 | 345.9817 | 5.696%
10646 | 28-70.5 | -70.3862 | 28.0243 | 1070.9043 | 186.3528 | 215.0772 | 259.9547 | 300.0264 | 346.2762 | 5.711%
10647 | 28-70.5 | -70.6575 | 28.0243 | 1081.1018 | 186.369 | 215.0778 | 259.9265 | 299.9686 | 346.1803 | 5.717%
10648 | 28-71 | -70.9288 | 28.0243 | 1091.4797 | 186.3769 | 215.0634 | 259.8717 | 299.8727 | 346.0321 | 5.722%
10649 | 28-71 | -71.2001 | 28.0243 | 1102.0329 | 186.387 | 215.0482 | 259.8105 | 299.7647 | 345.8644 | 5.729%
10650 | 28-71.5 | -71.4715 | 28.0243 | 1112.7562 | 186.3363 | 214.9442 | 259.6122 | 299.4727 | 345.4546 | 5.731%
10651 | 28-71.5 | -71.7428 | 28.0243 | 1123.6449 | 186.3011 | 214.862 | 259.4466 | 299.2238 | 345.101 | 5.733%
10652 | 28-72 | -72.0141 | 28.0243 | 1134.694 | 186.2789 | 214.7968 | 259.3048 | 299.0055 | 344.786 | 5.738%
10653 | 28-72.5 | -72.2854 | 28.0243 | 1145.899 | 186.1922 | 214.6375 | 259.0182 | 298.5927 | 344.2153 | 5.737%
10654 | 28-72.5 | -72.5568 | 28.0243 | 1157.2553 | 186.1406 | 214.5215 | 258.7879 | 298.2488 | 343.7286 | 5.74%
10655 | 28-73 | -72.8281 | 28.0243 | 1168.7584 | 186.1083 | 214.4261 | 258.5804 | 297.929 | 343.2673 | 5.747%
10656 | 28-73 | -73.0994 | 28.0243 | 1180.404 | 186.0209 | 214.2481 | 258.2424 | 297.4321 | 342.5708 | 5.749%
10657 | 28-73.5 | -73.3707 | 28.0243 | 1192.1878 | 185.9952 | 214.1573 | 258.0356 | 297.109 | 342.1009 | 5.757%
10658 | 28-73.5 | -73.642 | 28.0243 | 1204.1059 | 185.9975 | 214.1096 | 257.8976 | 296.8801 | 341.7566 | 5.768%
10659 | 28-74 | -73.9134 | 28.0243 | 1216.1542 | 185.944 | 213.9875 | 257.6542 | 296.5159 | 341.2405 | 5.772%
10660 | 28-74 | -74.1847 | 28.0243 | 1228.3288 | 185.9242 | 213.9229 | 257.5098 | 296.2916 | 340.9156 | 5.778%
10661 | 28-74.5 | -74.456 | 28.0243 | 1240.626 | 185.9027 | 213.8665 | 257.3914 | 296.1116 | 340.6581 | 5.781%
10662 | 28-74.5 | -74.7273 | 28.0243 | 1253.0421 | 185.8173 | 213.7314 | 257.1704 | 295.8064 | 340.2484 | 5.775%
10663 | 28-75 | -74.9986 | 28.0243 | 1265.5736 | 185.7295 | 213.6033 | 256.973 | 295.5417 | 339.9007 | 5.767%
10664 | 28-75.5 | -75.27 | 28.0243 | 1278.2171 | 185.6024 | 213.4316 | 256.7259 | 295.2221 | 339.4924 | 5.753%
10665 | 28-75.5 | -75.5413 | 28.0243 | 1290.9692 | 185.3851 | 213.1493 | 256.3346 | 294.7272 | 338.8713 | 5.726%
10666 | 28-76 | -75.8126 | 28.0243 | 1303.8267 | 185.151 | 212.8621 | 255.9607 | 294.2723 | 338.3195 | 5.694%
10667 | 28-76 | -76.0839 | 28.0243 | 1316.7864 | 184.8609 | 212.5174 | 255.5283 | 293.7594 | 337.7117 | 5.652%
10668 | 28-76.5 | -76.3553 | 28.0243 | 1329.8455 | 184.4785 | 212.0657 | 254.9656 | 293.0954 | 336.9284 | 5.596%
10669 | 28-76.5 | -76.6266 | 28.0243 | 1343.0008 | 184.0733 | 211.6045 | 254.4182 | 292.4721 | 336.2187 | 5.535%
10670 | 28-77 | -76.8979 | 28.0243 | 1356.2496 | 183.6088 | 211.078 | 253.797 | 291.7683 | 335.4212 | 5.464%
10671 | 28-77 | -77.1692 | 28.0243 | 1369.5891 | 183.0727 | 210.4652 | 253.0656 | 290.9319 | 334.4648 | 5.385%
10672 | 28-77.5 | -77.4405 | 28.0243 | 1383.0166 | 182.5492 | 209.8867 | 252.4069 | 290.2069 | 333.6682 | 5.305%
10673 | 28-77.5 | -77.7119 | 28.0243 | 1396.5296 | 181.9836 | 209.2588 | 251.6874 | 289.4105 | 332.7881 | 5.22%
10674 | 28-78 | -77.9832 | 28.0243 | 1410.1255 | 181.3545 | 208.5462 | 250.8476 | 288.4597 | 331.7119 | 5.129%
10675 | 28-78.5 | -78.2545 | 28.0243 | 1423.802 | 180.7268 | 207.8451 | 250.037 | 287.5561 | 330.7054 | 5.038%
10676 | 28-78.5 | -78.5258 | 28.0243 | 1437.5567 | 179.8777 | 206.8594 | 248.8368 | 286.1634 | 329.0895 | 4.923%
10677 | 28-79 | -78.7971 | 28.0243 | 1451.3873 | 178.6331 | 205.4115 | 246.9999 | 283.969 | 326.4724 | 4.766%
10678 | 28-79 | -79.0685 | 28.0243 | 1465.2916 | 176.8118 | 203.5902 | 244.6654 | 281.1612 | 323.104 | 4.549%
10679 | 28-79.5 | -79.3398 | 28.0243 | 1479.2676 | 174.6432 | 201.5179 | 241.9872 | 277.9226 | 319.1996 | 4.303%
10680 | 28-79.5 | -79.6111 | 28.0243 | 1493.3131 | 172.2545 | 199.3164 | 239.1261 | 274.4503 | 314.9998 | 4.046%
10681 | 28-80 | -79.8824 | 28.0243 | 1507.4261 | 169.7257 | 197.0568 | 236.1945 | 270.8961 | 310.7053 | 3.788%
10682 | 28-80 | -80.1537 | 28.0243 | 1521.6048 | 166.9848 | 194.6565 | 233.0624 | 267.0845 | 306.0838 | 3.524%
10683 | 28-80.5 | -80.4251 | 28.0243 | 1535.8473 | 164.0308 | 192.1254 | 229.7485 | 263.0427 | 301.1736 | 3.258%
10684 | 28-80.5 | -80.6964 | 28.0243 | 1550.1517 | 160.9188 | 189.4464 | 226.3493 | 258.9066 | 296.1592 | 2.993%
10685 | 28-81 | -80.9677 | 28.0243 | 1564.5164 | 158.2428 | 187.1327 | 223.3751 | 255.2839 | 291.7627 | 2.78%
10686 | 28-81 | -81.239 | 28.0243 | 1578.9396 | 156.3329 | 185.4243 | 221.1852 | 252.637 | 288.5714 | 2.634%
10687 | 28-81.5 | -81.5104 | 28.0243 | 1593.4197 | 155.2174 | 184.3966 | 219.9294 | 251.176 | 286.872 | 2.549%
10688 | 28-82 | -81.7817 | 28.0243 | 1607.9551 | 154.3129 | 183.5751 | 218.9531 | 250.0636 | 285.6049 | 2.481%
10689 | 28-82 | -82.053 | 28.0243 | 1622.5443 | 153.7191 | 183.124 | 218.4967 | 249.6138 | 285.174 | 2.438%
10690 | 28-82.5 | -82.3243 | 28.0243 | 1637.1858 | 153.6548 | 183.2709 | 218.8869 | 250.2478 | 286.1156 | 2.432%
10691 | 28-82.5 | -82.5956 | 28.0243 | 1651.8782 | 154.2114 | 183.8538 | 219.8645 | 251.611 | 287.9565 | 2.467%
10692 | 28-83 | -82.867 | 28.0243 | 1666.62 | 155.1358 | 184.7207 | 221.234 | 253.4681 | 290.4147 | 2.526%
10693 | 28-83 | -83.1383 | 28.0243 | 1681.4099 | 156.348 | 185.8064 | 222.9227 | 255.7411 | 293.4075 | 2.605%
10694 | 28-83.5 | -83.4096 | 28.0243 | 1696.2466 | 157.7592 | 187.006 | 224.7273 | 258.1288 | 296.5105 | 2.699%
10695 | 28-83.5 | -83.6809 | 28.0243 | 1711.1288 | 159.44 | 188.3893 | 226.7558 | 260.7762 | 299.9145 | 2.815%
10696 | 28-84 | -83.9522 | 28.0243 | 1726.0554 | 161.436 | 190.001 | 229.0787 | 263.7789 | 303.7461 | 2.957%
10697 | 28-84 | -84.2236 | 28.0243 | 1741.0251 | 163.6693 | 191.8335 | 231.5529 | 266.9331 | 307.726 | 3.127%
10698 | 28-84.5 | -84.4949 | 28.0243 | 1756.0368 | 165.5495 | 193.3718 | 233.6679 | 269.6321 | 311.1351 | 3.275%
10699 | 28-85 | -84.7662 | 28.0243 | 1771.0893 | 166.8123 | 194.4677 | 235.2167 | 271.6258 | 313.6724 | 3.375%
10700 | 28-85 | -85.0375 | 28.0243 | 1786.1816 | 167.3748 | 194.9913 | 235.9674 | 272.5949 | 314.9089 | 3.421%
10701 | 28-85.5 | -85.3089 | 28.0243 | 1801.3126 | 167.8265 | 195.4139 | 236.5674 | 273.365 | 315.8874 | 3.458%
10702 | 28-85.5 | -85.5802 | 28.0243 | 1816.4813 | 168.2968 | 195.8666 | 237.195 | 274.1598 | 316.8861 | 3.498%
10703 | 28-86 | -85.8515 | 28.0243 | 1831.6867 | 168.6776 | 196.2067 | 237.6055 | 274.6331 | 317.4318 | 3.534%
10704 | 28-86 | -86.1228 | 28.0243 | 1846.9279 | 169.1267 | 196.5903 | 238.0327 | 275.0944 | 317.9276 | 3.578%
10705 | 28-86.5 | -86.3941 | 28.0243 | 1862.2039 | 169.6668 | 197.04 | 238.5045 | 275.5763 | 318.4115 | 3.633%
10706 | 28-86.5 | -86.6655 | 28.0243 | 1877.5138 | 170.1825 | 197.4337 | 238.8562 | 275.8737 | 318.6296 | 3.69%
10707 | 28-87 | -86.9368 | 28.0243 | 1892.8568 | 170.7391 | 197.8774 | 239.2826 | 276.2701 | 318.9767 | 3.751%
10708 | 28-87 | -87.2081 | 28.0243 | 1908.232 | 171.3215 | 198.3618 | 239.7722 | 276.7516 | 319.4362 | 3.815%
10709 | 28-87.5 | -87.4794 | 28.0243 | 1923.6386 | 171.8006 | 198.7424 | 240.13 | 277.0755 | 319.7074 | 3.87%
10710 | 28-88 | -87.7507 | 28.0243 | 1939.0757 | 172.2353 | 199.0978 | 240.4883 | 277.4271 | 320.0418 | 3.919%
10711 | 28-88 | -88.0221 | 28.0243 | 1954.5427 | 172.5819 | 199.3823 | 240.7792 | 277.7167 | 320.3231 | 3.959%
10712 | 28-88.5 | -88.2934 | 28.0243 | 1970.0387 | 172.6532 | 199.4121 | 240.7352 | 277.5963 | 320.1039 | 3.972%
10713 | 28-88.5 | -88.5647 | 28.0243 | 1985.563 | 172.5527 | 199.3209 | 240.5652 | 277.3484 | 319.7587 | 3.965%
10714 | 28-89 | -88.836 | 28.0243 | 2001.1149 | 172.2655 | 199.0869 | 240.2334 | 276.9233 | 319.22 | 3.939%
10715 | 28-89 | -89.1074 | 28.0243 | 2016.6937 | 171.7479 | 198.642 | 239.6313 | 276.1732 | 318.2914 | 3.889%
10716 | 28-89.5 | -89.3787 | 28.0243 | 2032.2987 | 171.102 | 198.1078 | 238.9844 | 275.4127 | 317.3989 | 3.824%
10717 | 28-89.5 | -89.65 | 28.0243 | 2047.9294 | 170.3539 | 197.5009 | 238.2999 | 274.65 | 316.5515 | 3.747%
10718 | 28-90 | -89.9213 | 28.0243 | 2063.585 | 169.5808 | 196.8745 | 237.6181 | 273.9298 | 315.7979 | 3.666%
10719 | 28-90 | -90.1926 | 28.0243 | 2079.2649 | 168.8996 | 196.3319 | 237.0922 | 273.4368 | 315.3611 | 3.593%
10720 | 28-90.5 | -90.464 | 28.0243 | 2094.9685 | 168.206 | 195.7785 | 236.5841 | 272.9911 | 315.0096 | 3.519%
10721 | 28-90.5 | -90.7353 | 28.0243 | 2110.6953 | 167.2954 | 195.0453 | 235.8448 | 272.2665 | 314.3221 | 3.427%
10722 | 28-50 | -50.0371 | 28.2956 | 1118.104 | 112.1498 | 145.7753 | 184.0981 | 208.091 | 235.2117 | 0.7453%
10723 | 28-50.5 | -50.3084 | 28.2956 | 1107.6843 | 113.438 | 147.6256 | 185.29 | 209.5256 | 236.9321 | 0.776%
10724 | 28-50.5 | -50.5797 | 28.2956 | 1097.4391 | 114.76 | 149.5211 | 186.4891 | 210.9546 | 238.6307 | 0.8088%
10725 | 28-51 | -50.851 | 28.2956 | 1087.3735 | 116.1293 | 151.4756 | 187.7127 | 212.4123 | 240.3628 | 0.8442%
10726 | 28-51 | -51.1224 | 28.2956 | 1077.4925 | 117.5778 | 153.5094 | 189.0078 | 213.9725 | 242.2355 | 0.8833%
10727 | 28-51.5 | -51.3937 | 28.2956 | 1067.8012 | 119.0238 | 155.4801 | 190.2536 | 215.4532 | 243.9914 | 0.9237%
10728 | 28-51.5 | -51.665 | 28.2956 | 1058.3049 | 120.4907 | 157.3939 | 191.4854 | 216.909 | 245.7088 | 0.966%
10729 | 28-52 | -51.9363 | 28.2956 | 1049.009 | 122.0071 | 159.2723 | 192.7501 | 218.4102 | 247.4871 | 1.011%
10730 | 28-52 | -52.2077 | 28.2956 | 1039.9187 | 123.4917 | 161.0362 | 193.9351 | 219.7897 | 249.0917 | 1.057%
10731 | 28-52.5 | -52.479 | 28.2956 | 1031.0397 | 124.9668 | 162.7061 | 195.0806 | 221.1165 | 250.6279 | 1.104%
10732 | 28-53 | -52.7503 | 28.2956 | 1022.3773 | 126.4474 | 164.2823 | 196.2186 | 222.4435 | 252.1742 | 1.153%
10733 | 28-53 | -53.0216 | 28.2956 | 1013.9373 | 127.8632 | 165.6934 | 197.2615 | 223.6413 | 253.5496 | 1.202%
10734 | 28-53.5 | -53.2929 | 28.2956 | 1005.7252 | 129.2698 | 167.0089 | 198.2984 | 224.8444 | 254.9452 | 1.251%
10735 | 28-53.5 | -53.5643 | 28.2956 | 997.7467 | 130.6896 | 168.2395 | 199.3657 | 226.1057 | 256.4332 | 1.303%
10736 | 28-54 | -53.8356 | 28.2956 | 990.0075 | 132.0652 | 169.3157 | 200.3662 | 227.2702 | 257.7878 | 1.354%
10737 | 28-54 | -54.1069 | 28.2956 | 982.5131 | 133.482 | 170.3483 | 201.4221 | 228.5148 | 259.253 | 1.409%
10738 | 28-54.5 | -54.3782 | 28.2956 | 975.2694 | 134.9652 | 171.3517 | 202.5674 | 229.8861 | 260.8906 | 1.468%
10739 | 28-54.5 | -54.6495 | 28.2956 | 968.282 | 136.388 | 172.2315 | 203.6383 | 231.1499 | 262.3803 | 1.526%
10740 | 28-55 | -54.9209 | 28.2956 | 961.5564 | 137.8501 | 173.1259 | 204.7797 | 232.5179 | 264.0154 | 1.588%
10741 | 28-55 | -55.1922 | 28.2956 | 955.0982 | 139.3715 | 174.0724 | 206.0156 | 234.0214 | 265.8367 | 1.656%
10742 | 28-55.5 | -55.4635 | 28.2956 | 948.9129 | 140.8195 | 174.9737 | 207.1746 | 235.4174 | 267.5131 | 1.723%
10743 | 28-55.5 | -55.7348 | 28.2956 | 943.0059 | 142.2966 | 175.9049 | 208.3955 | 236.9066 | 269.321 | 1.795%
10744 | 28-56 | -56.0061 | 28.2956 | 937.3825 | 143.8161 | 176.8752 | 209.6875 | 238.498 | 271.2697 | 1.871%
10745 | 28-56.5 | -56.2775 | 28.2956 | 932.0478 | 145.2741 | 177.8043 | 210.904 | 239.9805 | 273.0683 | 1.948%
10746 | 28-56.5 | -56.5488 | 28.2956 | 927.0068 | 146.7601 | 178.7524 | 212.1531 | 241.5089 | 274.929 | 2.029%
10747 | 28-57 | -56.8201 | 28.2956 | 922.2644 | 148.2746 | 179.7183 | 213.4281 | 243.0709 | 276.8328 | 2.114%
10748 | 28-57 | -57.0914 | 28.2956 | 917.8252 | 149.7301 | 180.636 | 214.6135 | 244.5033 | 278.5578 | 2.2%
10749 | 28-57.5 | -57.3628 | 28.2956 | 913.6935 | 151.2029 | 181.559 | 215.8204 | 245.9731 | 280.3405 | 2.29%
10750 | 28-57.5 | -57.6341 | 28.2956 | 909.8738 | 152.6811 | 182.4787 | 217.0316 | 247.4551 | 282.1453 | 2.383%
10751 | 28-58 | -57.9054 | 28.2956 | 906.3698 | 154.0865 | 183.3417 | 218.1602 | 248.8302 | 283.8139 | 2.475%
10752 | 28-58 | -58.1767 | 28.2956 | 903.1853 | 155.5632 | 184.253 | 219.3798 | 250.3383 | 285.6675 | 2.574%
10753 | 28-58.5 | -58.448 | 28.2956 | 900.3236 | 157.063 | 185.1865 | 220.6397 | 251.9043 | 287.6013 | 2.678%
10754 | 28-58.5 | -58.7194 | 28.2956 | 897.7879 | 158.4662 | 186.0723 | 221.821 | 253.3621 | 289.3904 | 2.779%
10755 | 28-59 | -58.9907 | 28.2956 | 895.581 | 159.8874 | 187.0253 | 223.1127 | 254.972 | 291.3833 | 2.885%
10756 | 28-59.5 | -59.262 | 28.2956 | 893.7053 | 161.2703 | 187.9953 | 224.4288 | 256.6137 | 293.4169 | 2.992%
10757 | 28-59.5 | -59.5333 | 28.2956 | 892.1628 | 162.5399 | 188.8901 | 225.6195 | 258.0811 | 295.216 | 3.095%
10758 | 28-60 | -59.8046 | 28.2956 | 890.9554 | 163.7969 | 189.8097 | 226.8567 | 259.6164 | 297.1095 | 3.198%
10759 | 28-60 | -60.076 | 28.2956 | 890.0843 | 164.9867 | 190.7097 | 228.0665 | 261.1169 | 298.9592 | 3.299%
10760 | 28-60.5 | -60.3473 | 28.2956 | 889.5507 | 166.0586 | 191.5318 | 229.1515 | 262.447 | 300.5824 | 3.394%
10761 | 28-60.5 | -60.6186 | 28.2956 | 889.355 | 167.0931 | 192.3591 | 230.2517 | 263.8024 | 302.2436 | 3.488%
10762 | 28-61 | -60.8899 | 28.2956 | 889.4975 | 168.0403 | 193.1584 | 231.3126 | 265.1077 | 303.8417 | 3.575%
10763 | 28-61 | -61.1613 | 28.2956 | 889.9781 | 168.8727 | 193.9051 | 232.2905 | 266.3008 | 305.2917 | 3.656%
10764 | 28-61.5 | -61.4326 | 28.2956 | 890.7962 | 169.6586 | 194.6681 | 233.295 | 267.5305 | 306.7909 | 3.733%
10765 | 28-61.5 | -61.7039 | 28.2956 | 891.9508 | 170.3464 | 195.4112 | 234.2696 | 268.721 | 308.2397 | 3.803%
10766 | 28-62 | -61.9752 | 28.2956 | 893.4407 | 170.9446 | 196.1314 | 235.2108 | 269.8683 | 309.6333 | 3.866%
10767 | 28-62 | -62.2465 | 28.2956 | 895.2642 | 171.5712 | 196.9197 | 236.2663 | 271.1752 | 311.2432 | 3.931%
10768 | 28-62.5 | -62.5179 | 28.2956 | 897.4193 | 172.1952 | 197.7043 | 237.3169 | 272.4764 | 312.8463 | 3.997%
10769 | 28-63 | -62.7892 | 28.2956 | 899.9034 | 172.8153 | 198.4812 | 238.3532 | 273.7567 | 314.4208 | 4.063%
10770 | 28-63 | -63.0605 | 28.2956 | 902.7141 | 173.5085 | 199.3672 | 239.5604 | 275.2683 | 316.3015 | 4.135%
10771 | 28-63.5 | -63.3318 | 28.2956 | 905.848 | 174.2106 | 200.26 | 240.7706 | 276.7789 | 318.1756 | 4.209%
10772 | 28-63.5 | -63.6031 | 28.2956 | 909.3021 | 174.9095 | 201.1412 | 241.954 | 278.2475 | 319.9886 | 4.285%
10773 | 28-64 | -63.8745 | 28.2956 | 913.0725 | 175.6608 | 202.097 | 243.2501 | 279.8654 | 321.996 | 4.366%
10774 | 28-64 | -64.1458 | 28.2956 | 917.1553 | 176.4013 | 203.0273 | 244.4944 | 281.4055 | 323.8925 | 4.448%
10775 | 28-64.5 | -64.4171 | 28.2956 | 921.5465 | 177.1205 | 203.9166 | 245.6631 | 282.8355 | 325.636 | 4.53%
10776 | 28-64.5 | -64.6884 | 28.2956 | 926.2416 | 177.8537 | 204.8193 | 246.8437 | 284.2755 | 327.3864 | 4.615%
10777 | 28-65 | -64.9598 | 28.2956 | 931.236 | 178.5514 | 205.6643 | 247.9278 | 285.5809 | 328.9552 | 4.699%
10778 | 28-65 | -65.2311 | 28.2956 | 936.5249 | 179.219 | 206.4622 | 248.9353 | 286.7811 | 330.3832 | 4.782%
10779 | 28-65.5 | -65.5024 | 28.2956 | 942.1033 | 179.8856 | 207.2572 | 249.9369 | 287.9723 | 331.7984 | 4.865%
10780 | 28-66 | -65.7737 | 28.2956 | 947.966 | 180.4859 | 207.9526 | 250.7817 | 288.9509 | 332.9319 | 4.945%
10781 | 28-66 | -66.045 | 28.2956 | 954.1079 | 181.0457 | 208.5916 | 251.5426 | 289.8192 | 333.9224 | 5.021%
10782 | 28-66.5 | -66.3164 | 28.2956 | 960.5236 | 181.6059 | 209.2382 | 252.3239 | 290.7206 | 334.9623 | 5.098%
10783 | 28-66.5 | -66.5877 | 28.2956 | 967.2075 | 182.0844 | 209.7755 | 252.9493 | 291.4213 | 335.7465 | 5.166%
10784 | 28-67 | -66.859 | 28.2956 | 974.1542 | 182.5301 | 210.2787 | 253.5393 | 292.0863 | 336.4955 | 5.23%
10785 | 28-67 | -67.1303 | 28.2956 | 981.358 | 182.9906 | 210.818 | 254.2035 | 292.8633 | 337.4042 | 5.294%
10786 | 28-67.5 | -67.4016 | 28.2956 | 988.8133 | 183.3778 | 211.2642 | 254.7415 | 293.4829 | 338.1176 | 5.349%
10787 | 28-67.5 | -67.673 | 28.2956 | 996.5144 | 183.7464 | 211.6989 | 255.2812 | 294.1183 | 338.8651 | 5.4%
10788 | 28-68 | -67.9443 | 28.2956 | 1004.4557 | 184.1357 | 212.1784 | 255.9089 | 294.8846 | 339.7975 | 5.45%
10789 | 28-68 | -68.2156 | 28.2956 | 1012.6315 | 184.4707 | 212.5916 | 256.4508 | 295.5468 | 340.6042 | 5.494%
10790 | 28-68.5 | -68.4869 | 28.2956 | 1021.036 | 184.7993 | 213.0028 | 256.9985 | 296.223 | 341.4353 | 5.536%
10791 | 28-69 | -68.7583 | 28.2956 | 1029.6638 | 185.1483 | 213.4469 | 257.6012 | 296.9759 | 342.3703 | 5.579%
10792 | 28-69 | -69.0296 | 28.2956 | 1038.5092 | 185.4168 | 213.7836 | 258.0507 | 297.5318 | 343.0545 | 5.614%
10793 | 28-69.5 | -69.3009 | 28.2956 | 1047.5666 | 185.6687 | 214.1047 | 258.4872 | 298.0778 | 343.7332 | 5.645%
10794 | 28-69.5 | -69.5722 | 28.2956 | 1056.8306 | 185.9292 | 214.445 | 258.9616 | 298.6804 | 344.4922 | 5.676%
10795 | 28-70 | -69.8435 | 28.2956 | 1066.2957 | 186.0827 | 214.6379 | 259.2201 | 299.0008 | 344.8874 | 5.696%
10796 | 28-70 | -70.1149 | 28.2956 | 1075.9567 | 186.2131 | 214.8008 | 259.4367 | 299.2679 | 345.2154 | 5.712%
10797 | 28-70.5 | -70.3862 | 28.2956 | 1085.8082 | 186.3385 | 214.9579 | 259.6463 | 299.527 | 345.5343 | 5.729%
10798 | 28-70.5 | -70.6575 | 28.2956 | 1095.8452 | 186.3644 | 214.9698 | 259.6321 | 299.4856 | 345.4576 | 5.736%
10799 | 28-71 | -70.9288 | 28.2956 | 1106.0625 | 186.3826 | 214.9678 | 259.5928 | 299.4082 | 345.3314 | 5.743%
10800 | 28-71 | -71.2001 | 28.2956 | 1116.455 | 186.404 | 214.9662 | 259.549 | 299.3212 | 345.189 | 5.752%
10801 | 28-71.5 | -71.4715 | 28.2956 | 1127.0181 | 186.3635 | 214.8741 | 259.3657 | 299.0469 | 344.8003 | 5.755%
10802 | 28-71.5 | -71.7428 | 28.2956 | 1137.7468 | 186.3388 | 214.8042 | 259.2151 | 298.8157 | 344.4675 | 5.759%
10803 | 28-72 | -72.0141 | 28.2956 | 1148.6365 | 186.3267 | 214.7504 | 259.0869 | 298.6128 | 344.1702 | 5.765%
10804 | 28-72.5 | -72.2854 | 28.2956 | 1159.6827 | 186.2464 | 214.5977 | 258.8068 | 298.2065 | 343.6057 | 5.765%
10805 | 28-72.5 | -72.5568 | 28.2956 | 1170.8807 | 186.1973 | 214.4829 | 258.5756 | 297.8595 | 343.113 | 5.769%
10806 | 28-73 | -72.8281 | 28.2956 | 1182.2265 | 186.1639 | 214.3845 | 258.3616 | 297.5298 | 342.6376 | 5.776%
10807 | 28-73 | -73.0994 | 28.2956 | 1193.7155 | 186.0732 | 214.2017 | 258.0162 | 297.0232 | 341.9287 | 5.779%
10808 | 28-73.5 | -73.3707 | 28.2956 | 1205.3438 | 186.0396 | 214.1002 | 257.7942 | 296.6805 | 341.434 | 5.786%
10809 | 28-73.5 | -73.642 | 28.2956 | 1217.1073 | 186.0294 | 214.036 | 257.6331 | 296.4223 | 341.0529 | 5.795%
10810 | 28-74 | -73.9134 | 28.2956 | 1229.0021 | 185.9584 | 213.892 | 257.3604 | 296.022 | 340.4926 | 5.797%
10811 | 28-74 | -74.1847 | 28.2956 | 1241.0243 | 185.9182 | 213.8032 | 257.186 | 295.7625 | 340.1264 | 5.8%
10812 | 28-74.5 | -74.456 | 28.2956 | 1253.1703 | 185.8729 | 213.7201 | 257.0366 | 295.5477 | 339.83 | 5.799%
10813 | 28-74.5 | -74.7273 | 28.2956 | 1265.4365 | 185.7605 | 213.5564 | 256.7849 | 295.2106 | 339.3875 | 5.789%
10814 | 28-75 | -74.9986 | 28.2956 | 1277.8193 | 185.6439 | 213.3996 | 256.5604 | 294.9211 | 339.0186 | 5.776%
10815 | 28-75.5 | -75.27 | 28.2956 | 1290.3154 | 185.4848 | 213.1975 | 256.2867 | 294.5797 | 338.5953 | 5.755%
10816 | 28-75.5 | -75.5413 | 28.2956 | 1302.9214 | 185.2324 | 212.8821 | 255.8674 | 294.0628 | 337.9609 | 5.721%
10817 | 28-76 | -75.8126 | 28.2956 | 1315.6342 | 184.9629 | 212.5627 | 255.468 | 293.5904 | 337.4024 | 5.682%
10818 | 28-76 | -76.0839 | 28.2956 | 1328.4507 | 184.6384 | 212.1877 | 255.014 | 293.0656 | 336.7959 | 5.633%
10819 | 28-76.5 | -76.3553 | 28.2956 | 1341.3678 | 184.2237 | 211.7091 | 254.4354 | 292.3976 | 336.0245 | 5.571%
10820 | 28-76.5 | -76.6266 | 28.2956 | 1354.3826 | 183.7875 | 211.2227 | 253.8744 | 291.7732 | 335.3304 | 5.502%
10821 | 28-77 | -76.8979 | 28.2956 | 1367.4923 | 183.2921 | 210.6713 | 253.24 | 291.0688 | 334.549 | 5.425%
10822 | 28-77 | -77.1692 | 28.2956 | 1380.6941 | 182.7243 | 210.0318 | 252.4921 | 290.2272 | 333.6023 | 5.34%
10823 | 28-77.5 | -77.4405 | 28.2956 | 1393.9855 | 182.1686 | 209.4246 | 251.8122 | 289.4891 | 332.8039 | 5.254%
10824 | 28-77.5 | -77.7119 | 28.2956 | 1407.3637 | 181.5709 | 208.7667 | 251.0675 | 288.6734 | 331.9125 | 5.164%
10825 | 28-78 | -77.9832 | 28.2956 | 1420.8263 | 180.9102 | 208.0231 | 250.1987 | 287.6966 | 330.8148 | 5.069%
10826 | 28-78.5 | -78.2545 | 28.2956 | 1434.371 | 180.2509 | 207.2888 | 249.3535 | 286.7576 | 329.7729 | 4.974%
10827 | 28-78.5 | -78.5258 | 28.2956 | 1447.9952 | 179.387 | 206.2903 | 248.1445 | 285.3605 | 328.1585 | 4.858%
10828 | 28-79 | -78.7971 | 28.2956 | 1461.6969 | 178.1582 | 204.8679 | 246.3498 | 283.2245 | 325.62 | 4.703%
10829 | 28-79 | -79.0685 | 28.2956 | 1475.4737 | 176.399 | 203.1106 | 244.1094 | 280.5399 | 322.4099 | 4.494%
10830 | 28-79.5 | -79.3398 | 28.2956 | 1489.3235 | 174.2936 | 201.1031 | 241.5268 | 277.4264 | 318.6668 | 4.257%
10831 | 28-79.5 | -79.6111 | 28.2956 | 1503.2443 | 171.9291 | 198.9428 | 238.7312 | 274.0429 | 314.5846 | 4.004%
10832 | 28-80 | -79.8824 | 28.2956 | 1517.2341 | 169.3855 | 196.6994 | 235.8331 | 270.5393 | 310.3618 | 3.746%
10833 | 28-80 | -80.1537 | 28.2956 | 1531.291 | 166.5477 | 194.2605 | 232.6617 | 266.6887 | 305.7025 | 3.477%
10834 | 28-80.5 | -80.4251 | 28.2956 | 1545.413 | 163.4167 | 191.6222 | 229.2166 | 262.4941 | 300.6146 | 3.199%
10835 | 28-80.5 | -80.6964 | 28.2956 | 1559.5983 | 160.0575 | 188.7509 | 225.5965 | 258.0945 | 295.2864 | 2.918%
10836 | 28-81 | -80.9677 | 28.2956 | 1573.8453 | 157.1244 | 186.2313 | 222.3883 | 254.1918 | 290.5554 | 2.691%
10837 | 28-81 | -81.239 | 28.2956 | 1588.1521 | 154.971 | 184.3362 | 219.9804 | 251.284 | 287.0525 | 2.532%
10838 | 28-81.5 | -81.5104 | 28.2956 | 1602.5171 | 153.6265 | 183.1428 | 218.5217 | 249.5803 | 285.0633 | 2.434%
10839 | 28-82 | -81.7817 | 28.2956 | 1616.9388 | 152.5185 | 182.1832 | 217.3716 | 248.2615 | 283.5511 | 2.357%
10840 | 28-82 | -82.053 | 28.2956 | 1631.4156 | 151.7346 | 181.5963 | 216.7438 | 247.6075 | 282.8773 | 2.304%
10841 | 28-82.5 | -82.3243 | 28.2956 | 1645.946 | 151.4828 | 181.5927 | 216.9416 | 248.0104 | 283.542 | 2.287%
10842 | 28-82.5 | -82.5956 | 28.2956 | 1660.5284 | 151.8128 | 181.9928 | 217.6809 | 249.0836 | 285.0312 | 2.306%
10843 | 28-83 | -82.867 | 28.2956 | 1675.1616 | 152.5112 | 182.6781 | 218.8102 | 250.6457 | 287.1288 | 2.348%
10844 | 28-83 | -83.1383 | 28.2956 | 1689.8442 | 153.5378 | 183.6048 | 220.2851 | 252.6535 | 289.7943 | 2.411%
10845 | 28-83.5 | -83.4096 | 28.2956 | 1704.5748 | 154.8025 | 184.6713 | 221.9067 | 254.8108 | 292.6096 | 2.49%
10846 | 28-83.5 | -83.6809 | 28.2956 | 1719.3521 | 156.42 | 185.9766 | 223.823 | 257.3131 | 295.8283 | 2.594%
10847 | 28-84 | -83.9522 | 28.2956 | 1734.1749 | 158.4357 | 187.5797 | 226.1249 | 260.2824 | 299.6107 | 2.729%
10848 | 28-84 | -84.2236 | 28.2956 | 1749.042 | 160.7548 | 189.4864 | 228.6619 | 263.5042 | 303.6627 | 2.896%
10849 | 28-84.5 | -84.4949 | 28.2956 | 1763.9523 | 162.7269 | 191.1089 | 230.8456 | 266.2765 | 307.1494 | 3.043%
10850 | 28-85 | -84.7662 | 28.2956 | 1778.9045 | 164.0655 | 192.2658 | 232.4395 | 268.3135 | 309.7263 | 3.145%
10851 | 28-85 | -85.0375 | 28.2956 | 1793.8976 | 164.6946 | 192.8357 | 233.2291 | 269.3186 | 310.9942 | 3.194%
10852 | 28-85.5 | -85.3089 | 28.2956 | 1808.9305 | 165.195 | 193.2839 | 233.8485 | 270.1013 | 311.9758 | 3.234%
10853 | 28-85.5 | -85.5802 | 28.2956 | 1824.0022 | 165.6941 | 193.7457 | 234.4742 | 270.8826 | 312.9458 | 3.275%
10854 | 28-86 | -85.8515 | 28.2956 | 1839.1117 | 166.1015 | 194.0956 | 234.8849 | 271.3458 | 313.4681 | 3.311%
10855 | 28-86 | -86.1228 | 28.2956 | 1854.258 | 166.6041 | 194.5081 | 235.3412 | 271.8357 | 313.9912 | 3.357%
10856 | 28-86.5 | -86.3941 | 28.2956 | 1869.4402 | 167.2281 | 195.0074 | 235.8738 | 272.3884 | 314.5575 | 3.417%
10857 | 28-86.5 | -86.6655 | 28.2956 | 1884.6573 | 167.808 | 195.4403 | 236.2704 | 272.7355 | 314.8304 | 3.475%
10858 | 28-87 | -86.9368 | 28.2956 | 1899.9085 | 168.4103 | 195.9085 | 236.7194 | 273.1519 | 315.1936 | 3.537%
10859 | 28-87 | -87.2081 | 28.2956 | 1915.1928 | 169.024 | 196.4053 | 237.213 | 273.6285 | 315.6365 | 3.601%
10860 | 28-87.5 | -87.4794 | 28.2956 | 1930.5095 | 169.5405 | 196.8061 | 237.584 | 273.958 | 315.9032 | 3.657%
10861 | 28-88 | -87.7507 | 28.2956 | 1945.8577 | 170.0279 | 197.194 | 237.9727 | 274.337 | 316.2604 | 3.71%
10862 | 28-88 | -88.0221 | 28.2956 | 1961.2366 | 170.433 | 197.5179 | 238.304 | 274.667 | 316.5811 | 3.753%
10863 | 28-88.5 | -88.2934 | 28.2956 | 1976.6456 | 170.5246 | 197.5682 | 238.275 | 274.5556 | 316.3629 | 3.768%
10864 | 28-88.5 | -88.5647 | 28.2956 | 1992.0837 | 170.4011 | 197.4671 | 238.0764 | 274.2603 | 315.9466 | 3.761%
10865 | 28-89 | -88.836 | 28.2956 | 2007.5503 | 170.0517 | 197.1952 | 237.675 | 273.7345 | 315.2687 | 3.731%
10866 | 28-89 | -89.1074 | 28.2956 | 2023.0447 | 169.4445 | 196.6772 | 236.9787 | 272.8514 | 314.1592 | 3.676%
10867 | 28-89.5 | -89.3787 | 28.2956 | 2038.5662 | 168.6633 | 196.0199 | 236.1888 | 271.8951 | 313.0058 | 3.601%
10868 | 28-89.5 | -89.65 | 28.2956 | 2054.1141 | 167.7496 | 195.2682 | 235.3313 | 270.8977 | 311.8474 | 3.514%
10869 | 28-90 | -89.9213 | 28.2956 | 2069.6878 | 166.8287 | 194.5488 | 234.5029 | 269.9764 | 310.8253 | 3.426%
10870 | 28-90 | -90.1926 | 28.2956 | 2085.2866 | 166.0704 | 193.9666 | 233.9065 | 269.3823 | 310.249 | 3.353%
10871 | 28-90.5 | -90.464 | 28.2956 | 2100.91 | 165.3417 | 193.406 | 233.3785 | 268.9038 | 309.8484 | 3.281%
10872 | 28-90.5 | -90.7353 | 28.2956 | 2116.5573 | 164.3773 | 192.6572 | 232.6141 | 268.1447 | 309.1148 | 3.192%
10873 | 29-50 | -50.0371 | 28.567 | 1132.6248 | 112.6215 | 146.3092 | 184.3952 | 208.4233 | 235.5833 | 0.7546%
10874 | 29-50.5 | -50.3084 | 28.567 | 1122.3628 | 113.8534 | 148.0775 | 185.5403 | 209.8074 | 237.2493 | 0.7845%
10875 | 29-50.5 | -50.5797 | 28.567 | 1112.2753 | 115.1191 | 149.8903 | 186.6912 | 211.1828 | 238.8884 | 0.8163%
10876 | 29-51 | -50.851 | 28.567 | 1102.3673 | 116.4347 | 151.7661 | 187.8677 | 212.5858 | 240.5569 | 0.8507%
10877 | 29-51 | -51.1224 | 28.567 | 1092.6435 | 117.8331 | 153.7338 | 189.1178 | 214.0914 | 242.3636 | 0.8888%
10878 | 29-51.5 | -51.3937 | 28.567 | 1083.109 | 119.2385 | 155.6477 | 190.3255 | 215.5233 | 244.0579 | 0.9283%
10879 | 29-51.5 | -51.665 | 28.567 | 1073.7689 | 120.676 | 157.5158 | 191.5284 | 216.94 | 245.7237 | 0.97%
10880 | 29-52 | -51.9363 | 28.567 | 1064.6283 | 122.1746 | 159.3597 | 192.774 | 218.4134 | 247.4634 | 1.015%
10881 | 29-52 | -52.2077 | 28.567 | 1055.6924 | 123.6517 | 161.099 | 193.9482 | 219.7754 | 249.0423 | 1.061%
10882 | 29-52.5 | -52.479 | 28.567 | 1046.9665 | 125.13 | 162.755 | 195.0912 | 221.0938 | 250.5626 | 1.108%
10883 | 29-53 | -52.7503 | 28.567 | 1038.4559 | 126.6249 | 164.329 | 196.2343 | 222.4196 | 252.0997 | 1.158%
10884 | 29-53 | -53.0216 | 28.567 | 1030.1661 | 128.0653 | 165.7493 | 197.2898 | 223.624 | 253.4738 | 1.207%
10885 | 29-53.5 | -53.2929 | 28.567 | 1022.1023 | 129.5062 | 167.0853 | 198.3467 | 224.8418 | 254.8767 | 1.258%
10886 | 29-53.5 | -53.5643 | 28.567 | 1014.27 | 130.9697 | 168.3476 | 199.4415 | 226.1262 | 256.3819 | 1.311%
10887 | 29-54 | -53.8356 | 28.567 | 1006.6746 | 132.3984 | 169.4665 | 200.4758 | 227.3205 | 257.7609 | 1.365%
10888 | 29-54 | -54.1069 | 28.567 | 999.3216 | 133.8722 | 170.5445 | 201.5673 | 228.5978 | 259.2542 | 1.423%
10889 | 29-54.5 | -54.3782 | 28.567 | 992.2164 | 135.4137 | 171.5923 | 202.7485 | 230.0025 | 260.9214 | 1.485%
10890 | 29-54.5 | -54.6495 | 28.567 | 985.3643 | 136.894 | 172.5075 | 203.8531 | 231.2978 | 262.4388 | 1.547%
10891 | 29-55 | -54.9209 | 28.567 | 978.7708 | 138.4066 | 173.4307 | 205.021 | 232.689 | 264.0927 | 1.612%
10892 | 29-55 | -55.1922 | 28.567 | 972.4409 | 139.9692 | 174.3983 | 206.2742 | 234.2057 | 265.9213 | 1.683%
10893 | 29-55.5 | -55.4635 | 28.567 | 966.3801 | 141.4464 | 175.3119 | 207.4419 | 235.6064 | 267.597 | 1.753%
10894 | 29-55.5 | -55.7348 | 28.567 | 960.5934 | 142.9418 | 176.248 | 208.6635 | 237.0919 | 269.3957 | 1.827%
10895 | 29-56 | -56.0061 | 28.567 | 955.0857 | 144.4691 | 177.2161 | 209.9484 | 238.6713 | 271.326 | 1.905%
10896 | 29-56.5 | -56.2775 | 28.567 | 949.862 | 145.9259 | 178.1374 | 211.1527 | 240.1374 | 273.1028 | 1.983%
10897 | 29-56.5 | -56.5488 | 28.567 | 944.927 | 147.4033 | 179.0731 | 212.3844 | 241.6434 | 274.9352 | 2.066%
10898 | 29-57 | -56.8201 | 28.567 | 940.2852 | 148.9014 | 180.0218 | 213.6358 | 243.1757 | 276.802 | 2.152%
10899 | 29-57 | -57.0914 | 28.567 | 935.9411 | 150.3276 | 180.9145 | 214.7874 | 244.5658 | 278.4746 | 2.238%
10900 | 29-57.5 | -57.3628 | 28.567 | 931.8987 | 151.7583 | 181.8055 | 215.9518 | 245.9834 | 280.193 | 2.327%
10901 | 29-57.5 | -57.6341 | 28.567 | 928.1621 | 153.1829 | 182.6872 | 217.113 | 247.4041 | 281.923 | 2.418%
10902 | 29-58 | -57.9054 | 28.567 | 924.735 | 154.5264 | 183.5074 | 218.1852 | 248.71 | 283.5069 | 2.507%
10903 | 29-58 | -58.1767 | 28.567 | 921.6208 | 155.9374 | 184.373 | 219.3452 | 250.1453 | 285.2721 | 2.604%
10904 | 29-58.5 | -58.448 | 28.567 | 918.8228 | 157.3745 | 185.2612 | 220.5477 | 251.6429 | 287.1241 | 2.705%
10905 | 29-58.5 | -58.7194 | 28.567 | 916.3438 | 158.7197 | 186.1091 | 221.6848 | 253.0507 | 288.8566 | 2.803%
10906 | 29-59 | -58.9907 | 28.567 | 914.1864 | 160.0909 | 187.0333 | 222.9457 | 254.6284 | 290.816 | 2.906%
10907 | 29-59.5 | -59.262 | 28.567 | 912.353 | 161.432 | 187.9835 | 224.2445 | 256.2557 | 292.8391 | 3.011%
10908 | 29-59.5 | -59.5333 | 28.567 | 910.8455 | 162.6673 | 188.8661 | 225.4291 | 257.7234 | 294.6468 | 3.111%
10909 | 29-60 | -59.8046 | 28.567 | 909.6654 | 163.8961 | 189.7796 | 226.6688 | 259.2697 | 296.5622 | 3.213%
10910 | 29-60 | -60.076 | 28.567 | 908.8142 | 165.0622 | 190.6775 | 227.8858 | 260.7868 | 298.4404 | 3.312%
10911 | 29-60.5 | -60.3473 | 28.567 | 908.2927 | 166.1136 | 191.4986 | 228.9779 | 262.1324 | 300.0895 | 3.405%
10912 | 29-60.5 | -60.6186 | 28.567 | 908.1015 | 167.1366 | 192.3291 | 230.0898 | 263.5078 | 301.7812 | 3.498%
10913 | 29-61 | -60.8899 | 28.567 | 908.2407 | 168.0809 | 193.1353 | 231.1655 | 264.8357 | 303.4115 | 3.586%
10914 | 29-61 | -61.1613 | 28.567 | 908.7104 | 168.918 | 193.8914 | 232.1596 | 266.0516 | 304.8925 | 3.667%
10915 | 29-61.5 | -61.4326 | 28.567 | 909.5098 | 169.7135 | 194.6651 | 233.181 | 267.3042 | 306.4218 | 3.745%
10916 | 29-61.5 | -61.7039 | 28.567 | 910.6383 | 170.4132 | 195.4198 | 234.1721 | 268.5159 | 307.8973 | 3.817%
10917 | 29-62 | -61.9752 | 28.567 | 912.0944 | 171.0196 | 196.1496 | 235.1252 | 269.6768 | 309.3067 | 3.881%
10918 | 29-62 | -62.2465 | 28.567 | 913.8768 | 171.6496 | 196.9394 | 236.1785 | 270.9778 | 310.9056 | 3.947%
10919 | 29-62.5 | -62.5179 | 28.567 | 915.9834 | 172.2717 | 197.7174 | 237.214 | 272.2552 | 312.4742 | 4.013%
10920 | 29-63 | -62.7892 | 28.567 | 918.412 | 172.8848 | 198.4803 | 238.2239 | 273.4969 | 313.9946 | 4.079%
10921 | 29-63 | -63.0605 | 28.567 | 921.1601 | 173.5668 | 199.3465 | 239.3963 | 274.959 | 315.807 | 4.151%
10922 | 29-63.5 | -63.3318 | 28.567 | 924.2248 | 174.2542 | 200.2144 | 240.5638 | 276.4092 | 317.5989 | 4.225%
10923 | 29-63.5 | -63.6031 | 28.567 | 927.6029 | 174.9366 | 201.0681 | 241.7008 | 277.8126 | 319.3235 | 4.3%
10924 | 29-64 | -63.8745 | 28.567 | 931.2911 | 175.6718 | 201.9977 | 242.9529 | 279.3692 | 321.2478 | 4.381%
10925 | 29-64 | -64.1458 | 28.567 | 935.2857 | 176.3977 | 202.9044 | 244.1578 | 280.8542 | 323.0697 | 4.462%
10926 | 29-64.5 | -64.4171 | 28.567 | 939.5827 | 177.1048 | 203.774 | 245.2936 | 282.2384 | 324.7512 | 4.544%
10927 | 29-64.5 | -64.6884 | 28.567 | 944.1779 | 177.8283 | 204.6618 | 246.4498 | 283.6447 | 326.4564 | 4.629%
10928 | 29-65 | -64.9598 | 28.567 | 949.0672 | 178.5183 | 205.4957 | 247.5171 | 284.9277 | 327.9959 | 4.713%
10929 | 29-65 | -65.2311 | 28.567 | 954.2458 | 179.1794 | 206.2858 | 248.5148 | 286.1162 | 329.4099 | 4.795%
10930 | 29-65.5 | -65.5024 | 28.567 | 959.7092 | 179.8406 | 207.076 | 249.513 | 287.3054 | 330.8249 | 4.879%
10931 | 29-66 | -65.7737 | 28.567 | 965.4524 | 180.4363 | 207.7687 | 250.3581 | 288.2876 | 331.9662 | 4.957%
10932 | 29-66 | -66.045 | 28.567 | 971.4705 | 180.9925 | 208.4061 | 251.1213 | 289.162 | 332.968 | 5.034%
10933 | 29-66.5 | -66.3164 | 28.567 | 977.7584 | 181.55 | 209.0521 | 251.9059 | 290.0709 | 334.0205 | 5.11%
10934 | 29-66.5 | -66.5877 | 28.567 | 984.3108 | 182.0273 | 209.5904 | 252.5365 | 290.7809 | 334.8193 | 5.178%
10935 | 29-67 | -66.859 | 28.567 | 991.1226 | 182.473 | 210.0965 | 253.1344 | 291.4588 | 335.5874 | 5.242%
10936 | 29-67 | -67.1303 | 28.567 | 998.1884 | 182.9349 | 210.6406 | 253.8095 | 292.2529 | 336.5208 | 5.305%
10937 | 29-67.5 | -67.4016 | 28.567 | 1005.5029 | 183.3238 | 211.092 | 254.3587 | 292.8896 | 337.2588 | 5.36%
10938 | 29-67.5 | -67.673 | 28.567 | 1013.0605 | 183.6935 | 211.5306 | 254.9077 | 293.5396 | 338.0275 | 5.411%
10939 | 29-68 | -67.9443 | 28.567 | 1020.8559 | 184.0825 | 212.0124 | 255.5422 | 294.317 | 338.9767 | 5.462%
10940 | 29-68 | -68.2156 | 28.567 | 1028.8837 | 184.4151 | 212.4246 | 256.0854 | 294.9829 | 339.79 | 5.505%
10941 | 29-68.5 | -68.4869 | 28.567 | 1037.1384 | 184.7408 | 212.8331 | 256.6309 | 295.6574 | 340.6201 | 5.546%
10942 | 29-69 | -68.7583 | 28.567 | 1045.6146 | 185.0869 | 213.274 | 257.2296 | 296.4058 | 341.5496 | 5.589%
10943 | 29-69 | -69.0296 | 28.567 | 1054.307 | 185.353 | 213.607 | 257.6733 | 296.9536 | 342.2229 | 5.624%
10944 | 29-69.5 | -69.3009 | 28.567 | 1063.2102 | 185.603 | 213.9245 | 258.1031 | 297.4898 | 342.888 | 5.655%
10945 | 29-69.5 | -69.5722 | 28.567 | 1072.319 | 185.862 | 214.2613 | 258.5703 | 298.0814 | 343.631 | 5.686%
10946 | 29-70 | -69.8435 | 28.567 | 1081.6281 | 186.0178 | 214.4562 | 258.8301 | 298.4022 | 344.0254 | 5.707%
10947 | 29-70 | -70.1149 | 28.567 | 1091.1324 | 186.1541 | 214.6264 | 259.0565 | 298.6814 | 344.3682 | 5.725%
10948 | 29-70.5 | -70.3862 | 28.567 | 1100.8267 | 186.2882 | 214.7954 | 259.2832 | 298.9626 | 344.7153 | 5.742%
10949 | 29-70.5 | -70.6575 | 28.567 | 1110.7062 | 186.3229 | 214.8188 | 259.2849 | 298.9414 | 344.6641 | 5.75%
10950 | 29-71 | -70.9288 | 28.567 | 1120.7658 | 186.351 | 214.8296 | 259.2635 | 298.8867 | 344.5665 | 5.759%
10951 | 29-71 | -71.2001 | 28.567 | 1131.0007 | 186.3836 | 214.8425 | 259.2398 | 298.8252 | 344.4561 | 5.769%
10952 | 29-71.5 | -71.4715 | 28.567 | 1141.4062 | 186.3529 | 214.7628 | 259.0732 | 298.5717 | 344.0933 | 5.773%
10953 | 29-71.5 | -71.7428 | 28.567 | 1151.9776 | 186.338 | 214.7049 | 258.9385 | 298.3601 | 343.7846 | 5.779%
10954 | 29-72 | -72.0141 | 28.567 | 1162.7103 | 186.3349 | 214.6619 | 258.8239 | 298.1736 | 343.507 | 5.786%
10955 | 29-72.5 | -72.2854 | 28.567 | 1173.6 | 186.2603 | 214.5156 | 258.5513 | 297.7758 | 342.9523 | 5.787%
10956 | 29-72.5 | -72.5568 | 28.567 | 1184.6421 | 186.2139 | 214.4033 | 258.3224 | 297.4307 | 342.4613 | 5.792%
10957 | 29-73 | -72.8281 | 28.567 | 1195.8325 | 186.1806 | 214.3047 | 258.1075 | 297.0996 | 341.9836 | 5.799%
10958 | 29-73 | -73.0994 | 28.567 | 1207.1671 | 186.0885 | 214.1208 | 257.7619 | 296.5938 | 341.2769 | 5.801%
10959 | 29-73.5 | -73.3707 | 28.567 | 1218.6417 | 186.049 | 214.0123 | 257.5311 | 296.2408 | 340.7703 | 5.808%
10960 | 29-73.5 | -73.642 | 28.567 | 1230.2523 | 186.0282 | 213.9349 | 257.3526 | 295.9612 | 340.363 | 5.816%
10961 | 29-74 | -73.9134 | 28.567 | 1241.9953 | 185.9419 | 213.772 | 257.0553 | 295.531 | 339.7667 | 5.816%
10962 | 29-74 | -74.1847 | 28.567 | 1253.8667 | 185.8838 | 213.6626 | 256.8561 | 295.2431 | 339.368 | 5.816%
10963 | 29-74.5 | -74.456 | 28.567 | 1265.8629 | 185.8173 | 213.5563 | 256.6808 | 295.0002 | 339.0412 | 5.811%
10964 | 29-74.5 | -74.7273 | 28.567 | 1277.9804 | 185.6803 | 213.3669 | 256.4023 | 294.6359 | 338.5715 | 5.797%
10965 | 29-75 | -74.9986 | 28.567 | 1290.2158 | 185.5374 | 213.1844 | 256.1537 | 294.3248 | 338.1849 | 5.778%
10966 | 29-75.5 | -75.27 | 28.567 | 1302.5656 | 185.3488 | 212.9542 | 255.8559 | 293.964 | 337.7488 | 5.752%
10967 | 29-75.5 | -75.5413 | 28.567 | 1315.0266 | 185.0636 | 212.6082 | 255.411 | 293.4275 | 337.1032 | 5.712%
10968 | 29-76 | -75.8126 | 28.567 | 1327.5956 | 184.7601 | 212.2577 | 254.987 | 292.9378 | 336.5377 | 5.665%
10969 | 29-76 | -76.0839 | 28.567 | 1340.2696 | 184.4018 | 211.8527 | 254.5108 | 292.3998 | 335.9299 | 5.609%
10970 | 29-76.5 | -76.3553 | 28.567 | 1353.0455 | 183.9551 | 211.3468 | 253.9148 | 291.725 | 335.1662 | 5.54%
10971 | 29-76.5 | -76.6266 | 28.567 | 1365.9205 | 183.4878 | 210.8347 | 253.3386 | 291.097 | 334.4837 | 5.466%
10972 | 29-77 | -76.8979 | 28.567 | 1378.8917 | 182.9613 | 210.2572 | 252.6885 | 290.3881 | 333.7127 | 5.383%
10973 | 29-77 | -77.1692 | 28.567 | 1391.9564 | 182.3608 | 209.5889 | 251.9197 | 289.5344 | 332.766 | 5.292%
10974 | 29-77.5 | -77.4405 | 28.567 | 1405.112 | 181.7714 | 208.9496 | 251.2121 | 288.7741 | 331.9529 | 5.201%
10975 | 29-77.5 | -77.7119 | 28.567 | 1418.3559 | 181.1396 | 208.2578 | 250.4351 | 287.9285 | 331.0357 | 5.106%
10976 | 29-78 | -77.9832 | 28.567 | 1431.6855 | 180.445 | 207.4791 | 249.5303 | 286.9157 | 329.9027 | 5.006%
10977 | 29-78.5 | -78.2545 | 28.567 | 1445.0986 | 179.7518 | 206.7083 | 248.6447 | 285.9335 | 328.8148 | 4.907%
10978 | 29-78.5 | -78.5258 | 28.567 | 1458.5926 | 178.8734 | 205.697 | 247.4266 | 284.5312 | 327.2005 | 4.79%
10979 | 29-79 | -78.7971 | 28.567 | 1472.1654 | 177.6644 | 204.3051 | 245.681 | 282.4624 | 324.7515 | 4.638%
10980 | 29-79 | -79.0685 | 28.567 | 1485.8148 | 175.9856 | 202.622 | 243.5485 | 279.9179 | 321.7209 | 4.439%
10981 | 29-79.5 | -79.3398 | 28.567 | 1499.5385 | 173.944 | 200.6795 | 241.0618 | 276.9298 | 318.1392 | 4.21%
10982 | 29-79.5 | -79.6111 | 28.567 | 1513.3346 | 171.5791 | 198.5417 | 238.3062 | 273.6033 | 314.1349 | 3.96%
10983 | 29-80 | -79.8824 | 28.567 | 1527.2011 | 168.9727 | 196.2769 | 235.3904 | 270.0864 | 309.9047 | 3.698%
10984 | 29-80 | -80.1537 | 28.567 | 1541.1359 | 166.0169 | 193.7781 | 232.1509 | 266.1608 | 305.163 | 3.421%
10985 | 29-80.5 | -80.4251 | 28.567 | 1555.1373 | 162.7151 | 191.0395 | 228.5926 | 261.8364 | 299.926 | 3.133%
10986 | 29-80.5 | -80.6964 | 28.567 | 1569.2033 | 159.1473 | 188.0263 | 224.8172 | 257.2562 | 294.3881 | 2.842%
10987 | 29-81 | -80.9677 | 28.567 | 1583.3323 | 155.9934 | 185.3488 | 221.4355 | 253.1504 | 289.4192 | 2.604%
10988 | 29-81 | -81.239 | 28.567 | 1597.5224 | 153.6142 | 183.29 | 218.8432 | 250.0247 | 285.6593 | 2.434%
10989 | 29-81.5 | -81.5104 | 28.567 | 1611.7721 | 152.0397 | 181.9282 | 217.1874 | 248.0862 | 283.3908 | 2.326%
10990 | 29-82 | -81.7817 | 28.567 | 1626.0797 | 150.7117 | 180.8148 | 215.851 | 246.5459 | 281.6155 | 2.238%
10991 | 29-82 | -82.053 | 28.567 | 1640.4437 | 149.704 | 180.0681 | 215.0197 | 245.6481 | 280.6501 | 2.174%
10992 | 29-82.5 | -82.3243 | 28.567 | 1654.8625 | 149.2114 | 179.8735 | 214.9704 | 245.7519 | 280.9536 | 2.145%
10993 | 29-82.5 | -82.5956 | 28.567 | 1669.3347 | 149.2447 | 180.0442 | 215.4078 | 246.4556 | 281.9924 | 2.146%
10994 | 29-83 | -82.867 | 28.567 | 1683.8588 | 149.6654 | 180.5116 | 216.2474 | 247.6605 | 283.652 | 2.17%
10995 | 29-83 | -83.1383 | 28.567 | 1698.4335 | 150.4801 | 181.2623 | 217.4849 | 249.373 | 285.9525 | 2.216%
10996 | 29-83.5 | -83.4096 | 28.567 | 1713.0574 | 151.5948 | 182.1976 | 218.9252 | 251.3017 | 288.4817 | 2.281%
10997 | 29-83.5 | -83.6809 | 28.567 | 1727.7292 | 153.1175 | 183.4101 | 220.7084 | 253.6324 | 291.4816 | 2.373%
10998 | 29-84 | -83.9522 | 28.567 | 1742.4477 | 155.0931 | 184.9615 | 222.9223 | 256.484 | 295.1096 | 2.496%
10999 | 29-84 | -84.2236 | 28.567 | 1757.2116 | 157.3984 | 186.8511 | 225.4019 | 259.6229 | 299.0468 | 2.65%
11000 | 29-84.5 | -84.4949 | 28.567 | 1772.0198 | 159.3571 | 188.4616 | 227.5327 | 262.3169 | 302.4232 | 2.787%
11001 | 29-85 | -84.7662 | 28.567 | 1786.8711 | 160.6757 | 189.596 | 229.0693 | 264.2697 | 304.8824 | 2.881%
11002 | 29-85 | -85.0375 | 28.567 | 1801.7644 | 161.2931 | 190.1551 | 229.8214 | 265.2166 | 306.066 | 2.927%
11003 | 29-85.5 | -85.3089 | 28.567 | 1816.6986 | 161.7778 | 190.5876 | 230.4005 | 265.938 | 306.9599 | 2.964%
11004 | 29-85.5 | -85.5802 | 28.567 | 1831.6727 | 162.2549 | 191.0241 | 230.9784 | 266.6492 | 307.8319 | 3.001%
11005 | 29-86 | -85.8515 | 28.567 | 1846.6855 | 162.6746 | 191.3784 | 231.3837 | 267.0971 | 308.326 | 3.036%
11006 | 29-86 | -86.1228 | 28.567 | 1861.7363 | 163.2406 | 191.8333 | 231.8914 | 267.6462 | 308.9174 | 3.083%
11007 | 29-86.5 | -86.3941 | 28.567 | 1876.8239 | 163.9768 | 192.4099 | 232.528 | 268.3282 | 309.6437 | 3.146%
11008 | 29-86.5 | -86.6655 | 28.567 | 1891.9474 | 164.6227 | 192.8906 | 232.9867 | 268.7509 | 310.0082 | 3.205%
11009 | 29-87 | -86.9368 | 28.567 | 1907.106 | 165.2477 | 193.3733 | 233.4501 | 269.1812 | 310.3844 | 3.264%
11010 | 29-87 | -87.2081 | 28.567 | 1922.2988 | 165.85 | 193.8576 | 233.9186 | 269.6203 | 310.7745 | 3.323%
11011 | 29-87.5 | -87.4794 | 28.567 | 1937.5248 | 166.3697 | 194.2588 | 234.2796 | 269.9293 | 311.0073 | 3.375%
11012 | 29-88 | -87.7507 | 28.567 | 1952.7833 | 166.8902 | 194.6696 | 234.6881 | 270.3244 | 311.3756 | 3.427%
11013 | 29-88 | -88.0221 | 28.567 | 1968.0735 | 167.3508 | 195.0363 | 235.0634 | 270.7007 | 311.7447 | 3.473%
11014 | 29-88.5 | -88.2934 | 28.567 | 1983.3946 | 167.4812 | 195.1309 | 235.0722 | 270.6279 | 311.5655 | 3.491%
11015 | 29-88.5 | -88.5647 | 28.567 | 1998.7457 | 167.3653 | 195.0399 | 234.8783 | 270.3284 | 311.1334 | 3.485%
11016 | 29-89 | -88.836 | 28.567 | 2014.1262 | 166.9964 | 194.7337 | 234.452 | 269.7595 | 310.3894 | 3.455%
11017 | 29-89 | -89.1074 | 28.567 | 2029.5354 | 166.354 | 194.1599 | 233.7175 | 268.8152 | 309.1899 | 3.399%
11018 | 29-89.5 | -89.3787 | 28.567 | 2044.9725 | 165.4805 | 193.3934 | 232.8257 | 267.7156 | 307.8421 | 3.321%
11019 | 29-89.5 | -89.65 | 28.567 | 2060.4369 | 164.4248 | 192.4962 | 231.8134 | 266.506 | 306.4008 | 3.227%
11020 | 29-90 | -89.9213 | 28.567 | 2075.9279 | 163.3457 | 191.6452 | 230.8187 | 265.3568 | 305.0748 | 3.134%
11021 | 29-90 | -90.1926 | 28.567 | 2091.4449 | 162.5088 | 191.0137 | 230.1404 | 264.6451 | 304.3361 | 3.061%
11022 | 29-90.5 | -90.464 | 28.567 | 2106.9871 | 161.7625 | 190.4537 | 229.5996 | 264.14 | 303.8911 | 2.995%
11023 | 29-90.5 | -90.7353 | 28.567 | 2122.5541 | 160.799 | 189.7171 | 228.8525 | 263.3963 | 303.1698 | 2.914%
11024 | 29-50 | -50.0371 | 28.8383 | 1147.265 | 113.183 | 146.9798 | 184.8119 | 208.9324 | 236.202 | 0.7667%
11025 | 29-50.5 | -50.3084 | 28.8383 | 1137.1578 | 114.3623 | 148.6684 | 185.9101 | 210.2643 | 237.8098 | 0.7958%
11026 | 29-50.5 | -50.5797 | 28.8383 | 1127.225 | 115.5743 | 150.3995 | 187.0118 | 211.583 | 239.3836 | 0.8267%
11027 | 29-51 | -50.851 | 28.8383 | 1117.4714 | 116.8388 | 152.1979 | 188.1406 | 212.9289 | 240.984 | 0.8602%
11028 | 29-51 | -51.1224 | 28.8383 | 1107.9017 | 118.1901 | 154.0949 | 189.3463 | 214.3795 | 242.7231 | 0.8975%
11029 | 29-51.5 | -51.3937 | 28.8383 | 1098.5207 | 119.558 | 155.9485 | 190.5174 | 215.7636 | 244.356 | 0.9363%
11030 | 29-51.5 | -51.665 | 28.8383 | 1089.3334 | 120.9692 | 157.7676 | 191.694 | 217.1443 | 245.9742 | 0.9774%
11031 | 29-52 | -51.9363 | 28.8383 | 1080.3447 | 122.453 | 159.574 | 192.9245 | 218.5959 | 247.6839 | 1.022%
11032 | 29-52 | -52.2077 | 28.8383 | 1071.5596 | 123.9251 | 161.2854 | 194.0929 | 219.9482 | 249.2483 | 1.068%
11033 | 29-52.5 | -52.479 | 28.8383 | 1062.9832 | 125.4088 | 162.9244 | 195.2391 | 221.2677 | 250.7668 | 1.116%
11034 | 29-53 | -52.7503 | 28.8383 | 1054.6207 | 126.9198 | 164.4929 | 196.3941 | 222.6037 | 252.3117 | 1.166%
11035 | 29-53 | -53.0216 | 28.8383 | 1046.4771 | 128.3865 | 165.9187 | 197.4679 | 223.8237 | 253.6977 | 1.216%
11036 | 29-53.5 | -53.2929 | 28.8383 | 1038.5577 | 129.8636 | 167.2712 | 198.55 | 225.0641 | 255.1194 | 1.269%
11037 | 29-53.5 | -53.5643 | 28.8383 | 1030.8677 | 131.3731 | 168.5614 | 199.6778 | 226.3797 | 256.6531 | 1.325%
11038 | 29-54 | -53.8356 | 28.8383 | 1023.4123 | 132.8559 | 169.7179 | 200.749 | 227.609 | 258.0635 | 1.382%
11039 | 29-54 | -54.1069 | 28.8383 | 1016.1965 | 134.3862 | 170.8351 | 201.8778 | 228.9212 | 259.5882 | 1.442%
11040 | 29-54.5 | -54.3782 | 28.8383 | 1009.2257 | 135.9846 | 171.9206 | 203.095 | 230.3599 | 261.2862 | 1.508%
11041 | 29-54.5 | -54.6495 | 28.8383 | 1002.505 | 137.5204 | 172.8702 | 204.2316 | 231.684 | 262.8276 | 1.573%
11042 | 29-55 | -54.9209 | 28.8383 | 996.0393 | 139.0809 | 173.8208 | 205.4227 | 233.0938 | 264.4936 | 1.642%
11043 | 29-55 | -55.1922 | 28.8383 | 989.8339 | 140.682 | 174.8076 | 206.6895 | 234.6178 | 266.3215 | 1.716%
11044 | 29-55.5 | -55.4635 | 28.8383 | 983.8935 | 142.1859 | 175.7317 | 207.8619 | 236.0172 | 267.9879 | 1.789%
11045 | 29-55.5 | -55.7348 | 28.8383 | 978.223 | 143.6976 | 176.6713 | 209.0805 | 237.4931 | 269.7686 | 1.865%
11046 | 29-56 | -56.0061 | 28.8383 | 972.8272 | 145.2311 | 177.6359 | 210.3544 | 239.0538 | 271.6708 | 1.946%
11047 | 29-56.5 | -56.2775 | 28.8383 | 967.7107 | 146.6857 | 178.548 | 211.5411 | 240.4942 | 273.4119 | 2.026%
11048 | 29-56.5 | -56.5488 | 28.8383 | 962.878 | 148.1536 | 179.47 | 212.7508 | 241.9703 | 275.2044 | 2.109%
11049 | 29-57 | -56.8201 | 28.8383 | 958.3333 | 149.6349 | 180.4007 | 213.9758 | 243.4681 | 277.0269 | 2.197%
11050 | 29-57 | -57.0914 | 28.8383 | 954.0809 | 151.0328 | 181.2688 | 215.0933 | 244.8151 | 278.6454 | 2.283%
11051 | 29-57.5 | -57.3628 | 28.8383 | 950.1245 | 152.4262 | 182.1312 | 216.2204 | 246.1872 | 280.3087 | 2.371%
11052 | 29-57.5 | -57.6341 | 28.8383 | 946.4681 | 153.8048 | 182.9802 | 217.34 | 247.5582 | 281.9791 | 2.461%
11053 | 29-58 | -57.9054 | 28.8383 | 943.115 | 155.0937 | 183.7624 | 218.3619 | 248.8023 | 283.4875 | 2.549%
11054 | 29-58 | -58.1767 | 28.8383 | 940.0685 | 156.4429 | 184.5864 | 219.4675 | 250.1711 | 285.1716 | 2.642%
11055 | 29-58.5 | -58.448 | 28.8383 | 937.3316 | 157.8163 | 185.4329 | 220.6168 | 251.6047 | 286.9468 | 2.74%
11056 | 29-58.5 | -58.7194 | 28.8383 | 934.9071 | 159.1026 | 186.2459 | 221.7121 | 252.9645 | 288.6241 | 2.836%
11057 | 29-59 | -58.9907 | 28.8383 | 932.7974 | 160.4219 | 187.1429 | 222.9423 | 254.5087 | 290.5467 | 2.936%
11058 | 29-59.5 | -59.262 | 28.8383 | 931.0046 | 161.7185 | 188.0738 | 224.2219 | 256.1172 | 292.552 | 3.038%
11059 | 29-59.5 | -59.5333 | 28.8383 | 929.5306 | 162.9161 | 188.9435 | 225.3964 | 257.5779 | 294.3566 | 3.136%
11060 | 29-60 | -59.8046 | 28.8383 | 928.3769 | 164.1124 | 189.8496 | 226.6337 | 259.1269 | 296.2814 | 3.236%
11061 | 29-60 | -60.076 | 28.8383 | 927.5447 | 165.2495 | 190.7435 | 227.8524 | 260.6515 | 298.1745 | 3.334%
11062 | 29-60.5 | -60.3473 | 28.8383 | 927.0349 | 166.2747 | 191.5612 | 228.9455 | 262.0025 | 299.8347 | 3.426%
11063 | 29-60.5 | -60.6186 | 28.8383 | 926.8479 | 167.2784 | 192.3916 | 230.0613 | 263.3856 | 301.5389 | 3.517%
11064 | 29-61 | -60.8899 | 28.8383 | 926.9841 | 168.2098 | 193.2 | 231.1417 | 264.7208 | 303.1796 | 3.605%
11065 | 29-61 | -61.1613 | 28.8383 | 927.4432 | 169.0398 | 193.9595 | 232.1404 | 265.9423 | 304.6673 | 3.685%
11066 | 29-61.5 | -61.4326 | 28.8383 | 928.2248 | 169.8348 | 194.74 | 233.1712 | 267.2068 | 306.2115 | 3.765%
11067 | 29-61.5 | -61.7039 | 28.8383 | 929.3281 | 170.5404 | 195.5035 | 234.174 | 268.4326 | 307.704 | 3.837%
11068 | 29-62 | -61.9752 | 28.8383 | 930.7518 | 171.1541 | 196.241 | 235.1351 | 269.6018 | 309.1216 | 3.903%
11069 | 29-62 | -62.2465 | 28.8383 | 932.4946 | 171.7869 | 197.0311 | 236.1841 | 270.8935 | 310.705 | 3.97%
11070 | 29-62.5 | -62.5179 | 28.8383 | 934.5547 | 172.4068 | 197.8014 | 237.2022 | 272.1439 | 312.2342 | 4.037%
11071 | 29-63 | -62.7892 | 28.8383 | 936.9299 | 173.0123 | 198.549 | 238.1829 | 273.3427 | 313.6945 | 4.103%
11072 | 29-63 | -63.0605 | 28.8383 | 939.6178 | 173.6823 | 199.3938 | 239.3176 | 274.7507 | 315.4325 | 4.175%
11073 | 29-63.5 | -63.3318 | 28.8383 | 942.6158 | 174.3539 | 200.2348 | 240.4388 | 276.1356 | 317.1353 | 4.248%
11074 | 29-63.5 | -63.6031 | 28.8383 | 945.9209 | 175.0177 | 201.0581 | 241.5247 | 277.4676 | 318.7631 | 4.322%
11075 | 29-64 | -63.8745 | 28.8383 | 949.5299 | 175.7335 | 201.9572 | 242.7269 | 278.9553 | 320.5948 | 4.402%
11076 | 29-64 | -64.1458 | 28.8383 | 953.4394 | 176.4408 | 202.8351 | 243.8856 | 280.3769 | 322.3321 | 4.483%
11077 | 29-64.5 | -64.4171 | 28.8383 | 957.6456 | 177.1315 | 203.6801 | 244.9822 | 281.7078 | 323.9427 | 4.564%
11078 | 29-64.5 | -64.6884 | 28.8383 | 962.1446 | 177.8416 | 204.5486 | 246.1092 | 283.0751 | 325.5968 | 4.648%
11079 | 29-65 | -64.9598 | 28.8383 | 966.9323 | 178.5199 | 205.3669 | 247.1543 | 284.3297 | 327.0999 | 4.731%
11080 | 29-65 | -65.2311 | 28.8383 | 972.0045 | 179.1707 | 206.1447 | 248.1368 | 285.5002 | 328.4926 | 4.813%
11081 | 29-65.5 | -65.5024 | 28.8383 | 977.3567 | 179.8228 | 206.9265 | 249.1277 | 286.6834 | 329.9037 | 4.895%
11082 | 29-66 | -65.7737 | 28.8383 | 982.9843 | 180.4107 | 207.613 | 249.9699 | 287.6662 | 331.0502 | 4.973%
11083 | 29-66 | -66.045 | 28.8383 | 988.8826 | 180.9604 | 208.2463 | 250.7335 | 288.5457 | 332.063 | 5.049%
11084 | 29-66.5 | -66.3164 | 28.8383 | 995.0467 | 181.5133 | 208.8907 | 251.522 | 289.464 | 333.1322 | 5.124%
11085 | 29-66.5 | -66.5877 | 28.8383 | 1001.4718 | 181.9875 | 209.4291 | 252.1583 | 290.1857 | 333.9503 | 5.192%
11086 | 29-67 | -66.859 | 28.8383 | 1008.1528 | 182.4318 | 209.9374 | 252.7652 | 290.8793 | 334.7427 | 5.255%
11087 | 29-67 | -67.1303 | 28.8383 | 1015.0847 | 182.894 | 210.4863 | 253.4531 | 291.6942 | 335.707 | 5.318%
11088 | 29-67.5 | -67.4016 | 28.8383 | 1022.2622 | 183.2841 | 210.9431 | 254.0153 | 292.3516 | 336.4754 | 5.373%
11089 | 29-67.5 | -67.673 | 28.8383 | 1029.6803 | 183.654 | 211.3858 | 254.5752 | 293.0193 | 337.2703 | 5.424%
11090 | 29-68 | -67.9443 | 28.8383 | 1037.3338 | 184.0418 | 211.8697 | 255.2176 | 293.8105 | 338.2406 | 5.473%
11091 | 29-68 | -68.2156 | 28.8383 | 1045.2175 | 184.371 | 212.28 | 255.7616 | 294.4799 | 339.061 | 5.516%
11092 | 29-68.5 | -68.4869 | 28.8383 | 1053.3262 | 184.6926 | 212.6847 | 256.304 | 295.1522 | 339.8898 | 5.557%
11093 | 29-69 | -68.7583 | 28.8383 | 1061.6546 | 185.035 | 213.1217 | 256.8985 | 295.8957 | 340.814 | 5.599%
11094 | 29-69 | -69.0296 | 28.8383 | 1070.1978 | 185.2972 | 213.449 | 257.3333 | 296.4317 | 341.4718 | 5.634%
11095 | 29-69.5 | -69.3009 | 28.8383 | 1078.9504 | 185.5431 | 213.76 | 257.7525 | 296.9531 | 342.1166 | 5.665%
11096 | 29-69.5 | -69.5722 | 28.8383 | 1087.9074 | 185.798 | 214.0898 | 258.2078 | 297.5278 | 342.8366 | 5.696%
11097 | 29-70 | -69.8435 | 28.8383 | 1097.0639 | 185.9529 | 214.2829 | 258.4638 | 297.8429 | 343.2227 | 5.716%
11098 | 29-70 | -70.1149 | 28.8383 | 1106.4148 | 186.0922 | 214.4572 | 258.6963 | 298.13 | 343.5757 | 5.735%
11099 | 29-70.5 | -70.3862 | 28.8383 | 1115.9551 | 186.2329 | 214.636 | 258.9382 | 298.4318 | 343.9499 | 5.753%
11100 | 29-70.5 | -70.6575 | 28.8383 | 1125.6802 | 186.2745 | 214.6691 | 258.9544 | 298.4297 | 343.9236 | 5.762%
11101 | 29-71 | -70.9288 | 28.8383 | 1135.5851 | 186.3111 | 214.6917 | 258.9505 | 298.3981 | 343.856 | 5.771%
11102 | 29-71 | -71.2001 | 28.8383 | 1145.6651 | 186.3537 | 214.7184 | 258.9472 | 298.3633 | 343.7803 | 5.782%
11103 | 29-71.5 | -71.4715 | 28.8383 | 1155.9158 | 186.3316 | 214.65 | 258.7963 | 298.1299 | 343.4429 | 5.787%
11104 | 29-71.5 | -71.7428 | 28.8383 | 1166.3325 | 186.3247 | 214.6026 | 258.6764 | 297.9372 | 343.1581 | 5.794%
11105 | 29-72 | -72.0141 | 28.8383 | 1176.9107 | 186.3287 | 214.5688 | 258.5746 | 297.7669 | 342.9008 | 5.803%
11106 | 29-72.5 | -72.2854 | 28.8383 | 1187.6462 | 186.2583 | 214.4276 | 258.3089 | 297.3778 | 342.3572 | 5.804%
11107 | 29-72.5 | -72.5568 | 28.8383 | 1198.5347 | 186.214 | 214.3185 | 258.0848 | 297.0393 | 341.8748 | 5.809%
11108 | 29-73 | -72.8281 | 28.8383 | 1209.572 | 186.1815 | 214.2218 | 257.8741 | 296.7147 | 341.4068 | 5.817%
11109 | 29-73 | -73.0994 | 28.8383 | 1220.754 | 186.0892 | 214.0398 | 257.5342 | 296.2185 | 340.7148 | 5.818%
11110 | 29-73.5 | -73.3707 | 28.8383 | 1232.0768 | 186.0455 | 213.9277 | 257.3011 | 295.8647 | 340.2094 | 5.824%
11111 | 29-73.5 | -73.642 | 28.8383 | 1243.5364 | 186.0161 | 213.8406 | 257.1116 | 295.573 | 339.7889 | 5.831%
11112 | 29-74 | -73.9134 | 28.8383 | 1255.1292 | 185.9165 | 213.6623 | 256.7954 | 295.1209 | 339.1672 | 5.829%
11113 | 29-74 | -74.1847 | 28.8383 | 1266.8513 | 185.8433 | 213.5367 | 256.5784 | 294.8139 | 338.7481 | 5.826%
11114 | 29-74.5 | -74.456 | 28.8383 | 1278.6993 | 185.7592 | 213.4121 | 256.3842 | 294.5522 | 338.4029 | 5.819%
11115 | 29-74.5 | -74.7273 | 28.8383 | 1290.6695 | 185.6009 | 213.201 | 256.0841 | 294.1669 | 337.9136 | 5.8%
11116 | 29-75 | -74.9986 | 28.8383 | 1302.7587 | 185.4352 | 212.9967 | 255.8167 | 293.8405 | 337.5166 | 5.777%
11117 | 29-75.5 | -75.27 | 28.8383 | 1314.9634 | 185.221 | 212.7432 | 255.5003 | 293.4665 | 337.075 | 5.745%
11118 | 29-75.5 | -75.5413 | 28.8383 | 1327.2804 | 184.9071 | 212.371 | 255.0348 | 292.9157 | 336.4239 | 5.699%
11119 | 29-76 | -75.8126 | 28.8383 | 1339.7067 | 184.5734 | 211.9935 | 254.5905 | 292.4135 | 335.8561 | 5.647%
11120 | 29-76 | -76.0839 | 28.8383 | 1352.2391 | 184.184 | 211.561 | 254.0945 | 291.8641 | 335.2484 | 5.585%
11121 | 29-76.5 | -76.3553 | 28.8383 | 1364.8747 | 183.7065 | 211.0287 | 253.4807 | 291.1813 | 334.4896 | 5.509%
11122 | 29-76.5 | -76.6266 | 28.8383 | 1377.6106 | 183.2088 | 210.4908 | 252.8885 | 290.5477 | 333.8156 | 5.429%
11123 | 29-77 | -76.8979 | 28.8383 | 1390.444 | 182.6511 | 209.8865 | 252.2203 | 289.8304 | 333.0492 | 5.34%
11124 | 29-77 | -77.1692 | 28.8383 | 1403.3722 | 182.0174 | 209.1871 | 251.4257 | 288.9572 | 332.0916 | 5.244%
11125 | 29-77.5 | -77.4405 | 28.8383 | 1416.3925 | 181.393 | 208.5129 | 250.6843 | 288.165 | 331.2502 | 5.147%
11126 | 29-77.5 | -77.7119 | 28.8383 | 1429.5025 | 180.7251 | 207.7831 | 249.8672 | 287.2782 | 330.2909 | 5.048%
11127 | 29-78 | -77.9832 | 28.8383 | 1442.6995 | 179.9937 | 206.9644 | 248.9179 | 286.2173 | 329.1064 | 4.943%
11128 | 29-78.5 | -78.2545 | 28.8383 | 1455.9813 | 179.2638 | 206.1526 | 247.9851 | 285.1826 | 327.9601 | 4.841%
11129 | 29-78.5 | -78.5258 | 28.8383 | 1469.3453 | 178.371 | 205.1283 | 246.7569 | 283.7737 | 326.3439 | 4.722%
11130 | 29-79 | -78.7971 | 28.8383 | 1482.7895 | 177.1884 | 203.7733 | 245.0688 | 281.7823 | 323.9968 | 4.574%
11131 | 29-79 | -79.0685 | 28.8383 | 1496.3115 | 175.6132 | 202.1774 | 243.0617 | 279.3994 | 321.1719 | 4.388%
11132 | 29-79.5 | -79.3398 | 28.8383 | 1509.9093 | 173.6394 | 200.2995 | 240.6702 | 276.5357 | 317.7498 | 4.168%
11133 | 29-79.5 | -79.6111 | 28.8383 | 1523.5808 | 171.2454 | 198.1594 | 237.9208 | 273.2239 | 313.7711 | 3.916%
11134 | 29-80 | -79.8824 | 28.8383 | 1537.3239 | 168.5186 | 195.8033 | 234.9221 | 269.6128 | 309.4338 | 3.645%
11135 | 29-80 | -80.1537 | 28.8383 | 1551.1367 | 165.4196 | 193.1868 | 231.5781 | 265.5672 | 304.5543 | 3.358%
11136 | 29-80.5 | -80.4251 | 28.8383 | 1565.0173 | 161.9841 | 190.3494 | 227.9304 | 261.1429 | 299.2057 | 3.064%
11137 | 29-80.5 | -80.6964 | 28.8383 | 1578.9638 | 158.2932 | 187.261 | 224.0857 | 256.4906 | 293.5932 | 2.769%
11138 | 29-81 | -80.9677 | 28.8383 | 1592.9746 | 154.9821 | 184.4882 | 220.6094 | 252.2814 | 288.5117 | 2.526%
11139 | 29-81 | -81.239 | 28.8383 | 1607.0479 | 152.401 | 182.2968 | 217.8762 | 248.9939 | 284.5658 | 2.348%
11140 | 29-81.5 | -81.5104 | 28.8383 | 1621.1819 | 150.597 | 180.7657 | 216.0303 | 246.8307 | 282.0319 | 2.229%
11141 | 29-82 | -81.7817 | 28.8383 | 1635.3752 | 149.0333 | 179.4746 | 214.4942 | 245.0529 | 279.9748 | 2.131%
11142 | 29-82 | -82.053 | 28.8383 | 1649.626 | 147.769 | 178.5224 | 213.425 | 243.8692 | 278.6663 | 2.056%
11143 | 29-82.5 | -82.3243 | 28.8383 | 1663.9329 | 146.9816 | 178.0748 | 213.0701 | 243.6016 | 278.5199 | 2.011%
11144 | 29-82.5 | -82.5956 | 28.8383 | 1678.2943 | 146.6456 | 177.9439 | 213.1355 | 243.849 | 279.0015 | 1.992%
11145 | 29-83 | -82.867 | 28.8383 | 1692.7089 | 146.7353 | 178.1339 | 213.6333 | 244.6326 | 280.1441 | 1.997%
11146 | 29-83 | -83.1383 | 28.8383 | 1707.1753 | 147.3175 | 178.6749 | 214.6155 | 246.0278 | 282.0528 | 2.028%
11147 | 29-83.5 | -83.4096 | 28.8383 | 1721.6921 | 148.2908 | 179.489 | 215.8892 | 247.7457 | 284.3174 | 2.081%
11148 | 29-83.5 | -83.6809 | 28.8383 | 1736.2579 | 149.6947 | 180.6064 | 217.5254 | 249.8869 | 287.076 | 2.159%
11149 | 29-84 | -83.9522 | 28.8383 | 1750.8716 | 151.5431 | 182.0464 | 219.5783 | 252.5302 | 290.438 | 2.265%
11150 | 29-84 | -84.2236 | 28.8383 | 1765.5318 | 153.6929 | 183.7757 | 221.8605 | 255.4126 | 294.0463 | 2.396%
11151 | 29-84.5 | -84.4949 | 28.8383 | 1780.2374 | 155.5108 | 185.2193 | 223.7999 | 257.8565 | 297.101 | 2.512%
11152 | 29-85 | -84.7662 | 28.8383 | 1794.9872 | 156.7146 | 186.1976 | 225.1686 | 259.5891 | 299.2757 | 2.59%
11153 | 29-85 | -85.0375 | 28.8383 | 1809.7801 | 157.2483 | 186.6427 | 225.8078 | 260.3849 | 300.2615 | 2.626%
11154 | 29-85.5 | -85.3089 | 28.8383 | 1824.6149 | 157.66 | 186.9769 | 226.2888 | 260.9741 | 300.981 | 2.654%
11155 | 29-85.5 | -85.5802 | 28.8383 | 1839.4907 | 158.0705 | 187.3258 | 226.7742 | 261.5603 | 301.688 | 2.682%
11156 | 29-86 | -85.8515 | 28.8383 | 1854.4063 | 158.4896 | 187.6937 | 227.168 | 261.9859 | 302.1459 | 2.714%
11157 | 29-86 | -86.1228 | 28.8383 | 1869.3608 | 159.1278 | 188.224 | 227.7475 | 262.6219 | 302.8421 | 2.763%
11158 | 29-86.5 | -86.3941 | 28.8383 | 1884.3532 | 160.0025 | 188.926 | 228.5297 | 263.4888 | 303.8013 | 2.83%
11159 | 29-86.5 | -86.6655 | 28.8383 | 1899.3825 | 160.7165 | 189.4841 | 229.068 | 264.0123 | 304.2926 | 2.888%
11160 | 29-87 | -86.9368 | 28.8383 | 1914.4478 | 161.3453 | 189.9926 | 229.5407 | 264.4543 | 304.6835 | 2.942%
11161 | 29-87 | -87.2081 | 28.8383 | 1929.5483 | 161.902 | 190.4266 | 229.9612 | 264.832 | 304.9961 | 2.99%
11162 | 29-87.5 | -87.4794 | 28.8383 | 1944.683 | 162.3965 | 190.8047 | 230.2942 | 265.1013 | 305.1751 | 3.035%
11163 | 29-88 | -87.7507 | 28.8383 | 1959.8511 | 162.9341 | 191.2517 | 230.7162 | 265.5071 | 305.5504 | 3.084%
11164 | 29-88 | -88.0221 | 28.8383 | 1975.0518 | 163.448 | 191.7055 | 231.1424 | 265.9398 | 305.9818 | 3.132%
11165 | 29-88.5 | -88.2934 | 28.8383 | 1990.2842 | 163.6332 | 191.885 | 231.2121 | 265.9349 | 305.8786 | 3.153%
11166 | 29-88.5 | -88.5647 | 28.8383 | 2005.5477 | 163.5518 | 191.8452 | 231.0563 | 265.6739 | 305.4849 | 3.151%
11167 | 29-89 | -88.836 | 28.8383 | 2020.8414 | 163.2005 | 191.5621 | 230.6493 | 265.1188 | 304.7473 | 3.125%
11168 | 29-89 | -89.1074 | 28.8383 | 2036.1646 | 162.5706 | 191.0004 | 229.9318 | 264.1838 | 303.5471 | 3.075%
11169 | 29-89.5 | -89.3787 | 28.8383 | 2051.5166 | 161.6438 | 190.1433 | 228.9787 | 262.9933 | 302.0714 | 2.999%
11170 | 29-89.5 | -89.65 | 28.8383 | 2066.8967 | 160.4681 | 189.1018 | 227.8302 | 261.5951 | 300.377 | 2.903%
11171 | 29-90 | -89.9213 | 28.8383 | 2082.3042 | 159.2208 | 188.0843 | 226.6507 | 260.1931 | 298.7139 | 2.806%
11172 | 29-90 | -90.1926 | 28.8383 | 2097.7384 | 158.3041 | 187.3625 | 225.8795 | 259.3476 | 297.7906 | 2.735%
11173 | 29-90.5 | -90.464 | 28.8383 | 2113.1988 | 157.5548 | 186.782 | 225.331 | 258.8193 | 297.3022 | 2.676%
11174 | 29-90.5 | -90.7353 | 28.8383 | 2128.6847 | 156.638 | 186.1005 | 224.6384 | 258.1333 | 296.6414 | 2.607%
11175 | 29-50 | -50.0371 | 29.1096 | 1162.0198 | 113.7639 | 147.6852 | 185.2374 | 209.434 | 236.7923 | 0.7794%
11176 | 29-50.5 | -50.3084 | 29.1096 | 1152.0646 | 114.8957 | 149.2997 | 186.2896 | 210.7126 | 238.3385 | 0.8079%
11177 | 29-50.5 | -50.5797 | 29.1096 | 1142.2837 | 116.0594 | 150.9551 | 187.3435 | 211.9745 | 239.845 | 0.838%
11178 | 29-51 | -50.851 | 29.1096 | 1132.6816 | 117.2776 | 152.6815 | 188.4257 | 213.2634 | 241.3761 | 0.8706%
11179 | 29-51 | -51.1224 | 29.1096 | 1123.2628 | 118.586 | 154.5088 | 189.5875 | 214.6584 | 243.0455 | 0.9072%
11180 | 29-51.5 | -51.3937 | 29.1096 | 1114.0321 | 119.92 | 156.3024 | 190.7231 | 215.9962 | 244.6191 | 0.9453%
11181 | 29-51.5 | -51.665 | 29.1096 | 1104.9943 | 121.3077 | 158.0724 | 191.8747 | 217.3435 | 246.1935 | 0.9861%
11182 | 29-52 | -51.9363 | 29.1096 | 1096.154 | 122.7791 | 159.841 | 193.091 | 218.775 | 247.8758 | 1.031%
11183 | 29-52 | -52.2077 | 29.1096 | 1087.5162 | 124.2477 | 161.5239 | 194.2542 | 220.1194 | 249.429 | 1.077%
11184 | 29-52.5 | -52.479 | 29.1096 | 1079.0857 | 125.7366 | 163.1438 | 195.4035 | 221.4409 | 250.9482 | 1.125%
11185 | 29-53 | -52.7503 | 29.1096 | 1070.8676 | 127.2621 | 164.7035 | 196.5691 | 222.7871 | 252.5024 | 1.176%
11186 | 29-53 | -53.0216 | 29.1096 | 1062.8666 | 128.7544 | 166.1323 | 197.6621 | 224.0264 | 253.9075 | 1.228%
11187 | 29-53.5 | -53.2929 | 29.1096 | 1055.0879 | 130.2675 | 167.4982 | 198.7705 | 225.2926 | 255.3541 | 1.282%
11188 | 29-53.5 | -53.5643 | 29.1096 | 1047.5363 | 131.8231 | 168.8127 | 199.9313 | 226.6405 | 256.9184 | 1.341%
11189 | 29-54 | -53.8356 | 29.1096 | 1040.2169 | 133.3593 | 170.0023 | 201.0391 | 227.9048 | 258.3614 | 1.4%
11190 | 29-54 | -54.1069 | 29.1096 | 1033.1346 | 134.945 | 171.1536 | 202.2039 | 229.2511 | 259.9169 | 1.464%
11191 | 29-54.5 | -54.3782 | 29.1096 | 1026.2943 | 136.5983 | 172.2713 | 203.4551 | 230.7218 | 261.6436 | 1.533%
11192 | 29-54.5 | -54.6495 | 29.1096 | 1019.7009 | 138.1865 | 173.2529 | 204.622 | 232.0736 | 263.209 | 1.602%
11193 | 29-55 | -54.9209 | 29.1096 | 1013.3594 | 139.7905 | 174.2273 | 205.8327 | 233.4982 | 264.8833 | 1.674%
11194 | 29-55 | -55.1922 | 29.1096 | 1007.2743 | 141.4245 | 175.2288 | 207.1072 | 235.0227 | 266.702 | 1.752%
11195 | 29-55.5 | -55.4635 | 29.1096 | 1001.4505 | 142.9519 | 176.1607 | 208.2813 | 236.4175 | 268.356 | 1.827%
11196 | 29-55.5 | -55.7348 | 29.1096 | 995.8926 | 144.4795 | 177.1028 | 209.496 | 237.8829 | 270.1177 | 1.906%
11197 | 29-56 | -56.0061 | 29.1096 | 990.605 | 146.0212 | 178.0646 | 210.7596 | 239.4259 | 271.9929 | 1.99%
11198 | 29-56.5 | -56.2775 | 29.1096 | 985.5922 | 147.4771 | 178.9696 | 211.9323 | 240.8455 | 273.7046 | 2.071%
11199 | 29-56.5 | -56.5488 | 29.1096 | 980.8582 | 148.9382 | 179.8796 | 213.123 | 242.2958 | 275.4631 | 2.156%
11200 | 29-57 | -56.8201 | 29.1096 | 976.4073 | 150.4042 | 180.7933 | 214.3239 | 243.7628 | 277.2467 | 2.245%
11201 | 29-57 | -57.0914 | 29.1096 | 972.2433 | 151.7759 | 181.638 | 215.4105 | 245.0719 | 278.8189 | 2.331%
11202 | 29-57.5 | -57.3628 | 29.1096 | 968.3699 | 153.1355 | 182.4737 | 216.5037 | 246.4035 | 280.4337 | 2.42%
11203 | 29-57.5 | -57.6341 | 29.1096 | 964.7907 | 154.4733 | 183.2927 | 217.5857 | 247.7298 | 282.0512 | 2.509%
11204 | 29-58 | -57.9054 | 29.1096 | 961.5088 | 155.7141 | 184.0406 | 218.5632 | 248.9201 | 283.4945 | 2.595%
11205 | 29-58 | -58.1767 | 29.1096 | 958.5276 | 157.0061 | 184.8279 | 219.6209 | 250.2306 | 285.1078 | 2.686%
11206 | 29-58.5 | -58.448 | 29.1096 | 955.8496 | 158.3199 | 185.6378 | 220.7236 | 251.6082 | 286.8157 | 2.782%
11207 | 29-58.5 | -58.7194 | 29.1096 | 953.4775 | 159.551 | 186.4197 | 221.7818 | 252.9254 | 288.4441 | 2.874%
11208 | 29-59 | -58.9907 | 29.1096 | 951.4136 | 160.8183 | 187.2889 | 222.9789 | 254.4315 | 290.3228 | 2.972%
11209 | 29-59.5 | -59.262 | 29.1096 | 949.6599 | 162.0672 | 188.1964 | 224.2312 | 256.0094 | 292.2935 | 3.072%
11210 | 29-59.5 | -59.5333 | 29.1096 | 948.2182 | 163.2222 | 189.0482 | 225.3863 | 257.4494 | 294.0763 | 3.168%
11211 | 29-60 | -59.8046 | 29.1096 | 947.0898 | 164.3803 | 189.9404 | 226.6088 | 258.9832 | 295.9852 | 3.266%
11212 | 29-60 | -60.076 | 29.1096 | 946.2758 | 165.4826 | 190.8232 | 227.8158 | 260.4956 | 297.8656 | 3.361%
11213 | 29-60.5 | -60.3473 | 29.1096 | 945.7772 | 166.4761 | 191.6317 | 228.8988 | 261.8356 | 299.5138 | 3.451%
11214 | 29-60.5 | -60.6186 | 29.1096 | 945.5944 | 167.4539 | 192.4564 | 230.008 | 263.2115 | 301.2099 | 3.541%
11215 | 29-61 | -60.8899 | 29.1096 | 945.7276 | 168.3647 | 193.2611 | 231.0835 | 264.5404 | 302.8428 | 3.628%
11216 | 29-61 | -61.1613 | 29.1096 | 946.1766 | 169.1789 | 194.0182 | 232.0772 | 265.7544 | 304.3199 | 3.708%
11217 | 29-61.5 | -61.4326 | 29.1096 | 946.941 | 169.9637 | 194.7986 | 233.1064 | 267.0156 | 305.8584 | 3.787%
11218 | 29-61.5 | -61.7039 | 29.1096 | 948.02 | 170.6688 | 195.5641 | 234.1096 | 268.2402 | 307.3476 | 3.86%
11219 | 29-62 | -61.9752 | 29.1096 | 949.4126 | 171.2854 | 196.3031 | 235.0697 | 269.4056 | 308.7578 | 3.927%
11220 | 29-62 | -62.2465 | 29.1096 | 951.1174 | 171.9182 | 197.0896 | 236.1087 | 270.6809 | 310.3164 | 3.995%
11221 | 29-62.5 | -62.5179 | 29.1096 | 953.1327 | 172.5348 | 197.8513 | 237.1084 | 271.903 | 311.8051 | 4.062%
11222 | 29-63 | -62.7892 | 29.1096 | 955.4565 | 173.1333 | 198.5845 | 238.0618 | 273.0616 | 313.209 | 4.128%
11223 | 29-63 | -63.0605 | 29.1096 | 958.0865 | 173.7918 | 199.4086 | 239.1597 | 274.4168 | 314.8741 | 4.2%
11224 | 29-63.5 | -63.3318 | 29.1096 | 961.0203 | 174.4477 | 200.2235 | 240.2361 | 275.7387 | 316.491 | 4.274%
11225 | 29-63.5 | -63.6031 | 29.1096 | 964.2551 | 175.0929 | 201.017 | 241.2727 | 277.0022 | 318.0262 | 4.347%
11226 | 29-64 | -63.8745 | 29.1096 | 967.7878 | 175.7878 | 201.8839 | 242.4234 | 278.4193 | 319.7635 | 4.426%
11227 | 29-64 | -64.1458 | 29.1096 | 971.6152 | 176.474 | 202.7305 | 243.5329 | 279.7742 | 321.4124 | 4.505%
11228 | 29-64.5 | -64.4171 | 29.1096 | 975.7338 | 177.1452 | 203.5473 | 244.5867 | 281.0479 | 322.9481 | 4.585%
11229 | 29-64.5 | -64.6884 | 29.1096 | 980.1399 | 177.8382 | 204.3927 | 245.6803 | 282.3719 | 324.5468 | 4.669%
11230 | 29-65 | -64.9598 | 29.1096 | 984.8296 | 178.5009 | 205.1916 | 246.6994 | 283.5943 | 326.0103 | 4.751%
11231 | 29-65 | -65.2311 | 29.1096 | 989.7989 | 179.1376 | 205.9533 | 247.6625 | 284.7424 | 327.377 | 4.831%
11232 | 29-65.5 | -65.5024 | 29.1096 | 995.0436 | 179.7772 | 206.7221 | 248.64 | 285.9122 | 328.7748 | 4.912%
11233 | 29-66 | -65.7737 | 29.1096 | 1000.5593 | 180.3539 | 207.3983 | 249.4742 | 286.8894 | 329.9191 | 4.989%
11234 | 29-66 | -66.045 | 29.1096 | 1006.3416 | 180.8939 | 208.0242 | 250.2345 | 287.7702 | 330.9392 | 5.063%
11235 | 29-66.5 | -66.3164 | 29.1096 | 1012.3859 | 181.4387 | 208.6636 | 251.0242 | 288.696 | 332.0242 | 5.137%
11236 | 29-66.5 | -66.5877 | 29.1096 | 1018.6875 | 181.907 | 209.2003 | 251.6664 | 289.4315 | 332.8661 | 5.203%
11237 | 29-67 | -66.859 | 29.1096 | 1025.2416 | 182.3477 | 209.7099 | 252.2836 | 290.1446 | 333.6897 | 5.266%
11238 | 29-67 | -67.1303 | 29.1096 | 1032.0434 | 182.8086 | 210.2631 | 252.9858 | 290.9838 | 334.6911 | 5.328%
11239 | 29-67.5 | -67.4016 | 29.1096 | 1039.088 | 183.1988 | 210.7255 | 253.5637 | 291.667 | 335.4981 | 5.382%
11240 | 29-67.5 | -67.673 | 29.1096 | 1046.3705 | 183.5681 | 211.1726 | 254.1367 | 292.3566 | 336.3262 | 5.432%
11241 | 29-68 | -67.9443 | 29.1096 | 1053.8859 | 183.9537 | 211.6583 | 254.7882 | 293.1642 | 337.322 | 5.481%
11242 | 29-68 | -68.2156 | 29.1096 | 1061.6293 | 184.279 | 212.0669 | 255.3346 | 293.8404 | 338.1545 | 5.522%
11243 | 29-68.5 | -68.4869 | 29.1096 | 1069.5956 | 184.5957 | 212.468 | 255.8755 | 294.5132 | 338.9866 | 5.562%
11244 | 29-69 | -68.7583 | 29.1096 | 1077.78 | 184.9332 | 212.9003 | 256.4661 | 295.2537 | 339.9088 | 5.604%
11245 | 29-69 | -69.0296 | 29.1096 | 1086.1774 | 185.1901 | 213.2219 | 256.8945 | 295.7825 | 340.5586 | 5.638%
11246 | 29-69.5 | -69.3009 | 29.1096 | 1094.7829 | 185.4303 | 213.5258 | 257.3042 | 296.2921 | 341.1888 | 5.668%
11247 | 29-69.5 | -69.5722 | 29.1096 | 1103.5917 | 185.6792 | 213.8473 | 257.7472 | 296.8506 | 341.8876 | 5.699%
11248 | 29-70 | -69.8435 | 29.1096 | 1112.5988 | 185.8315 | 214.0372 | 257.9988 | 297.1602 | 342.267 | 5.719%
11249 | 29-70 | -70.1149 | 29.1096 | 1121.7996 | 185.9715 | 214.2134 | 258.2351 | 297.453 | 342.628 | 5.737%
11250 | 29-70.5 | -70.3862 | 29.1096 | 1131.1891 | 186.1159 | 214.3984 | 258.4878 | 297.7699 | 343.0226 | 5.755%
11251 | 29-70.5 | -70.6575 | 29.1096 | 1140.7627 | 186.1617 | 214.4384 | 258.5158 | 297.7845 | 343.0191 | 5.765%
11252 | 29-71 | -70.9288 | 29.1096 | 1150.5158 | 186.2042 | 214.4703 | 258.527 | 297.7737 | 342.9795 | 5.775%
11253 | 29-71 | -71.2001 | 29.1096 | 1160.4439 | 186.2545 | 214.5084 | 258.5414 | 297.7628 | 342.9353 | 5.786%
11254 | 29-71.5 | -71.4715 | 29.1096 | 1170.5424 | 186.2391 | 214.4494 | 258.4048 | 297.5485 | 342.623 | 5.792%
11255 | 29-71.5 | -71.7428 | 29.1096 | 1180.8069 | 186.2385 | 214.4109 | 258.2982 | 297.3736 | 342.3614 | 5.8%
11256 | 29-72 | -72.0141 | 29.1096 | 1191.2332 | 186.2482 | 214.3852 | 258.2085 | 297.2192 | 342.1251 | 5.809%
11257 | 29-72.5 | -72.2854 | 29.1096 | 1201.8169 | 186.182 | 214.2505 | 257.9534 | 296.8449 | 341.6013 | 5.811%
11258 | 29-72.5 | -72.5568 | 29.1096 | 1212.5539 | 186.1407 | 214.1467 | 257.7389 | 296.5201 | 341.1381 | 5.816%
11259 | 29-73 | -72.8281 | 29.1096 | 1223.4402 | 186.1105 | 214.0548 | 257.5375 | 296.2095 | 340.6899 | 5.823%
11260 | 29-73 | -73.0994 | 29.1096 | 1234.4718 | 186.02 | 213.8779 | 257.2088 | 295.7305 | 340.0229 | 5.824%
11261 | 29-73.5 | -73.3707 | 29.1096 | 1245.6447 | 185.9737 | 213.7647 | 256.9771 | 295.381 | 339.5254 | 5.83%
11262 | 29-73.5 | -73.642 | 29.1096 | 1256.9551 | 185.9374 | 213.6702 | 256.7797 | 295.081 | 339.0964 | 5.835%
11263 | 29-74 | -73.9134 | 29.1096 | 1268.3994 | 185.8271 | 213.4798 | 256.4496 | 294.6134 | 338.4575 | 5.831%
11264 | 29-74 | -74.1847 | 29.1096 | 1279.974 | 185.7413 | 213.3404 | 256.217 | 294.2896 | 338.0203 | 5.827%
11265 | 29-74.5 | -74.456 | 29.1096 | 1291.6751 | 185.6417 | 213.1992 | 256.0047 | 294.0085 | 337.6547 | 5.817%
11266 | 29-74.5 | -74.7273 | 29.1096 | 1303.4996 | 185.4639 | 212.9676 | 255.6831 | 293.6013 | 337.1433 | 5.795%
11267 | 29-75 | -74.9986 | 29.1096 | 1315.4438 | 185.2764 | 212.7417 | 255.395 | 293.2557 | 336.7296 | 5.767%
11268 | 29-75.5 | -75.27 | 29.1096 | 1327.5047 | 185.0374 | 212.4643 | 255.0573 | 292.8638 | 336.2747 | 5.731%
11269 | 29-75.5 | -75.5413 | 29.1096 | 1339.6789 | 184.6959 | 212.0659 | 254.569 | 292.2944 | 335.611 | 5.679%
11270 | 29-76 | -75.8126 | 29.1096 | 1351.9635 | 184.3323 | 211.6597 | 254.0992 | 291.7706 | 335.0273 | 5.621%
11271 | 29-76 | -76.0839 | 29.1096 | 1364.3553 | 183.9113 | 211.1969 | 253.5763 | 291.1985 | 334.4031 | 5.553%
11272 | 29-76.5 | -76.3553 | 29.1096 | 1376.8514 | 183.4017 | 210.6346 | 252.9375 | 290.4966 | 333.6332 | 5.472%
11273 | 29-76.5 | -76.6266 | 29.1096 | 1389.449 | 182.8714 | 210.067 | 252.3218 | 289.8466 | 332.9526 | 5.386%
11274 | 29-77 | -76.8979 | 29.1096 | 1402.1454 | 182.2802 | 209.4318 | 251.6286 | 289.1111 | 332.1775 | 5.291%
11275 | 29-77 | -77.1692 | 29.1096 | 1414.9377 | 181.6111 | 208.6979 | 250.8021 | 288.2096 | 331.197 | 5.189%
11276 | 29-77.5 | -77.4405 | 29.1096 | 1427.8234 | 180.9491 | 207.9841 | 250.0191 | 287.3748 | 330.3124 | 5.088%
11277 | 29-77.5 | -77.7119 | 29.1096 | 1440.7999 | 180.2419 | 207.2114 | 249.1542 | 286.4361 | 329.2973 | 4.983%
11278 | 29-78 | -77.9832 | 29.1096 | 1453.8648 | 179.4701 | 206.348 | 248.1539 | 285.319 | 328.0508 | 4.875%
11279 | 29-78.5 | -78.2545 | 29.1096 | 1467.0156 | 178.6995 | 205.4904 | 247.1674 | 284.224 | 326.8366 | 4.767%
11280 | 29-78.5 | -78.5258 | 29.1096 | 1480.2501 | 177.7923 | 204.4536 | 245.9305 | 282.8105 | 325.2214 | 4.648%
11281 | 29-79 | -78.7971 | 29.1096 | 1493.5658 | 176.6469 | 203.1446 | 244.3128 | 280.913 | 322.997 | 4.505%
11282 | 29-79 | -79.0685 | 29.1096 | 1506.9608 | 175.1949 | 201.6518 | 242.4527 | 278.7188 | 320.4112 | 4.334%
11283 | 29-79.5 | -79.3398 | 29.1096 | 1520.4327 | 173.3123 | 199.8575 | 240.1819 | 276.011 | 317.188 | 4.124%
11284 | 29-79.5 | -79.6111 | 29.1096 | 1533.9796 | 170.9125 | 197.7339 | 237.4642 | 272.7458 | 313.2743 | 3.874%
11285 | 29-80 | -79.8824 | 29.1096 | 1547.5994 | 168.0868 | 195.3074 | 234.4065 | 269.0698 | 308.8656 | 3.595%
11286 | 29-80 | -80.1537 | 29.1096 | 1561.2901 | 164.8761 | 192.5956 | 230.9889 | 264.9415 | 303.8932 | 3.301%
11287 | 29-80.5 | -80.4251 | 29.1096 | 1575.05 | 161.3541 | 189.682 | 227.2936 | 260.4679 | 298.4939 | 3.003%
11288 | 29-80.5 | -80.6964 | 29.1096 | 1588.877 | 157.6014 | 186.5405 | 223.4321 | 255.8067 | 292.8831 | 2.709%
11289 | 29-81 | -80.9677 | 29.1096 | 1602.7695 | 154.1856 | 183.6886 | 219.9056 | 251.5487 | 287.7555 | 2.463%
11290 | 29-81 | -81.239 | 29.1096 | 1616.7257 | 151.425 | 181.3715 | 217.0583 | 248.1321 | 283.6638 | 2.279%
11291 | 29-81.5 | -81.5104 | 29.1096 | 1630.7439 | 149.3902 | 179.6677 | 215.0286 | 245.7509 | 280.8716 | 2.149%
11292 | 29-82 | -81.7817 | 29.1096 | 1644.8225 | 147.5871 | 178.1916 | 213.2933 | 243.7347 | 278.5294 | 2.041%
11293 | 29-82 | -82.053 | 29.1096 | 1658.9599 | 146.0572 | 177.0195 | 211.9783 | 242.2528 | 276.8604 | 1.954%
11294 | 29-82.5 | -82.3243 | 29.1096 | 1673.1546 | 144.9541 | 176.2935 | 211.2963 | 241.5846 | 276.2253 | 1.895%
11295 | 29-82.5 | -82.5956 | 29.1096 | 1687.405 | 144.2181 | 175.8283 | 210.9596 | 241.3363 | 276.0988 | 1.857%
11296 | 29-83 | -82.867 | 29.1096 | 1701.7097 | 143.9424 | 175.7057 | 211.0828 | 241.656 | 276.6702 | 1.843%
11297 | 29-83 | -83.1383 | 29.1096 | 1716.0674 | 144.2584 | 176.0026 | 211.7774 | 242.6921 | 278.1334 | 1.858%
11298 | 29-83.5 | -83.4096 | 29.1096 | 1730.4766 | 145.0589 | 176.6596 | 212.8549 | 244.1615 | 280.086 | 1.898%
11299 | 29-83.5 | -83.6809 | 29.1096 | 1744.936 | 146.3029 | 177.645 | 214.309 | 246.0698 | 282.5499 | 1.962%
11300 | 29-84 | -83.9522 | 29.1096 | 1759.4444 | 147.9678 | 178.9369 | 216.1558 | 248.4495 | 285.5782 | 2.05%
11301 | 29-84 | -84.2236 | 29.1096 | 1774.0004 | 149.8969 | 180.4792 | 218.1941 | 251.0197 | 288.7914 | 2.158%
11302 | 29-84.5 | -84.4949 | 29.1096 | 1788.6029 | 151.5239 | 181.7446 | 219.9124 | 253.1792 | 291.4845 | 2.252%
11303 | 29-85 | -84.7662 | 29.1096 | 1803.2507 | 152.5983 | 182.573 | 221.108 | 254.6879 | 293.3731 | 2.315%
11304 | 29-85 | -85.0375 | 29.1096 | 1817.9426 | 153.057 | 182.9201 | 221.6478 | 255.3521 | 294.1877 | 2.342%
11305 | 29-85.5 | -85.3089 | 29.1096 | 1832.6775 | 153.4071 | 183.175 | 222.0478 | 255.8324 | 294.7639 | 2.363%
11306 | 29-85.5 | -85.5802 | 29.1096 | 1847.4544 | 153.7622 | 183.4548 | 222.4557 | 256.3137 | 295.3322 | 2.385%
11307 | 29-86 | -85.8515 | 29.1096 | 1862.2722 | 154.1733 | 183.8275 | 222.8353 | 256.7159 | 295.7554 | 2.414%
11308 | 29-86 | -86.1228 | 29.1096 | 1877.1298 | 154.8525 | 184.4245 | 223.4611 | 257.4093 | 296.5224 | 2.46%
11309 | 29-86.5 | -86.3941 | 29.1096 | 1892.0264 | 155.8114 | 185.2278 | 224.3424 | 258.405 | 297.6467 | 2.526%
11310 | 29-86.5 | -86.6655 | 29.1096 | 1906.9608 | 156.564 | 185.8565 | 224.9393 | 259.0069 | 298.241 | 2.582%
11311 | 29-87 | -86.9368 | 29.1096 | 1921.9322 | 157.1888 | 186.3842 | 225.423 | 259.4672 | 298.6597 | 2.63%
11312 | 29-87 | -87.2081 | 29.1096 | 1936.9397 | 157.7076 | 186.7854 | 225.8145 | 259.8118 | 298.9349 | 2.67%
11313 | 29-87.5 | -87.4794 | 29.1096 | 1951.9824 | 158.1776 | 187.1467 | 226.1294 | 260.0582 | 299.0855 | 2.708%
11314 | 29-88 | -87.7507 | 29.1096 | 1967.0594 | 158.7192 | 187.6148 | 226.5572 | 260.4684 | 299.4635 | 2.752%
11315 | 29-88 | -88.0221 | 29.1096 | 1982.1699 | 159.2613 | 188.1211 | 227.0114 | 260.9309 | 299.9267 | 2.797%
11316 | 29-88.5 | -88.2934 | 29.1096 | 1997.313 | 159.4728 | 188.3458 | 227.114 | 260.9608 | 299.8603 | 2.819%
11317 | 29-88.5 | -88.5647 | 29.1096 | 2012.4881 | 159.3992 | 188.3203 | 226.9712 | 260.7088 | 299.4706 | 2.817%
11318 | 29-89 | -88.836 | 29.1096 | 2027.6942 | 159.0429 | 188.0292 | 226.5638 | 260.1454 | 298.7148 | 2.793%
11319 | 29-89 | -89.1074 | 29.1096 | 2042.9307 | 158.4133 | 187.4643 | 225.8575 | 259.2161 | 297.5131 | 2.747%
11320 | 29-89.5 | -89.3787 | 29.1096 | 2058.1969 | 157.4498 | 186.5439 | 224.8668 | 257.967 | 295.9529 | 2.675%
11321 | 29-89.5 | -89.65 | 29.1096 | 2073.492 | 156.1983 | 185.3911 | 223.6321 | 256.4459 | 294.0899 | 2.583%
11322 | 29-90 | -89.9213 | 29.1096 | 2088.8152 | 154.8436 | 184.2453 | 222.3306 | 254.8723 | 292.1937 | 2.488%
11323 | 29-90 | -90.1926 | 29.1096 | 2104.1661 | 153.8763 | 183.4431 | 221.4949 | 253.9288 | 291.1304 | 2.421%
11324 | 29-90.5 | -90.464 | 29.1096 | 2119.5439 | 153.1267 | 182.8441 | 220.9371 | 253.3738 | 290.5926 | 2.368%
11325 | 29-90.5 | -90.7353 | 29.1096 | 2134.9479 | 152.2434 | 182.1948 | 220.2788 | 252.7183 | 289.9562 | 2.31%
11326 | 29-50 | -50.0371 | 29.3809 | 1176.885 | 114.3986 | 148.4722 | 185.7243 | 210.0188 | 237.4922 | 0.7939%
11327 | 29-50.5 | -50.3084 | 29.3809 | 1167.0791 | 115.4892 | 150.0196 | 186.7325 | 211.2444 | 238.9749 | 0.8218%
11328 | 29-50.5 | -50.5797 | 29.3809 | 1157.4472 | 116.6112 | 151.607 | 187.7412 | 212.4509 | 240.4137 | 0.8513%
11329 | 29-51 | -50.851 | 29.3809 | 1147.9935 | 117.79 | 153.2645 | 188.7803 | 213.6857 | 241.8778 | 0.8833%
11330 | 29-51 | -51.1224 | 29.3809 | 1138.7226 | 119.0619 | 155.0232 | 189.9024 | 215.03 | 243.4833 | 0.9192%
11331 | 29-51.5 | -51.3937 | 29.3809 | 1129.6391 | 120.3674 | 156.7569 | 191.0071 | 216.328 | 245.0062 | 0.9569%
11332 | 29-51.5 | -51.665 | 29.3809 | 1120.7474 | 121.7364 | 158.4774 | 192.1385 | 217.6486 | 246.5462 | 0.9975%
11333 | 29-52 | -51.9363 | 29.3809 | 1112.0523 | 123.1994 | 160.2075 | 193.345 | 219.0662 | 248.2097 | 1.042%
11334 | 29-52 | -52.2077 | 29.3809 | 1103.5584 | 124.667 | 161.8602 | 194.5057 | 220.4061 | 249.7558 | 1.089%
11335 | 29-52.5 | -52.479 | 29.3809 | 1095.2703 | 126.1627 | 163.4587 | 195.6598 | 221.7318 | 251.2785 | 1.138%
11336 | 29-53 | -52.7503 | 29.3809 | 1087.193 | 127.703 | 165.0067 | 196.8375 | 223.0906 | 252.8456 | 1.19%
11337 | 29-53 | -53.0216 | 29.3809 | 1079.331 | 129.2211 | 166.4353 | 197.9519 | 224.353 | 254.2755 | 1.243%
11338 | 29-53.5 | -53.2929 | 29.3809 | 1071.6893 | 130.7696 | 167.8104 | 199.0879 | 225.6481 | 255.752 | 1.3%
11339 | 29-53.5 | -53.5643 | 29.3809 | 1064.2725 | 132.3697 | 169.1431 | 200.2819 | 227.0295 | 257.3497 | 1.36%
11340 | 29-54 | -53.8356 | 29.3809 | 1057.0853 | 133.9566 | 170.3578 | 201.4252 | 228.3288 | 258.8262 | 1.423%
11341 | 29-54 | -54.1069 | 29.3809 | 1050.1327 | 135.5939 | 171.5341 | 202.6241 | 229.7078 | 260.4123 | 1.49%
11342 | 29-54.5 | -54.3782 | 29.3809 | 1043.4192 | 137.2981 | 172.6791 | 203.9069 | 231.2084 | 262.166 | 1.563%
11343 | 29-54.5 | -54.6495 | 29.3809 | 1036.9495 | 138.9334 | 173.689 | 205.1001 | 232.584 | 263.7516 | 1.635%
11344 | 29-55 | -54.9209 | 29.3809 | 1030.7282 | 140.575 | 174.6832 | 206.3258 | 234.0183 | 265.4286 | 1.711%
11345 | 29-55 | -55.1922 | 29.3809 | 1024.7599 | 142.2354 | 175.695 | 207.6026 | 235.5368 | 267.2309 | 1.792%
11346 | 29-55.5 | -55.4635 | 29.3809 | 1019.0491 | 143.7818 | 176.6314 | 208.7735 | 236.9207 | 268.864 | 1.87%
11347 | 29-55.5 | -55.7348 | 29.3809 | 1013.6001 | 145.3236 | 177.5744 | 209.9813 | 238.3714 | 270.6012 | 1.952%
11348 | 29-56 | -56.0061 | 29.3809 | 1008.4172 | 146.8745 | 178.5335 | 211.2341 | 239.8957 | 272.4475 | 2.038%
11349 | 29-56.5 | -56.2775 | 29.3809 | 1003.5045 | 148.3346 | 179.4329 | 212.3945 | 241.2961 | 274.1318 | 2.122%
11350 | 29-56.5 | -56.5488 | 29.3809 | 998.866 | 149.7924 | 180.333 | 213.5692 | 242.7245 | 275.861 | 2.209%
11351 | 29-57 | -56.8201 | 29.3809 | 994.5056 | 151.247 | 181.2322 | 214.7498 | 244.1656 | 277.612 | 2.299%
11352 | 29-57 | -57.0914 | 29.3809 | 990.427 | 152.597 | 182.0562 | 215.8089 | 245.4411 | 279.1431 | 2.386%
11353 | 29-57.5 | -57.3628 | 29.3809 | 986.6337 | 153.9285 | 182.8682 | 216.8716 | 246.7358 | 280.7134 | 2.475%
11354 | 29-57.5 | -57.6341 | 29.3809 | 983.1289 | 155.2304 | 183.661 | 217.92 | 248.0218 | 282.2825 | 2.564%
11355 | 29-58 | -57.9054 | 29.3809 | 979.9158 | 156.4271 | 184.3794 | 218.8592 | 249.1654 | 283.6692 | 2.649%
11356 | 29-58 | -58.1767 | 29.3809 | 976.9973 | 157.6678 | 185.1366 | 219.8775 | 250.4279 | 285.2241 | 2.738%
11357 | 29-58.5 | -58.448 | 29.3809 | 974.3761 | 158.9256 | 185.9172 | 220.9427 | 251.7603 | 286.8777 | 2.831%
11358 | 29-58.5 | -58.7194 | 29.3809 | 972.0545 | 160.1042 | 186.6729 | 221.9688 | 253.0401 | 288.4623 | 2.922%
11359 | 29-59 | -58.9907 | 29.3809 | 970.0347 | 161.3187 | 187.5155 | 223.1326 | 254.5067 | 290.2941 | 3.017%
11360 | 29-59.5 | -59.262 | 29.3809 | 968.3187 | 162.5158 | 188.3976 | 224.3532 | 256.0469 | 292.22 | 3.114%
11361 | 29-59.5 | -59.5333 | 29.3809 | 966.9079 | 163.6224 | 189.2278 | 225.4819 | 257.4562 | 293.9669 | 3.207%
11362 | 29-60 | -59.8046 | 29.3809 | 965.8039 | 164.7352 | 190.1013 | 226.6809 | 258.9618 | 295.842 | 3.303%
11363 | 29-60 | -60.076 | 29.3809 | 965.0076 | 165.795 | 190.9676 | 227.8662 | 260.4476 | 297.6898 | 3.396%
11364 | 29-60.5 | -60.3473 | 29.3809 | 964.5197 | 166.7487 | 191.7618 | 228.9296 | 261.763 | 299.3075 | 3.484%
11365 | 29-60.5 | -60.6186 | 29.3809 | 964.3409 | 167.6922 | 192.5761 | 230.0246 | 263.121 | 300.9812 | 3.572%
11366 | 29-61 | -60.8899 | 29.3809 | 964.4712 | 168.5731 | 193.373 | 231.0889 | 264.4354 | 302.5955 | 3.656%
11367 | 29-61 | -61.1613 | 29.3809 | 964.9104 | 169.3634 | 194.1231 | 232.0713 | 265.6339 | 304.0518 | 3.735%
11368 | 29-61.5 | -61.4326 | 29.3809 | 965.6583 | 170.1316 | 194.8985 | 233.0912 | 266.8816 | 305.5716 | 3.814%
11369 | 29-61.5 | -61.7039 | 29.3809 | 966.7141 | 170.8289 | 195.6599 | 234.0859 | 268.0932 | 307.042 | 3.887%
11370 | 29-62 | -61.9752 | 29.3809 | 968.0767 | 171.4445 | 196.3949 | 235.0363 | 269.2433 | 308.4297 | 3.954%
11371 | 29-62 | -62.2465 | 29.3809 | 969.7449 | 172.0755 | 197.1753 | 236.0615 | 270.4971 | 309.9572 | 4.023%
11372 | 29-62.5 | -62.5179 | 29.3809 | 971.717 | 172.6888 | 197.9283 | 237.043 | 271.6913 | 311.4058 | 4.091%
11373 | 29-63 | -62.7892 | 29.3809 | 973.9913 | 173.2811 | 198.6485 | 237.9714 | 272.813 | 312.7577 | 4.158%
11374 | 29-63 | -63.0605 | 29.3809 | 976.5656 | 173.9288 | 199.4532 | 239.0346 | 274.1184 | 314.3541 | 4.23%
11375 | 29-63.5 | -63.3318 | 29.3809 | 979.4376 | 174.57 | 200.2435 | 240.0695 | 275.3819 | 315.8915 | 4.303%
11376 | 29-63.5 | -63.6031 | 29.3809 | 982.6045 | 175.1974 | 201.0092 | 241.0607 | 276.5829 | 317.3428 | 4.376%
11377 | 29-64 | -63.8745 | 29.3809 | 986.0637 | 175.8717 | 201.8457 | 242.1638 | 277.9354 | 318.9945 | 4.453%
11378 | 29-64 | -64.1458 | 29.3809 | 989.8119 | 176.5362 | 202.661 | 243.2256 | 279.2267 | 320.5601 | 4.532%
11379 | 29-64.5 | -64.4171 | 29.3809 | 993.8459 | 177.1857 | 203.4479 | 244.2353 | 280.4426 | 322.0209 | 4.61%
11380 | 29-64.5 | -64.6884 | 29.3809 | 998.1622 | 177.8581 | 204.2665 | 245.2919 | 281.7197 | 323.5608 | 4.692%
11381 | 29-65 | -64.9598 | 29.3809 | 1002.7573 | 178.5014 | 205.0414 | 246.2795 | 282.9036 | 324.9772 | 4.773%
11382 | 29-65 | -65.2311 | 29.3809 | 1007.6271 | 179.1201 | 205.7818 | 247.2159 | 284.02 | 326.3064 | 4.851%
11383 | 29-65.5 | -65.5024 | 29.3809 | 1012.7678 | 179.7432 | 206.5318 | 248.171 | 285.1642 | 327.6749 | 4.931%
11384 | 29-66 | -65.7737 | 29.3809 | 1018.1753 | 180.3046 | 207.1918 | 248.9878 | 286.1234 | 328.8005 | 5.006%
11385 | 29-66 | -66.045 | 29.3809 | 1023.8453 | 180.8309 | 207.8046 | 249.7368 | 286.9948 | 329.8143 | 5.078%
11386 | 29-66.5 | -66.3164 | 29.3809 | 1029.7734 | 181.3641 | 208.4349 | 250.5219 | 287.9209 | 330.9059 | 5.15%
11387 | 29-66.5 | -66.5877 | 29.3809 | 1035.9552 | 181.824 | 208.9668 | 251.1664 | 288.666 | 331.767 | 5.215%
11388 | 29-67 | -66.859 | 29.3809 | 1042.3861 | 182.2593 | 209.4758 | 251.7919 | 289.3966 | 332.6199 | 5.276%
11389 | 29-67 | -67.1303 | 29.3809 | 1049.0616 | 182.7174 | 210.032 | 252.5074 | 290.2596 | 333.6583 | 5.337%
11390 | 29-67.5 | -67.4016 | 29.3809 | 1055.977 | 183.1063 | 210.4987 | 253.0993 | 290.9668 | 334.5019 | 5.39%
11391 | 29-67.5 | -67.673 | 29.3809 | 1063.1276 | 183.4745 | 210.9493 | 253.6848 | 291.6776 | 335.3624 | 5.439%
11392 | 29-68 | -67.9443 | 29.3809 | 1070.5086 | 183.8584 | 211.4378 | 254.3468 | 292.5035 | 336.3865 | 5.487%
11393 | 29-68 | -68.2156 | 29.3809 | 1078.1154 | 184.1811 | 211.8465 | 254.8983 | 293.1897 | 337.2352 | 5.528%
11394 | 29-68.5 | -68.4869 | 29.3809 | 1085.943 | 184.4942 | 212.2458 | 255.4407 | 293.8674 | 338.0764 | 5.567%
11395 | 29-69 | -68.7583 | 29.3809 | 1093.9868 | 184.8273 | 212.6752 | 256.0309 | 294.6101 | 339.004 | 5.608%
11396 | 29-69 | -69.0296 | 29.3809 | 1102.2421 | 185.0795 | 212.9932 | 256.4579 | 295.1397 | 339.6574 | 5.641%
11397 | 29-69.5 | -69.3009 | 29.3809 | 1110.7039 | 185.3147 | 213.2926 | 256.8637 | 295.6462 | 340.2856 | 5.671%
11398 | 29-69.5 | -69.5722 | 29.3809 | 1119.3678 | 185.5583 | 213.6081 | 257.2998 | 296.1968 | 340.9753 | 5.7%
11399 | 29-70 | -69.8435 | 29.3809 | 1128.2288 | 185.7081 | 213.7957 | 257.5497 | 296.5053 | 341.3543 | 5.72%
11400 | 29-70 | -70.1149 | 29.3809 | 1137.2825 | 185.8477 | 213.9728 | 257.7891 | 296.8035 | 341.7235 | 5.738%
11401 | 29-70.5 | -70.3862 | 29.3809 | 1146.5243 | 185.9934 | 214.161 | 258.0484 | 297.1304 | 342.1324 | 5.756%
11402 | 29-70.5 | -70.6575 | 29.3809 | 1155.9495 | 186.0406 | 214.2043 | 258.0828 | 297.1546 | 342.1425 | 5.766%
11403 | 29-71 | -70.9288 | 29.3809 | 1165.5537 | 186.0862 | 214.2418 | 258.104 | 297.1581 | 342.1226 | 5.776%
11404 | 29-71 | -71.2001 | 29.3809 | 1175.3325 | 186.1414 | 214.2877 | 258.1313 | 297.1652 | 342.1027 | 5.788%
11405 | 29-71.5 | -71.4715 | 29.3809 | 1185.2816 | 186.1302 | 214.2351 | 258.0049 | 296.9648 | 341.8089 | 5.794%
11406 | 29-71.5 | -71.7428 | 29.3809 | 1195.3966 | 186.134 | 214.2034 | 257.9095 | 296.8053 | 341.5683 | 5.802%
11407 | 29-72 | -72.0141 | 29.3809 | 1205.6733 | 186.148 | 214.1848 | 257.8319 | 296.668 | 341.3551 | 5.811%
11408 | 29-72.5 | -72.2854 | 29.3809 | 1216.1077 | 186.0853 | 214.0567 | 257.5887 | 296.3109 | 340.8555 | 5.813%
11409 | 29-72.5 | -72.5568 | 29.3809 | 1226.6955 | 186.0466 | 213.9584 | 257.385 | 296.0023 | 340.4152 | 5.818%
11410 | 29-73 | -72.8281 | 29.3809 | 1237.433 | 186.0182 | 213.8713 | 257.1938 | 295.7074 | 339.9896 | 5.825%
11411 | 29-73 | -73.0994 | 29.3809 | 1248.3161 | 185.9291 | 213.6992 | 256.8761 | 295.2456 | 339.3478 | 5.826%
11412 | 29-73.5 | -73.3707 | 29.3809 | 1259.3411 | 185.8804 | 213.5854 | 256.6472 | 294.9025 | 338.8614 | 5.83%
11413 | 29-73.5 | -73.642 | 29.3809 | 1270.5042 | 185.8381 | 213.4852 | 256.4448 | 294.5984 | 338.4296 | 5.835%
11414 | 29-74 | -73.9134 | 29.3809 | 1281.8019 | 185.7189 | 213.2852 | 256.1043 | 294.1199 | 337.7794 | 5.829%
11415 | 29-74 | -74.1847 | 29.3809 | 1293.2304 | 185.6225 | 213.1341 | 255.8583 | 293.7812 | 337.3259 | 5.823%
11416 | 29-74.5 | -74.456 | 29.3809 | 1304.7864 | 185.5094 | 212.9777 | 255.6283 | 293.4803 | 336.9379 | 5.811%
11417 | 29-74.5 | -74.7273 | 29.3809 | 1316.4664 | 185.3138 | 212.7263 | 255.2841 | 293.0482 | 336.3992 | 5.785%
11418 | 29-75 | -74.9986 | 29.3809 | 1328.2672 | 185.1057 | 212.4787 | 254.9729 | 292.6787 | 335.961 | 5.755%
11419 | 29-75.5 | -75.27 | 29.3809 | 1340.1854 | 184.8432 | 212.1771 | 254.6105 | 292.2624 | 335.4826 | 5.714%
11420 | 29-75.5 | -75.5413 | 29.3809 | 1352.2181 | 184.4755 | 211.752 | 254.0957 | 291.6671 | 334.7945 | 5.658%
11421 | 29-76 | -75.8126 | 29.3809 | 1364.362 | 184.0836 | 211.3171 | 253.5975 | 291.116 | 334.1855 | 5.595%
11422 | 29-76 | -76.0839 | 29.3809 | 1376.6142 | 183.6326 | 210.8243 | 253.0458 | 290.5172 | 333.5377 | 5.521%
11423 | 29-76.5 | -76.3553 | 29.3809 | 1388.9719 | 183.092 | 210.2323 | 252.3806 | 289.7928 | 332.7513 | 5.435%
11424 | 29-76.5 | -76.6266 | 29.3809 | 1401.4321 | 182.5301 | 209.6354 | 251.7405 | 289.1244 | 332.0604 | 5.343%
11425 | 29-77 | -76.8979 | 29.3809 | 1413.9921 | 181.9059 | 208.9692 | 251.0212 | 288.3683 | 331.2726 | 5.243%
11426 | 29-77 | -77.1692 | 29.3809 | 1426.6492 | 181.2013 | 208.1997 | 250.1604 | 287.4347 | 330.2636 | 5.136%
11427 | 29-77.5 | -77.4405 | 29.3809 | 1439.4009 | 180.5009 | 207.445 | 249.3332 | 286.5535 | 329.3307 | 5.029%
11428 | 29-77.5 | -77.7119 | 29.3809 | 1452.2446 | 179.753 | 206.6278 | 248.418 | 285.5601 | 328.256 | 4.92%
11429 | 29-78 | -77.9832 | 29.3809 | 1465.1779 | 178.9389 | 205.7178 | 247.3649 | 284.385 | 326.946 | 4.806%
11430 | 29-78.5 | -78.2545 | 29.3809 | 1478.1982 | 178.1257 | 204.8126 | 246.3237 | 283.229 | 325.6641 | 4.694%
11431 | 29-78.5 | -78.5258 | 29.3809 | 1491.3034 | 177.196 | 203.7597 | 245.0745 | 281.8076 | 324.0469 | 4.573%
11432 | 29-79 | -78.7971 | 29.3809 | 1504.4912 | 176.0752 | 202.4897 | 243.5192 | 279.9952 | 321.9355 | 4.434%
11433 | 29-79 | -79.0685 | 29.3809 | 1517.7592 | 174.7286 | 201.0893 | 241.7932 | 277.9748 | 319.5718 | 4.275%
11434 | 29-79.5 | -79.3398 | 29.3809 | 1531.1056 | 172.9315 | 199.3752 | 239.6399 | 275.4202 | 316.5449 | 4.076%
11435 | 29-79.5 | -79.6111 | 29.3809 | 1544.528 | 170.5417 | 197.2791 | 236.9696 | 272.2215 | 312.7212 | 3.828%
11436 | 29-80 | -79.8824 | 29.3809 | 1558.0246 | 167.6538 | 194.8146 | 233.8879 | 268.5241 | 308.295 | 3.546%
11437 | 29-80 | -80.1537 | 29.3809 | 1571.5934 | 164.3652 | 192.0313 | 230.4268 | 264.3499 | 303.2745 | 3.248%
11438 | 29-80.5 | -80.4251 | 29.3809 | 1585.2325 | 160.776 | 189.0446 | 226.6985 | 259.8441 | 297.8445 | 2.948%
11439 | 29-80.5 | -80.6964 | 29.3809 | 1598.9399 | 156.9669 | 185.8336 | 222.8202 | 255.1734 | 292.2337 | 2.653%
11440 | 29-81 | -80.9677 | 29.3809 | 1612.7141 | 153.4493 | 182.8849 | 219.2418 | 250.8641 | 287.0567 | 2.405%
11441 | 29-81 | -81.239 | 29.3809 | 1626.5531 | 150.5135 | 180.4301 | 216.2812 | 247.3193 | 282.8202 | 2.214%
11442 | 29-81.5 | -81.5104 | 29.3809 | 1640.4553 | 148.244 | 178.5472 | 214.07 | 244.723 | 279.7733 | 2.075%
11443 | 29-82 | -81.7817 | 29.3809 | 1654.4191 | 146.1973 | 176.8796 | 212.1371 | 242.4698 | 277.1475 | 1.957%
11444 | 29-82 | -82.053 | 29.3809 | 1668.4429 | 144.4029 | 175.4812 | 210.5789 | 240.6924 | 275.1202 | 1.86%
11445 | 29-82.5 | -82.3243 | 29.3809 | 1682.5251 | 142.9878 | 174.4719 | 209.576 | 239.6302 | 274.0037 | 1.788%
11446 | 29-82.5 | -82.5956 | 29.3809 | 1696.6642 | 141.8605 | 173.6707 | 208.8473 | 238.8978 | 273.2827 | 1.733%
11447 | 29-83 | -82.867 | 29.3809 | 1710.8588 | 141.2157 | 173.2261 | 208.5958 | 238.7526 | 273.2807 | 1.703%
11448 | 29-83 | -83.1383 | 29.3809 | 1725.1074 | 141.2401 | 173.2549 | 208.9832 | 239.4049 | 274.2675 | 1.703%
11449 | 29-83.5 | -83.4096 | 29.3809 | 1739.4087 | 141.8212 | 173.7093 | 209.8254 | 240.5774 | 275.8485 | 1.73%
11450 | 29-83.5 | -83.6809 | 29.3809 | 1753.7613 | 142.8619 | 174.5256 | 211.0632 | 242.2112 | 277.9673 | 1.779%
11451 | 29-84 | -83.9522 | 29.3809 | 1768.164 | 144.3139 | 175.6528 | 212.686 | 244.3069 | 280.6387 | 1.85%
11452 | 29-84 | -84.2236 | 29.3809 | 1782.6154 | 146.0137 | 177.0211 | 214.4853 | 246.5729 | 283.4687 | 1.936%
11453 | 29-84.5 | -84.4949 | 29.3809 | 1797.1143 | 147.4504 | 178.1328 | 215.9977 | 248.4687 | 285.8278 | 2.011%
11454 | 29-85 | -84.7662 | 29.3809 | 1811.6596 | 148.4013 | 178.8399 | 217.0412 | 249.7812 | 287.4665 | 2.061%
11455 | 29-85 | -85.0375 | 29.3809 | 1826.25 | 148.7997 | 179.1124 | 217.5007 | 250.339 | 288.1425 | 2.082%
11456 | 29-85.5 | -85.3089 | 29.3809 | 1840.8845 | 149.1028 | 179.3113 | 217.8393 | 250.7361 | 288.6086 | 2.098%
11457 | 29-85.5 | -85.5802 | 29.3809 | 1855.562 | 149.4171 | 179.5454 | 218.1891 | 251.1382 | 289.0715 | 2.116%
11458 | 29-86 | -85.8515 | 29.3809 | 1870.2814 | 149.8133 | 179.914 | 218.5487 | 251.5108 | 289.4531 | 2.141%
11459 | 29-86 | -86.1228 | 29.3809 | 1885.0416 | 150.5019 | 180.5473 | 219.1878 | 252.2201 | 290.2393 | 2.183%
11460 | 29-86.5 | -86.3941 | 29.3809 | 1899.8417 | 151.4908 | 181.421 | 220.1106 | 253.2715 | 291.4368 | 2.245%
11461 | 29-86.5 | -86.6655 | 29.3809 | 1914.6807 | 152.2516 | 182.0896 | 220.7333 | 253.9106 | 292.0826 | 2.295%
11462 | 29-87 | -86.9368 | 29.3809 | 1929.5576 | 152.8645 | 182.6268 | 221.2197 | 254.3793 | 292.5174 | 2.336%
11463 | 29-87 | -87.2081 | 29.3809 | 1944.4715 | 153.3549 | 183.0118 | 221.5931 | 254.7055 | 292.7746 | 2.37%
11464 | 29-87.5 | -87.4794 | 29.3809 | 1959.4215 | 153.8028 | 183.3621 | 221.8929 | 254.9332 | 292.9024 | 2.402%
11465 | 29-88 | -87.7507 | 29.3809 | 1974.4068 | 154.3368 | 183.8362 | 222.3148 | 255.3338 | 293.2666 | 2.441%
11466 | 29-88 | -88.0221 | 29.3809 | 1989.4264 | 154.8825 | 184.3608 | 222.7717 | 255.7957 | 293.725 | 2.481%
11467 | 29-88.5 | -88.2934 | 29.3809 | 2004.4796 | 155.0903 | 184.5884 | 222.8761 | 255.8223 | 293.6492 | 2.5%
11468 | 29-88.5 | -88.5647 | 29.3809 | 2019.5656 | 154.9957 | 184.5367 | 222.7167 | 255.5444 | 293.222 | 2.496%
11469 | 29-89 | -88.836 | 29.3809 | 2034.6835 | 154.6085 | 184.2016 | 222.2835 | 254.9433 | 292.4142 | 2.472%
11470 | 29-89 | -89.1074 | 29.3809 | 2049.8326 | 153.9621 | 183.6103 | 221.5726 | 254.0025 | 291.1927 | 2.429%
11471 | 29-89.5 | -89.3787 | 29.3809 | 2065.0122 | 152.9754 | 182.6492 | 220.563 | 252.7216 | 289.5847 | 2.362%
11472 | 29-89.5 | -89.65 | 29.3809 | 2080.2215 | 151.6904 | 181.4352 | 219.2923 | 251.1442 | 287.6399 | 2.277%
11473 | 29-90 | -89.9213 | 29.3809 | 2095.4599 | 150.2877 | 180.2025 | 217.9358 | 249.4869 | 285.6241 | 2.189%
11474 | 29-90 | -90.1926 | 29.3809 | 2110.7266 | 149.2994 | 179.3518 | 217.0704 | 248.4912 | 284.48 | 2.128%
11475 | 29-90.5 | -90.464 | 29.3809 | 2126.0211 | 148.5529 | 178.7389 | 216.5083 | 247.9164 | 283.9022 | 2.083%
11476 | 29-90.5 | -90.7353 | 29.3809 | 2141.3425 | 147.6885 | 178.0985 | 215.8685 | 247.2714 | 283.2651 | 2.033%
11477 | 30-50 | -50.0371 | 29.6523 | 1191.8564 | 115.102 | 149.3641 | 186.3012 | 210.734 | 238.372 | 0.8107%
11478 | 30-50.5 | -50.3084 | 29.6523 | 1182.1971 | 116.158 | 150.8514 | 187.2678 | 211.9079 | 239.7911 | 0.8382%
11479 | 30-50.5 | -50.5797 | 29.6523 | 1172.7113 | 117.2454 | 152.3752 | 188.2346 | 213.0614 | 241.1637 | 0.8673%
11480 | 30-51 | -50.851 | 29.6523 | 1163.4032 | 118.392 | 153.9665 | 189.2351 | 214.2469 | 242.5655 | 0.8989%
11481 | 30-51 | -51.1224 | 29.6523 | 1154.2772 | 119.6346 | 155.6573 | 190.3236 | 215.5481 | 244.1166 | 0.9344%
11482 | 30-51.5 | -51.3937 | 29.6523 | 1145.3377 | 120.9178 | 157.3313 | 191.4036 | 216.8146 | 245.6 | 0.972%
11483 | 30-51.5 | -51.665 | 29.6523 | 1136.589 | 122.2736 | 159.002 | 192.5207 | 218.1169 | 247.1169 | 1.013%
11484 | 30-52 | -51.9363 | 29.6523 | 1128.0358 | 123.7331 | 160.6928 | 193.7233 | 219.5286 | 248.772 | 1.058%
11485 | 30-52 | -52.2077 | 29.6523 | 1119.6824 | 125.2034 | 162.3132 | 194.8851 | 220.8681 | 250.3157 | 1.105%
11486 | 30-52.5 | -52.479 | 29.6523 | 1111.5334 | 126.708 | 163.8875 | 196.0467 | 222.2012 | 251.8454 | 1.155%
11487 | 30-53 | -52.7503 | 29.6523 | 1103.5934 | 128.2648 | 165.4209 | 197.2399 | 223.5771 | 253.4316 | 1.208%
11488 | 30-53 | -53.0216 | 29.6523 | 1095.867 | 129.8096 | 166.8463 | 198.3788 | 224.8673 | 254.8932 | 1.263%
11489 | 30-53.5 | -53.2929 | 29.6523 | 1088.3587 | 131.393 | 168.2259 | 199.5445 | 226.1951 | 256.4056 | 1.322%
11490 | 30-53.5 | -53.5643 | 29.6523 | 1081.073 | 133.0359 | 169.5698 | 200.7725 | 227.6125 | 258.0411 | 1.385%
11491 | 30-54 | -53.8356 | 29.6523 | 1074.0146 | 134.67 | 170.8006 | 201.9504 | 228.947 | 259.5531 | 1.451%
11492 | 30-54 | -54.1069 | 29.6523 | 1067.188 | 136.3547 | 171.9955 | 203.1815 | 230.3579 | 261.1699 | 1.521%
11493 | 30-54.5 | -54.3782 | 29.6523 | 1060.5976 | 138.1048 | 173.1628 | 204.4928 | 231.8856 | 262.9484 | 1.598%
11494 | 30-54.5 | -54.6495 | 29.6523 | 1054.248 | 139.7808 | 174.1967 | 205.7075 | 233.2795 | 264.5479 | 1.674%
11495 | 30-55 | -54.9209 | 29.6523 | 1048.1435 | 141.453 | 175.2062 | 206.9426 | 234.7171 | 266.2201 | 1.753%
11496 | 30-55 | -55.1922 | 29.6523 | 1042.2884 | 143.1328 | 176.224 | 208.2162 | 236.2231 | 267.998 | 1.837%
11497 | 30-55.5 | -55.4635 | 29.6523 | 1036.6871 | 144.6929 | 177.161 | 209.3775 | 237.5871 | 269.5984 | 1.918%
11498 | 30-55.5 | -55.7348 | 29.6523 | 1031.3436 | 146.2461 | 178.1025 | 210.5737 | 239.0162 | 271.3015 | 2.003%
11499 | 30-56 | -56.0061 | 29.6523 | 1026.2619 | 147.8063 | 179.0583 | 211.8137 | 240.518 | 273.1133 | 2.091%
11500 | 30-56.5 | -56.2775 | 29.6523 | 1021.4462 | 149.2722 | 179.9526 | 212.9611 | 241.8979 | 274.7676 | 2.178%
11501 | 30-56.5 | -56.5488 | 29.6523 | 1016.9 | 150.7298 | 180.8446 | 214.1216 | 243.3062 | 276.4696 | 2.268%
11502 | 30-57 | -56.8201 | 29.6523 | 1012.6271 | 152.1772 | 181.7319 | 215.2854 | 244.7258 | 278.1932 | 2.36%
11503 | 30-57 | -57.0914 | 29.6523 | 1008.6309 | 153.5102 | 182.5379 | 216.3201 | 245.9708 | 279.6865 | 2.448%
11504 | 30-57.5 | -57.3628 | 29.6523 | 1004.9148 | 154.8165 | 183.3296 | 217.3555 | 247.2318 | 281.2155 | 2.538%
11505 | 30-57.5 | -57.6341 | 29.6523 | 1001.4819 | 156.0845 | 184.1002 | 218.3746 | 248.4816 | 282.7404 | 2.627%
11506 | 30-58 | -57.9054 | 29.6523 | 998.3352 | 157.24 | 184.7944 | 219.2815 | 249.5855 | 284.0783 | 2.71%
11507 | 30-58 | -58.1767 | 29.6523 | 995.4773 | 158.4342 | 185.5285 | 220.2695 | 250.8108 | 285.5879 | 2.799%
11508 | 30-58.5 | -58.448 | 29.6523 | 992.9107 | 159.6402 | 186.2874 | 221.3068 | 252.1095 | 287.2008 | 2.89%
11509 | 30-58.5 | -58.7194 | 29.6523 | 990.6378 | 160.7685 | 187.0219 | 222.3055 | 253.3563 | 288.7455 | 2.979%
11510 | 30-59 | -58.9907 | 29.6523 | 988.6605 | 161.9291 | 187.8395 | 223.4366 | 254.7829 | 290.5285 | 3.072%
11511 | 30-59.5 | -59.262 | 29.6523 | 986.9807 | 163.0704 | 188.695 | 224.6222 | 256.2802 | 292.4019 | 3.166%
11512 | 30-59.5 | -59.5333 | 29.6523 | 985.5998 | 164.1221 | 189.5006 | 225.7187 | 257.6501 | 294.1007 | 3.256%
11513 | 30-60 | -59.8046 | 29.6523 | 984.5192 | 165.1821 | 190.3514 | 226.8864 | 259.1163 | 295.9267 | 3.348%
11514 | 30-60 | -60.076 | 29.6523 | 983.7398 | 166.1909 | 191.1964 | 228.0412 | 260.5627 | 297.7243 | 3.439%
11515 | 30-60.5 | -60.3473 | 29.6523 | 983.2624 | 167.0959 | 191.9709 | 229.0756 | 261.8402 | 299.293 | 3.523%
11516 | 30-60.5 | -60.6186 | 29.6523 | 983.0873 | 167.9959 | 192.7702 | 230.1489 | 263.17 | 300.9307 | 3.609%
11517 | 30-61 | -60.8899 | 29.6523 | 983.2149 | 168.8406 | 193.5552 | 231.1957 | 264.4617 | 302.5157 | 3.691%
11518 | 30-61 | -61.1613 | 29.6523 | 983.6448 | 169.6021 | 194.2942 | 232.1607 | 265.6366 | 303.9409 | 3.768%
11519 | 30-61.5 | -61.4326 | 29.6523 | 984.3768 | 170.348 | 195.0597 | 233.1644 | 266.8619 | 305.4306 | 3.846%
11520 | 30-61.5 | -61.7039 | 29.6523 | 985.4101 | 171.0314 | 195.8116 | 234.1421 | 268.0491 | 306.8673 | 3.919%
11521 | 30-62 | -61.9752 | 29.6523 | 986.7438 | 171.6417 | 196.5369 | 235.0738 | 269.1715 | 308.2163 | 3.986%
11522 | 30-62 | -62.2465 | 29.6523 | 988.3768 | 172.2693 | 197.3088 | 236.0815 | 270.3988 | 309.7058 | 4.056%
11523 | 30-62.5 | -62.5179 | 29.6523 | 990.3074 | 172.8794 | 198.0533 | 237.0447 | 271.5652 | 311.1144 | 4.124%
11524 | 30-63 | -62.7892 | 29.6523 | 992.534 | 173.4667 | 198.7619 | 237.9501 | 272.6524 | 312.4176 | 4.192%
11525 | 30-63 | -63.0605 | 29.6523 | 995.0545 | 174.1044 | 199.5486 | 238.9811 | 273.9115 | 313.9498 | 4.264%
11526 | 30-63.5 | -63.3318 | 29.6523 | 997.8668 | 174.7317 | 200.3163 | 239.978 | 275.1217 | 315.4149 | 4.337%
11527 | 30-63.5 | -63.6031 | 29.6523 | 1000.9684 | 175.3424 | 201.0566 | 240.9289 | 276.2676 | 316.7928 | 4.409%
11528 | 30-64 | -63.8745 | 29.6523 | 1004.3565 | 175.9976 | 201.8659 | 241.9907 | 277.5653 | 318.3728 | 4.486%
11529 | 30-64 | -64.1458 | 29.6523 | 1008.0283 | 176.6404 | 202.6514 | 243.0088 | 278.7994 | 319.8647 | 4.563%
11530 | 30-64.5 | -64.4171 | 29.6523 | 1011.9806 | 177.2666 | 203.4072 | 243.9742 | 279.9583 | 321.2529 | 4.64%
11531 | 30-64.5 | -64.6884 | 29.6523 | 1016.2103 | 177.9152 | 204.1958 | 244.9904 | 281.1852 | 322.7307 | 4.719%
11532 | 30-65 | -64.9598 | 29.6523 | 1020.7137 | 178.5353 | 204.942 | 245.9403 | 282.3229 | 324.0907 | 4.798%
11533 | 30-65 | -65.2311 | 29.6523 | 1025.4874 | 179.132 | 205.6554 | 246.8417 | 283.3968 | 325.3684 | 4.874%
11534 | 30-65.5 | -65.5024 | 29.6523 | 1030.5275 | 179.7346 | 206.3807 | 247.7652 | 284.503 | 326.6911 | 4.952%
11535 | 30-66 | -65.7737 | 29.6523 | 1035.8301 | 180.2763 | 207.018 | 248.5545 | 285.4303 | 327.7799 | 5.025%
11536 | 30-66 | -66.045 | 29.6523 | 1041.3912 | 180.785 | 207.612 | 249.2831 | 286.2803 | 328.7714 | 5.095%
11537 | 30-66.5 | -66.3164 | 29.6523 | 1047.2067 | 181.3034 | 208.2285 | 250.0569 | 287.1981 | 329.8586 | 5.165%
11538 | 30-66.5 | -66.5877 | 29.6523 | 1053.2723 | 181.7524 | 208.7525 | 250.6994 | 287.9473 | 330.7318 | 5.227%
11539 | 30-67 | -66.859 | 29.6523 | 1059.5837 | 182.1803 | 209.2587 | 251.3301 | 288.6915 | 331.6092 | 5.287%
11540 | 30-67 | -67.1303 | 29.6523 | 1066.1365 | 182.6344 | 209.8161 | 252.0567 | 289.5756 | 332.6815 | 5.347%
11541 | 30-67.5 | -67.4016 | 29.6523 | 1072.9263 | 183.0204 | 210.2845 | 252.6588 | 290.3015 | 333.5547 | 5.399%
11542 | 30-67.5 | -67.673 | 29.6523 | 1079.9485 | 183.3865 | 210.7374 | 253.2541 | 291.0298 | 334.4425 | 5.447%
11543 | 30-68 | -67.9443 | 29.6523 | 1087.1988 | 183.7697 | 211.2296 | 253.9279 | 291.8757 | 335.4966 | 5.494%
11544 | 30-68 | -68.2156 | 29.6523 | 1094.6724 | 184.0916 | 211.6407 | 254.4875 | 292.5755 | 336.366 | 5.534%
11545 | 30-68.5 | -68.4869 | 29.6523 | 1102.3649 | 184.4029 | 212.0408 | 255.0352 | 293.263 | 337.2226 | 5.573%
11546 | 30-69 | -68.7583 | 29.6523 | 1110.2716 | 184.733 | 212.4697 | 255.6294 | 294.0143 | 338.1645 | 5.613%
11547 | 30-69 | -69.0296 | 29.6523 | 1118.3881 | 184.9816 | 212.7869 | 256.0606 | 294.5531 | 338.8336 | 5.644%
11548 | 30-69.5 | -69.3009 | 29.6523 | 1126.7096 | 185.2132 | 213.0849 | 256.4692 | 295.0665 | 339.4738 | 5.673%
11549 | 30-69.5 | -69.5722 | 29.6523 | 1135.2317 | 185.453 | 213.3981 | 256.9054 | 295.6198 | 340.1695 | 5.702%
11550 | 30-70 | -69.8435 | 29.6523 | 1143.95 | 185.6007 | 213.5849 | 257.157 | 295.9323 | 340.5555 | 5.721%
11551 | 30-70 | -70.1149 | 29.6523 | 1152.8598 | 185.7391 | 213.7623 | 257.3993 | 296.2361 | 340.9337 | 5.739%
11552 | 30-70.5 | -70.3862 | 29.6523 | 1161.9568 | 185.8843 | 213.9512 | 257.6616 | 296.5683 | 341.3509 | 5.757%
11553 | 30-70.5 | -70.6575 | 29.6523 | 1171.2365 | 185.9301 | 213.9936 | 257.6962 | 296.5938 | 341.3636 | 5.766%
11554 | 30-71 | -70.9288 | 29.6523 | 1180.6947 | 185.9762 | 214.0329 | 257.7215 | 296.6039 | 341.3534 | 5.775%
11555 | 30-71 | -71.2001 | 29.6523 | 1190.3271 | 186.0338 | 214.0833 | 257.7571 | 296.6229 | 341.3501 | 5.788%
11556 | 30-71.5 | -71.4715 | 29.6523 | 1200.1293 | 186.0243 | 214.0339 | 257.6363 | 296.4307 | 341.0679 | 5.794%
11557 | 30-71.5 | -71.7428 | 29.6523 | 1210.0973 | 186.0306 | 214.0071 | 257.5502 | 296.2849 | 340.8463 | 5.802%
11558 | 30-72 | -72.0141 | 29.6523 | 1220.227 | 186.0478 | 213.9952 | 257.4854 | 296.1665 | 340.6597 | 5.811%
11559 | 30-72.5 | -72.2854 | 29.6523 | 1230.5143 | 185.9877 | 213.8731 | 257.2545 | 295.8278 | 340.1862 | 5.813%
11560 | 30-72.5 | -72.5568 | 29.6523 | 1240.9553 | 185.9506 | 213.7796 | 257.0613 | 295.5355 | 339.7695 | 5.817%
11561 | 30-73 | -72.8281 | 29.6523 | 1251.5461 | 185.9229 | 213.6962 | 256.8791 | 295.2548 | 339.3651 | 5.824%
11562 | 30-73 | -73.0994 | 29.6523 | 1262.2829 | 185.8336 | 213.5269 | 256.5696 | 294.807 | 338.7445 | 5.824%
11563 | 30-73.5 | -73.3707 | 29.6523 | 1273.1619 | 185.782 | 213.4122 | 256.3436 | 294.4706 | 338.2698 | 5.828%
11564 | 30-73.5 | -73.642 | 29.6523 | 1284.1796 | 185.7343 | 213.3074 | 256.1382 | 294.1656 | 337.8398 | 5.831%
11565 | 30-74 | -73.9134 | 29.6523 | 1295.3323 | 185.6072 | 213.0994 | 255.7897 | 293.6793 | 337.1822 | 5.824%
11566 | 30-74 | -74.1847 | 29.6523 | 1306.6165 | 185.5018 | 212.938 | 255.5317 | 293.3271 | 336.7135 | 5.816%
11567 | 30-74.5 | -74.456 | 29.6523 | 1318.0289 | 185.3768 | 212.7674 | 255.284 | 293.0051 | 336.3007 | 5.802%
11568 | 30-74.5 | -74.7273 | 29.6523 | 1329.566 | 185.1644 | 212.4963 | 254.9152 | 292.5441 | 335.7281 | 5.774%
11569 | 30-75 | -74.9986 | 29.6523 | 1341.2247 | 184.9367 | 212.2264 | 254.5779 | 292.1451 | 335.2565 | 5.74%
11570 | 30-75.5 | -75.27 | 29.6523 | 1353.0017 | 184.6513 | 211.8996 | 254.1866 | 291.6969 | 334.743 | 5.696%
11571 | 30-75.5 | -75.5413 | 29.6523 | 1364.8939 | 184.2582 | 211.4464 | 253.6398 | 291.0665 | 334.0163 | 5.635%
11572 | 30-76 | -75.8126 | 29.6523 | 1376.8984 | 183.8395 | 210.9829 | 253.1107 | 290.4827 | 333.3733 | 5.568%
11573 | 30-76 | -76.0839 | 29.6523 | 1389.0121 | 183.3603 | 210.4612 | 252.5296 | 289.8548 | 332.6974 | 5.49%
11574 | 30-76.5 | -76.3553 | 29.6523 | 1401.2323 | 182.7908 | 209.8407 | 251.838 | 289.1069 | 331.8916 | 5.398%
11575 | 30-76.5 | -76.6266 | 29.6523 | 1413.556 | 182.1992 | 209.216 | 251.1746 | 288.4203 | 331.1897 | 5.302%
11576 | 30-77 | -76.8979 | 29.6523 | 1425.9805 | 181.5436 | 208.5201 | 250.4296 | 287.6435 | 330.3882 | 5.197%
11577 | 30-77 | -77.1692 | 29.6523 | 1438.5033 | 180.8043 | 207.7155 | 249.534 | 286.6763 | 329.3479 | 5.084%
11578 | 30-77.5 | -77.4405 | 29.6523 | 1451.1217 | 180.0659 | 206.9201 | 248.6624 | 285.7482 | 328.3656 | 4.973%
11579 | 30-77.5 | -77.7119 | 29.6523 | 1463.8332 | 179.2772 | 206.0581 | 247.6971 | 284.7001 | 327.2316 | 4.859%
11580 | 30-78 | -77.9832 | 29.6523 | 1476.6353 | 178.4201 | 205.1011 | 246.5912 | 283.4678 | 325.8596 | 4.74%
11581 | 30-78.5 | -78.2545 | 29.6523 | 1489.5258 | 177.5616 | 204.148 | 245.4959 | 282.2526 | 324.5131 | 4.624%
11582 | 30-78.5 | -78.5258 | 29.6523 | 1502.5021 | 176.5993 | 203.0739 | 244.229 | 280.8172 | 322.8873 | 4.499%
11583 | 30-79 | -78.7971 | 29.6523 | 1515.5622 | 175.4826 | 201.8299 | 242.7194 | 279.0699 | 320.8651 | 4.361%
11584 | 30-79 | -79.0685 | 29.6523 | 1528.7038 | 174.2097 | 200.5013 | 241.1008 | 277.1912 | 318.6849 | 4.211%
11585 | 30-79.5 | -79.3398 | 29.6523 | 1541.9248 | 172.4809 | 198.8556 | 239.0505 | 274.7724 | 315.834 | 4.021%
11586 | 30-79.5 | -79.6111 | 29.6523 | 1555.223 | 170.1132 | 196.7952 | 236.4392 | 271.6555 | 312.1197 | 3.778%
11587 | 30-80 | -79.8824 | 29.6523 | 1568.5966 | 167.2037 | 194.328 | 233.3721 | 267.9851 | 307.7362 | 3.497%
11588 | 30-80 | -80.1537 | 29.6523 | 1582.0435 | 163.8699 | 191.4971 | 229.8972 | 263.8022 | 302.7134 | 3.197%
11589 | 30-80.5 | -80.4251 | 29.6523 | 1595.5619 | 160.222 | 188.4341 | 226.1407 | 259.2698 | 297.2596 | 2.895%
11590 | 30-80.5 | -80.6964 | 29.6523 | 1609.1499 | 156.3426 | 185.1249 | 222.2273 | 254.5668 | 291.6208 | 2.599%
11591 | 30-81 | -80.9677 | 29.6523 | 1622.8056 | 152.7091 | 182.0512 | 218.5788 | 250.1837 | 286.3667 | 2.348%
11592 | 30-81 | -81.239 | 29.6523 | 1636.5274 | 149.5923 | 179.441 | 215.4956 | 246.4998 | 281.9722 | 2.15%
11593 | 30-81.5 | -81.5104 | 29.6523 | 1650.3136 | 147.0832 | 177.3716 | 213.1033 | 243.6895 | 278.6727 | 2.001%
11594 | 30-82 | -81.7817 | 29.6523 | 1664.1625 | 144.7907 | 175.5061 | 210.9738 | 241.201 | 275.7657 | 1.875%
11595 | 30-82 | -82.053 | 29.6523 | 1678.0725 | 142.7355 | 173.8779 | 209.1783 | 239.1352 | 273.3892 | 1.769%
11596 | 30-82.5 | -82.3243 | 29.6523 | 1692.042 | 141.0214 | 172.5878 | 207.8695 | 237.698 | 271.8145 | 1.686%
11597 | 30-82.5 | -82.5956 | 29.6523 | 1706.0696 | 139.5264 | 171.4603 | 206.7738 | 236.5122 | 270.5366 | 1.618%
11598 | 30-83 | -82.867 | 29.6523 | 1720.1538 | 138.5208 | 170.6935 | 206.1591 | 235.9163 | 269.9786 | 1.574%
11599 | 30-83 | -83.1383 | 29.6523 | 1734.2931 | 138.2324 | 170.434 | 206.2241 | 236.1659 | 270.4659 | 1.561%
11600 | 30-83.5 | -83.4096 | 29.6523 | 1748.4861 | 138.5439 | 170.6377 | 206.7884 | 236.9889 | 271.6111 | 1.574%
11601 | 30-83.5 | -83.6809 | 29.6523 | 1762.7316 | 139.3382 | 171.2477 | 207.7756 | 238.307 | 273.3352 | 1.608%
11602 | 30-84 | -83.9522 | 29.6523 | 1777.0281 | 140.5584 | 172.2003 | 209.1657 | 240.1098 | 275.6411 | 1.662%
11603 | 30-84 | -84.2236 | 29.6523 | 1791.3745 | 142.0387 | 173.419 | 210.7476 | 242.1 | 278.1245 | 1.731%
11604 | 30-84.5 | -84.4949 | 29.6523 | 1805.7694 | 143.302 | 174.4108 | 212.0835 | 243.7701 | 280.1978 | 1.791%
11605 | 30-85 | -84.7662 | 29.6523 | 1820.2118 | 144.1447 | 175.0301 | 213.0031 | 244.923 | 281.6334 | 1.831%
11606 | 30-85 | -85.0375 | 29.6523 | 1834.7003 | 144.4977 | 175.2516 | 213.4021 | 245.3997 | 282.2027 | 1.847%
11607 | 30-85.5 | -85.3089 | 29.6523 | 1849.2339 | 144.7679 | 175.4173 | 213.6986 | 245.7386 | 282.5908 | 1.86%
11608 | 30-85.5 | -85.5802 | 29.6523 | 1863.8115 | 145.0561 | 175.6297 | 214.0108 | 246.0885 | 282.9835 | 1.874%
11609 | 30-86 | -85.8515 | 29.6523 | 1878.432 | 145.4308 | 175.9859 | 214.345 | 246.4253 | 283.3161 | 1.895%
11610 | 30-86 | -86.1228 | 29.6523 | 1893.0942 | 146.0995 | 176.6124 | 214.9646 | 247.1088 | 284.0689 | 1.932%
11611 | 30-86.5 | -86.3941 | 29.6523 | 1907.7974 | 147.069 | 177.4836 | 215.8727 | 248.1434 | 285.2475 | 1.986%
11612 | 30-86.5 | -86.6655 | 29.6523 | 1922.5403 | 147.8098 | 178.1501 | 216.4868 | 248.775 | 285.8878 | 2.029%
11613 | 30-87 | -86.9368 | 29.6523 | 1937.3221 | 148.4033 | 178.6862 | 216.9645 | 249.2366 | 286.3181 | 2.064%
11614 | 30-87 | -87.2081 | 29.6523 | 1952.1419 | 148.8745 | 179.0701 | 217.3268 | 249.5527 | 286.5667 | 2.093%
11615 | 30-87.5 | -87.4794 | 29.6523 | 1966.9987 | 149.3027 | 179.4139 | 217.6111 | 249.7599 | 286.6686 | 2.119%
11616 | 30-88 | -87.7507 | 29.6523 | 1981.8916 | 149.8183 | 179.8796 | 218.0142 | 250.1345 | 286.9981 | 2.152%
11617 | 30-88 | -88.0221 | 29.6523 | 1996.8198 | 150.3447 | 180.3899 | 218.4489 | 250.5652 | 287.4145 | 2.187%
11618 | 30-88.5 | -88.2934 | 29.6523 | 2011.7824 | 150.52 | 180.5797 | 218.5234 | 250.5498 | 287.282 | 2.201%
11619 | 30-88.5 | -88.5647 | 29.6523 | 2026.7786 | 150.3765 | 180.4623 | 218.3171 | 250.2096 | 286.774 | 2.194%
11620 | 30-89 | -88.836 | 29.6523 | 2041.8077 | 149.9329 | 180.0471 | 217.8308 | 249.5391 | 285.8775 | 2.167%
11621 | 30-89 | -89.1074 | 29.6523 | 2056.8688 | 149.2521 | 179.405 | 217.0962 | 248.5652 | 284.6116 | 2.127%
11622 | 30-89.5 | -89.3787 | 29.6523 | 2071.9612 | 148.254 | 178.423 | 216.0834 | 247.2756 | 282.9877 | 2.066%
11623 | 30-89.5 | -89.65 | 29.6523 | 2087.0841 | 146.9742 | 177.2084 | 214.8233 | 245.7045 | 281.0433 | 1.992%
11624 | 30-90 | -89.9213 | 29.6523 | 2102.2369 | 145.5773 | 175.9709 | 213.4754 | 244.0475 | 279.0167 | 1.915%
11625 | 30-90 | -90.1926 | 29.6523 | 2117.4188 | 144.5957 | 175.1143 | 212.6149 | 243.0458 | 277.8523 | 1.862%
11626 | 30-90.5 | -90.464 | 29.6523 | 2132.6292 | 143.8558 | 174.493 | 212.0557 | 242.4619 | 277.2492 | 1.823%
11627 | 30-90.5 | -90.7353 | 29.6523 | 2147.8674 | 142.9965 | 173.8401 | 211.4214 | 241.8116 | 276.5927 | 1.779%
11628 | 30-50 | -50.0371 | 29.9236 | 1206.9302 | 115.7846 | 150.2315 | 186.8461 | 211.3912 | 239.1616 | 0.8273%
11629 | 30-50.5 | -50.3084 | 29.9236 | 1197.4147 | 116.8123 | 151.6658 | 187.774 | 212.516 | 240.5192 | 0.8545%
11630 | 30-50.5 | -50.5797 | 29.9236 | 1188.0722 | 117.8734 | 153.1336 | 188.7047 | 213.6238 | 241.8345 | 0.8833%
11631 | 30-51 | -50.851 | 29.9236 | 1178.9068 | 118.9968 | 154.6675 | 189.6738 | 214.769 | 243.1853 | 0.9146%
11632 | 30-51 | -51.1224 | 29.9236 | 1169.9227 | 120.2191 | 156.2987 | 190.7352 | 216.0351 | 244.6917 | 0.9501%
11633 | 30-51.5 | -51.3937 | 29.9236 | 1161.1242 | 121.4883 | 157.9202 | 191.797 | 217.2783 | 246.1457 | 0.9876%
11634 | 30-51.5 | -51.665 | 29.9236 | 1152.5154 | 122.8376 | 159.5467 | 192.9052 | 218.5691 | 247.6479 | 1.029%
11635 | 30-52 | -51.9363 | 29.9236 | 1144.1009 | 124.2989 | 161.2019 | 194.1071 | 219.9788 | 249.2995 | 1.075%
11636 | 30-52 | -52.2077 | 29.9236 | 1135.8848 | 125.7757 | 162.7925 | 195.2727 | 221.3212 | 250.845 | 1.122%
11637 | 30-52.5 | -52.479 | 29.9236 | 1127.8716 | 127.2921 | 164.3442 | 196.4437 | 222.6641 | 252.3847 | 1.173%
11638 | 30-53 | -52.7503 | 29.9236 | 1120.0656 | 128.8669 | 165.8639 | 197.6529 | 224.0577 | 253.9904 | 1.228%
11639 | 30-53 | -53.0216 | 29.9236 | 1112.4713 | 130.4391 | 167.2864 | 198.8158 | 225.3751 | 255.483 | 1.285%
11640 | 30-53.5 | -53.2929 | 29.9236 | 1105.093 | 132.0556 | 168.6678 | 200.0079 | 226.7311 | 257.0254 | 1.346%
11641 | 30-53.5 | -53.5643 | 29.9236 | 1097.935 | 133.7363 | 170.0169 | 201.2629 | 228.1754 | 258.6873 | 1.412%
11642 | 30-54 | -53.8356 | 29.9236 | 1091.0019 | 135.4102 | 171.2559 | 202.468 | 229.537 | 260.2256 | 1.48%
11643 | 30-54 | -54.1069 | 29.9236 | 1084.2978 | 137.1325 | 172.462 | 203.7223 | 230.9695 | 261.8616 | 1.554%
11644 | 30-54.5 | -54.3782 | 29.9236 | 1077.8271 | 138.9166 | 173.6425 | 205.0511 | 232.5115 | 263.65 | 1.634%
11645 | 30-54.5 | -54.6495 | 29.9236 | 1071.5941 | 140.6224 | 174.6925 | 206.2785 | 233.9146 | 265.2538 | 1.713%
11646 | 30-55 | -54.9209 | 29.9236 | 1065.6029 | 142.3159 | 175.7109 | 207.5163 | 235.3485 | 266.9143 | 1.796%
11647 | 30-55 | -55.1922 | 29.9236 | 1059.8576 | 144.0073 | 176.7295 | 208.7818 | 236.8373 | 268.6636 | 1.882%
11648 | 30-55.5 | -55.4635 | 29.9236 | 1054.3624 | 145.5755 | 177.6636 | 209.9301 | 238.1784 | 270.2287 | 1.966%
11649 | 30-55.5 | -55.7348 | 29.9236 | 1049.1211 | 147.1364 | 178.6009 | 211.1116 | 239.5824 | 271.8937 | 2.054%
11650 | 30-56 | -56.0061 | 29.9236 | 1044.1376 | 148.7037 | 179.5513 | 212.3357 | 241.058 | 273.6665 | 2.145%
11651 | 30-56.5 | -56.2775 | 29.9236 | 1039.4156 | 150.1745 | 180.4391 | 213.4687 | 242.4157 | 275.2887 | 2.234%
11652 | 30-56.5 | -56.5488 | 29.9236 | 1034.9587 | 151.6322 | 181.3222 | 214.614 | 243.8027 | 276.9619 | 2.326%
11653 | 30-57 | -56.8201 | 29.9236 | 1030.7704 | 153.0726 | 182.1977 | 215.7608 | 245.2004 | 278.6577 | 2.421%
11654 | 30-57 | -57.0914 | 29.9236 | 1026.8539 | 154.3912 | 182.9886 | 216.7759 | 246.4216 | 280.1222 | 2.51%
11655 | 30-57.5 | -57.3628 | 29.9236 | 1023.2125 | 155.6773 | 183.7643 | 217.7903 | 247.6569 | 281.6199 | 2.6%
11656 | 30-57.5 | -57.6341 | 29.9236 | 1019.849 | 156.9186 | 184.5182 | 218.7874 | 248.8798 | 283.1118 | 2.69%
11657 | 30-58 | -57.9054 | 29.9236 | 1016.7662 | 158.0417 | 185.1948 | 219.6712 | 249.9553 | 284.4153 | 2.773%
11658 | 30-58 | -58.1767 | 29.9236 | 1013.9668 | 159.1965 | 185.9107 | 220.635 | 251.1509 | 285.8883 | 2.861%
11659 | 30-58.5 | -58.448 | 29.9236 | 1011.4529 | 160.3558 | 186.651 | 221.6472 | 252.4184 | 287.4626 | 2.951%
11660 | 30-58.5 | -58.7194 | 29.9236 | 1009.2269 | 161.4366 | 187.3645 | 222.6169 | 253.6285 | 288.9613 | 3.038%
11661 | 30-59 | -58.9907 | 29.9236 | 1007.2907 | 162.5435 | 188.1548 | 223.7095 | 255.006 | 290.6821 | 3.128%
11662 | 30-59.5 | -59.262 | 29.9236 | 1005.6458 | 163.6269 | 188.9793 | 224.8517 | 256.4479 | 292.4858 | 3.22%
11663 | 30-59.5 | -59.5333 | 29.9236 | 1004.2937 | 164.6208 | 189.7556 | 225.908 | 257.7671 | 294.1211 | 3.306%
11664 | 30-60 | -59.8046 | 29.9236 | 1003.2357 | 165.6243 | 190.5782 | 227.0357 | 259.182 | 295.8819 | 3.395%
11665 | 30-60 | -60.076 | 29.9236 | 1002.4726 | 166.5784 | 191.3971 | 228.1525 | 260.5791 | 297.6163 | 3.483%
11666 | 30-60.5 | -60.3473 | 29.9236 | 1002.0052 | 167.4332 | 192.149 | 229.154 | 261.8138 | 299.1302 | 3.564%
11667 | 30-60.5 | -60.6186 | 29.9236 | 1001.8338 | 168.2881 | 192.9298 | 230.2003 | 263.1086 | 300.723 | 3.646%
11668 | 30-61 | -60.8899 | 29.9236 | 1001.9587 | 169.0941 | 193.6991 | 231.2244 | 264.3708 | 302.2701 | 3.726%
11669 | 30-61 | -61.1613 | 29.9236 | 1002.3796 | 169.8235 | 194.4236 | 232.1683 | 265.5181 | 303.6598 | 3.802%
11670 | 30-61.5 | -61.4326 | 29.9236 | 1003.0962 | 170.5442 | 195.1767 | 233.153 | 266.7181 | 305.1164 | 3.877%
11671 | 30-61.5 | -61.7039 | 29.9236 | 1004.1079 | 171.2112 | 195.9172 | 234.1117 | 267.8788 | 306.5175 | 3.95%
11672 | 30-62 | -61.9752 | 29.9236 | 1005.4139 | 171.8148 | 196.6317 | 235.0237 | 268.9728 | 307.8271 | 4.018%
11673 | 30-62 | -62.2465 | 29.9236 | 1007.0128 | 172.4387 | 197.3951 | 236.0143 | 270.1744 | 309.28 | 4.088%
11674 | 30-62.5 | -62.5179 | 29.9236 | 1008.9034 | 173.0468 | 198.133 | 236.9632 | 271.3185 | 310.6562 | 4.157%
11675 | 30-63 | -62.7892 | 29.9236 | 1011.084 | 173.6308 | 198.8338 | 237.8525 | 272.3814 | 311.9247 | 4.226%
11676 | 30-63 | -63.0605 | 29.9236 | 1013.5527 | 174.2604 | 199.6061 | 238.8578 | 273.6035 | 313.4058 | 4.298%
11677 | 30-63.5 | -63.3318 | 29.9236 | 1016.3074 | 174.8759 | 200.3552 | 239.8242 | 274.7715 | 314.8138 | 4.371%
11678 | 30-63.5 | -63.6031 | 29.9236 | 1019.3459 | 175.4714 | 201.0738 | 240.7421 | 275.8733 | 316.1339 | 4.443%
11679 | 30-64 | -63.8745 | 29.9236 | 1022.6654 | 176.1075 | 201.8571 | 241.7662 | 277.1218 | 317.6505 | 4.518%
11680 | 30-64 | -64.1458 | 29.9236 | 1026.2634 | 176.7279 | 202.6129 | 242.7423 | 278.3022 | 319.0741 | 4.593%
11681 | 30-64.5 | -64.4171 | 29.9236 | 1030.1368 | 177.3297 | 203.3369 | 243.6636 | 279.4052 | 320.3924 | 4.668%
11682 | 30-64.5 | -64.6884 | 29.9236 | 1034.2826 | 177.9527 | 204.0932 | 244.6363 | 280.578 | 321.803 | 4.746%
11683 | 30-65 | -64.9598 | 29.9236 | 1038.6975 | 178.5474 | 204.8076 | 245.5436 | 281.6629 | 323.0981 | 4.821%
11684 | 30-65 | -65.2311 | 29.9236 | 1043.3781 | 179.1196 | 205.4904 | 246.4042 | 282.6864 | 324.3138 | 4.896%
11685 | 30-65.5 | -65.5024 | 29.9236 | 1048.3207 | 179.6987 | 206.1864 | 247.2889 | 283.7448 | 325.5778 | 4.971%
11686 | 30-66 | -65.7737 | 29.9236 | 1053.5218 | 180.2178 | 206.7967 | 248.0442 | 284.6317 | 326.6186 | 5.042%
11687 | 30-66 | -66.045 | 29.9236 | 1058.9773 | 180.7054 | 207.367 | 248.7451 | 285.4506 | 327.5751 | 5.109%
11688 | 30-66.5 | -66.3164 | 29.9236 | 1064.6836 | 181.2054 | 207.964 | 249.4981 | 286.3468 | 328.6402 | 5.177%
11689 | 30-66.5 | -66.5877 | 29.9236 | 1070.6364 | 181.6401 | 208.475 | 250.1301 | 287.0885 | 329.5102 | 5.237%
11690 | 30-67 | -66.859 | 29.9236 | 1076.8317 | 182.0575 | 208.9731 | 250.758 | 287.8352 | 330.3972 | 5.295%
11691 | 30-67 | -67.1303 | 29.9236 | 1083.2653 | 182.5041 | 209.5266 | 251.4869 | 288.7283 | 331.487 | 5.353%
11692 | 30-67.5 | -67.4016 | 29.9236 | 1089.933 | 182.8848 | 209.9929 | 252.0931 | 289.4647 | 332.3788 | 5.404%
11693 | 30-67.5 | -67.673 | 29.9236 | 1096.8304 | 183.2468 | 210.445 | 252.6935 | 290.204 | 333.2852 | 5.451%
11694 | 30-68 | -67.9443 | 29.9236 | 1103.9533 | 183.6269 | 210.9374 | 253.3734 | 291.062 | 334.3589 | 5.497%
11695 | 30-68 | -68.2156 | 29.9236 | 1111.2973 | 183.9459 | 211.3483 | 253.9374 | 291.7709 | 335.2433 | 5.536%
11696 | 30-68.5 | -68.4869 | 29.9236 | 1118.858 | 184.2531 | 211.7462 | 254.487 | 292.4641 | 336.1107 | 5.574%
11697 | 30-69 | -68.7583 | 29.9236 | 1126.631 | 184.5772 | 212.1713 | 255.081 | 293.219 | 337.0609 | 5.613%
11698 | 30-69 | -69.0296 | 29.9236 | 1134.6119 | 184.8202 | 212.4858 | 255.5148 | 293.7659 | 337.745 | 5.643%
11699 | 30-69.5 | -69.3009 | 29.9236 | 1142.7964 | 185.0467 | 212.7814 | 255.926 | 294.287 | 338.3994 | 5.67%
11700 | 30-69.5 | -69.5722 | 29.9236 | 1151.18 | 185.2816 | 213.0918 | 256.3634 | 294.8455 | 339.1053 | 5.698%
11701 | 30-70 | -69.8435 | 29.9236 | 1159.7585 | 185.4263 | 213.2783 | 256.6196 | 295.1676 | 339.5073 | 5.716%
11702 | 30-70 | -70.1149 | 29.9236 | 1168.5275 | 185.5621 | 213.4558 | 256.8667 | 295.481 | 339.9013 | 5.732%
11703 | 30-70.5 | -70.3862 | 29.9236 | 1177.4827 | 185.7048 | 213.6444 | 257.1326 | 295.8208 | 340.331 | 5.749%
11704 | 30-70.5 | -70.6575 | 29.9236 | 1186.6199 | 185.7482 | 213.6862 | 257.1699 | 295.8524 | 340.3543 | 5.758%
11705 | 30-71 | -70.9288 | 29.9236 | 1195.9349 | 185.7932 | 213.7269 | 257.2013 | 295.8732 | 340.3607 | 5.767%
11706 | 30-71 | -71.2001 | 29.9236 | 1205.4235 | 185.8516 | 213.7813 | 257.2466 | 295.9078 | 340.3804 | 5.778%
11707 | 30-71.5 | -71.4715 | 29.9236 | 1215.0815 | 185.8424 | 213.7352 | 257.1347 | 295.7299 | 340.1194 | 5.784%
11708 | 30-71.5 | -71.7428 | 29.9236 | 1224.9051 | 185.8499 | 213.7133 | 257.0598 | 295.6018 | 339.9237 | 5.792%
11709 | 30-72 | -72.0141 | 29.9236 | 1234.8902 | 185.8693 | 213.7077 | 257.0089 | 295.5047 | 339.7678 | 5.8%
11710 | 30-72.5 | -72.2854 | 29.9236 | 1245.0328 | 185.8117 | 213.5925 | 256.7925 | 295.1883 | 339.3265 | 5.802%
11711 | 30-72.5 | -72.5568 | 29.9236 | 1255.3292 | 185.7756 | 213.5035 | 256.6101 | 294.9132 | 338.9352 | 5.806%
11712 | 30-73 | -72.8281 | 29.9236 | 1265.7755 | 185.7476 | 213.4225 | 256.4354 | 294.6453 | 338.55 | 5.812%
11713 | 30-73 | -73.0994 | 29.9236 | 1276.368 | 185.657 | 213.2549 | 256.1329 | 294.2098 | 337.9487 | 5.811%
11714 | 30-73.5 | -73.3707 | 29.9236 | 1287.1031 | 185.6014 | 213.1375 | 255.907 | 293.8765 | 337.481 | 5.813%
11715 | 30-73.5 | -73.642 | 29.9236 | 1297.9772 | 185.5468 | 213.0258 | 255.6949 | 293.5652 | 337.0455 | 5.815%
11716 | 30-74 | -73.9134 | 29.9236 | 1308.9868 | 185.4114 | 212.8085 | 255.3356 | 293.0669 | 336.3747 | 5.807%
11717 | 30-74 | -74.1847 | 29.9236 | 1320.1284 | 185.2959 | 212.6344 | 255.0607 | 292.6939 | 335.8805 | 5.798%
11718 | 30-74.5 | -74.456 | 29.9236 | 1331.3988 | 185.1582 | 212.447 | 254.7892 | 292.3416 | 335.4295 | 5.782%
11719 | 30-74.5 | -74.7273 | 29.9236 | 1342.7945 | 184.9291 | 212.1545 | 254.3913 | 291.8441 | 334.8114 | 5.752%
11720 | 30-75 | -74.9986 | 29.9236 | 1354.3126 | 184.6826 | 211.8614 | 254.0234 | 291.4077 | 334.2942 | 5.716%
11721 | 30-75.5 | -75.27 | 29.9236 | 1365.9497 | 184.3762 | 211.5092 | 253.6003 | 290.9214 | 333.7355 | 5.668%
11722 | 30-75.5 | -75.5413 | 29.9236 | 1377.7028 | 183.9604 | 211.0298 | 253.0216 | 290.2543 | 332.9663 | 5.605%
11723 | 30-76 | -75.8126 | 29.9236 | 1389.569 | 183.518 | 210.5402 | 252.4629 | 289.638 | 332.2877 | 5.533%
11724 | 30-76 | -76.0839 | 29.9236 | 1401.5454 | 183.0141 | 209.9927 | 251.8548 | 288.9826 | 331.5842 | 5.451%
11725 | 30-76.5 | -76.3553 | 29.9236 | 1413.629 | 182.4188 | 209.3468 | 251.1393 | 288.2129 | 330.76 | 5.356%
11726 | 30-76.5 | -76.6266 | 29.9236 | 1425.8172 | 181.8001 | 208.696 | 250.4526 | 287.5067 | 330.0435 | 5.254%
11727 | 30-77 | -76.8979 | 29.9236 | 1438.1072 | 181.1155 | 207.9723 | 249.6827 | 286.7087 | 329.2261 | 5.145%
11728 | 30-77 | -77.1692 | 29.9236 | 1450.4964 | 180.3448 | 207.136 | 248.7561 | 285.712 | 328.1589 | 5.028%
11729 | 30-77.5 | -77.4405 | 29.9236 | 1462.9822 | 179.5715 | 206.3034 | 247.8448 | 284.7422 | 327.1335 | 4.913%
11730 | 30-77.5 | -77.7119 | 29.9236 | 1475.5622 | 178.7451 | 205.401 | 246.8353 | 283.6472 | 325.9499 | 4.794%
11731 | 30-78 | -77.9832 | 29.9236 | 1488.2339 | 177.8482 | 204.4022 | 245.6845 | 282.3678 | 324.5291 | 4.671%
11732 | 30-78.5 | -78.2545 | 29.9236 | 1500.9949 | 176.9419 | 203.4059 | 244.5419 | 281.1023 | 323.1293 | 4.549%
11733 | 30-78.5 | -78.5258 | 29.9236 | 1513.843 | 175.9401 | 202.31 | 243.2563 | 279.6523 | 321.4945 | 4.421%
11734 | 30-79 | -78.7971 | 29.9236 | 1526.7758 | 174.807 | 201.0817 | 241.7789 | 277.9533 | 319.5407 | 4.283%
11735 | 30-79 | -79.0685 | 29.9236 | 1539.7913 | 173.5735 | 199.8046 | 240.2401 | 276.1816 | 317.5009 | 4.138%
11736 | 30-79.5 | -79.3398 | 29.9236 | 1552.8872 | 171.8882 | 198.2128 | 238.2726 | 273.8734 | 314.7945 | 3.954%
11737 | 30-79.5 | -79.6111 | 29.9236 | 1566.0616 | 169.5396 | 196.1883 | 235.7206 | 270.8382 | 311.1896 | 3.716%
11738 | 30-80 | -79.8824 | 29.9236 | 1579.3124 | 166.627 | 193.7263 | 232.6888 | 267.2202 | 306.8796 | 3.438%
11739 | 30-80 | -80.1537 | 29.9236 | 1592.6376 | 163.2724 | 190.865 | 229.2292 | 263.0644 | 301.8987 | 3.139%
11740 | 30-80.5 | -80.4251 | 29.9236 | 1606.0355 | 159.5886 | 187.7466 | 225.4734 | 258.5414 | 296.465 | 2.838%
11741 | 30-80.5 | -80.6964 | 29.9236 | 1619.504 | 155.6588 | 184.3621 | 221.5508 | 253.8371 | 290.8351 | 2.543%
11742 | 30-81 | -80.9677 | 29.9236 | 1633.0414 | 151.9241 | 181.1789 | 217.8508 | 249.4019 | 285.5295 | 2.289%
11743 | 30-81 | -81.239 | 29.9236 | 1646.646 | 148.6345 | 178.4171 | 214.6541 | 245.5891 | 280.9886 | 2.086%
11744 | 30-81.5 | -81.5104 | 29.9236 | 1660.3161 | 145.881 | 176.1527 | 212.0796 | 242.5627 | 277.4331 | 1.929%
11745 | 30-82 | -81.7817 | 29.9236 | 1674.05 | 143.3414 | 174.0786 | 209.7514 | 239.836 | 274.2413 | 1.795%
11746 | 30-82 | -82.053 | 29.9236 | 1687.8461 | 141.0281 | 172.215 | 207.724 | 237.4889 | 271.5246 | 1.681%
11747 | 30-82.5 | -82.3243 | 29.9236 | 1701.7028 | 139.0306 | 170.6471 | 206.1262 | 235.6974 | 269.5176 | 1.589%
11748 | 30-82.5 | -82.5956 | 29.9236 | 1715.6187 | 137.1949 | 169.2027 | 204.6906 | 234.0927 | 267.7254 | 1.51%
11749 | 30-83 | -82.867 | 29.9236 | 1729.5922 | 135.8438 | 168.1142 | 203.7294 | 233.067 | 266.6375 | 1.455%
11750 | 30-83 | -83.1383 | 29.9236 | 1743.622 | 135.2336 | 167.5489 | 203.4655 | 232.9057 | 266.6149 | 1.43%
11751 | 30-83.5 | -83.4096 | 29.9236 | 1757.7065 | 135.2449 | 167.4772 | 203.7263 | 233.3475 | 267.2852 | 1.43%
11752 | 30-83.5 | -83.6809 | 29.9236 | 1771.8445 | 135.7564 | 167.8478 | 204.4309 | 234.3102 | 268.5659 | 1.45%
11753 | 30-84 | -83.9522 | 29.9236 | 1786.0347 | 136.7098 | 168.5883 | 205.5558 | 235.7797 | 270.4563 | 1.489%
11754 | 30-84 | -84.2236 | 29.9236 | 1800.2757 | 137.9384 | 169.6175 | 206.8896 | 237.4567 | 272.5478 | 1.541%
11755 | 30-84.5 | -84.4949 | 29.9236 | 1814.5663 | 139.0014 | 170.4564 | 208.0249 | 238.8716 | 274.2996 | 1.586%
11756 | 30-85 | -84.7662 | 29.9236 | 1828.9053 | 139.7155 | 170.9656 | 208.8045 | 239.8447 | 275.5067 | 1.616%
11757 | 30-85 | -85.0375 | 29.9236 | 1843.2916 | 140.0154 | 171.1258 | 209.1373 | 240.233 | 275.9605 | 1.628%
11758 | 30-85.5 | -85.3089 | 29.9236 | 1857.7238 | 140.2462 | 171.25 | 209.3875 | 240.5082 | 276.2632 | 1.638%
11759 | 30-85.5 | -85.5802 | 29.9236 | 1872.2011 | 140.5009 | 171.431 | 209.6568 | 240.7988 | 276.5762 | 1.649%
11760 | 30-86 | -85.8515 | 29.9236 | 1886.7221 | 140.8452 | 171.7628 | 209.9577 | 241.0894 | 276.8469 | 1.666%
11761 | 30-86 | -86.1228 | 29.9236 | 1901.286 | 141.4847 | 172.3696 | 210.5471 | 241.7326 | 277.5471 | 1.697%
11762 | 30-86.5 | -86.3941 | 29.9236 | 1915.8917 | 142.4252 | 173.2246 | 211.4268 | 242.7319 | 278.6821 | 1.743%
11763 | 30-86.5 | -86.6655 | 29.9236 | 1930.5381 | 143.138 | 173.8779 | 212.022 | 243.342 | 279.2985 | 1.779%
11764 | 30-87 | -86.9368 | 29.9236 | 1945.2243 | 143.7041 | 174.4015 | 212.4799 | 243.7823 | 279.7062 | 1.809%
11765 | 30-87 | -87.2081 | 29.9236 | 1959.9494 | 144.1482 | 174.7726 | 212.8207 | 244.0752 | 279.9304 | 1.832%
11766 | 30-87.5 | -87.4794 | 29.9236 | 1974.7123 | 144.5504 | 175.1017 | 213.0839 | 244.257 | 280.002 | 1.854%
11767 | 30-88 | -87.7507 | 29.9236 | 1989.5123 | 145.0423 | 175.5527 | 213.4646 | 244.6037 | 280.2973 | 1.881%
11768 | 30-88 | -88.0221 | 29.9236 | 2004.3485 | 145.5457 | 176.0465 | 213.8767 | 245.0054 | 280.6774 | 1.91%
11769 | 30-88.5 | -88.2934 | 29.9236 | 2019.2199 | 145.6931 | 176.2086 | 213.9302 | 244.9624 | 280.5093 | 1.919%
11770 | 30-88.5 | -88.5647 | 29.9236 | 2034.1258 | 145.5126 | 176.0463 | 213.6929 | 244.5823 | 279.9514 | 1.91%
11771 | 30-89 | -88.836 | 29.9236 | 2049.0654 | 145.0284 | 175.5775 | 213.1731 | 243.8695 | 279.0021 | 1.885%
11772 | 30-89 | -89.1074 | 29.9236 | 2064.0378 | 144.3224 | 174.9007 | 212.4265 | 242.8797 | 277.7158 | 1.847%
11773 | 30-89.5 | -89.3787 | 29.9236 | 2079.0424 | 143.3161 | 173.9046 | 211.4158 | 241.5905 | 276.0902 | 1.794%
11774 | 30-89.5 | -89.65 | 29.9236 | 2094.0783 | 142.0413 | 172.6905 | 210.1688 | 240.0315 | 274.1561 | 1.729%
11775 | 30-90 | -89.9213 | 29.9236 | 2109.1448 | 140.6524 | 171.4529 | 208.8369 | 238.3874 | 272.1379 | 1.661%
11776 | 30-90 | -90.1926 | 29.9236 | 2124.2413 | 139.6803 | 170.5952 | 207.9881 | 237.3911 | 270.9699 | 1.616%
11777 | 30-90.5 | -90.464 | 29.9236 | 2139.367 | 138.9508 | 169.9709 | 207.4389 | 236.8087 | 270.3571 | 1.583%
11778 | 30-90.5 | -90.7353 | 29.9236 | 2154.5213 | 138.1016 | 169.3124 | 206.8172 | 236.1639 | 269.6958 | 1.546%
11779 | 1-61.5 | -61.4326 | 1.1635 | 986.7765 | 0.0003489 | 0.00072837 | 0.0026572 | 0.0091507 | 0.037667 | 0.0004651%
11780 | 1-61 | -61.1613 | 1.1635 | 985.9364 | 0.00035438 | 0.00074402 | 0.0027476 | 0.0096115 | 0.040373 | 0.0005153%
11781 | 1-61 | -60.8899 | 1.1635 | 985.4428 | 0.00035927 | 0.00075859 | 0.0028373 | 0.010082 | 0.043173 | 0.0005687%
11782 | 1-60.5 | -60.6186 | 1.1635 | 985.2965 | 0.0004679 | 0.00094473 | 0.003282 | 0.011242 | 0.047623 | 0.0005005%
11783 | 1-60.5 | -60.3473 | 1.1635 | 985.4974 | 0.00025635 | 0.00063669 | 0.0028344 | 0.01102 | 0.050168 | 0.0009892%
11784 | 1-60 | -60.076 | 1.1635 | 986.0455 | 0.00023702 | 0.00060303 | 0.0028273 | 0.011459 | 0.053925 | 0.001173%
11785 | 1-60 | -59.8046 | 1.1635 | 986.94 | 0.00023523 | 0.00060503 | 0.0029175 | 0.012122 | 0.058261 | 0.001312%
11786 | 1-59.5 | -59.5333 | 1.1635 | 988.1801 | 0.00023614 | 0.00061382 | 0.0030327 | 0.01286 | 0.062855 | 0.001446%
11787 | 1-59.5 | -59.262 | 1.1635 | 989.7645 | 0.00023755 | 0.00062403 | 0.0031544 | 0.013625 | 0.067598 | 0.001581%
11788 | 1-59 | -58.9907 | 1.1635 | 991.6915 | 0.00024157 | 0.00064597 | 0.0033648 | 0.014796 | 0.074153 | 0.001756%
11789 | 1-58.5 | -58.7194 | 1.1635 | 993.9591 | 0.00024188 | 0.00065893 | 0.0035592 | 0.016029 | 0.081583 | 0.001974%
11790 | 1-58.5 | -58.448 | 1.1635 | 996.565 | 0.00023585 | 0.00065777 | 0.0037237 | 0.017291 | 0.089843 | 0.002253%
11791 | 1-58 | -58.1767 | 1.1635 | 999.5066 | 0.00023306 | 0.00066833 | 0.0039682 | 0.018933 | 0.1 | 0.002566%
11792 | 1-58 | -57.9054 | 1.1635 | 1002.7809 | 0.0002339 | 0.00069119 | 0.0042925 | 0.020956 | 0.11213 | 0.002905%
11793 | 1-57.5 | -57.6341 | 1.1635 | 1006.3846 | 0.00023775 | 0.00072456 | 0.0046882 | 0.023336 | 0.12621 | 0.003263%
11794 | 1-57.5 | -57.3628 | 1.1635 | 1010.3143 | 0.00028932 | 0.00086181 | 0.0054107 | 0.02661 | 0.14313 | 0.003325%
11795 | 1-57 | -57.0914 | 1.1635 | 1014.566 | 0.00031285 | 0.00095545 | 0.006067 | 0.029861 | 0.16049 | 0.003579%
11796 | 1-57 | -56.8201 | 1.1635 | 1019.1359 | 0.0003344 | 0.0010346 | 0.0066681 | 0.033011 | 0.17785 | 0.003834%
11797 | 1-61.5 | -61.4326 | 1.4348 | 968.0579 | 0.00036538 | 0.00081712 | 0.0035116 | 0.014041 | 0.066429 | 0.001102%
11798 | 1-61 | -61.1613 | 1.4348 | 967.202 | 0.00036887 | 0.00082558 | 0.0035754 | 0.014514 | 0.070029 | 0.001177%
11799 | 1-61 | -60.8899 | 1.4348 | 966.6991 | 0.00037206 | 0.00083391 | 0.0036431 | 0.015015 | 0.073836 | 0.001256%
11800 | 1-60.5 | -60.6186 | 1.4348 | 966.55 | 0.0004793 | 0.0010151 | 0.0040738 | 0.016242 | 0.079498 | 0.00112%
11801 | 1-60.5 | -60.3473 | 1.4348 | 966.7547 | 0.00026705 | 0.00070505 | 0.0036333 | 0.016182 | 0.083688 | 0.001885%
11802 | 1-60 | -60.076 | 1.4348 | 967.3131 | 0.00024772 | 0.00067262 | 0.0036579 | 0.016897 | 0.089644 | 0.002157%
11803 | 1-60 | -59.8046 | 1.4348 | 968.2245 | 0.00024647 | 0.00067874 | 0.0038057 | 0.017973 | 0.096894 | 0.002368%
11804 | 1-59.5 | -59.5333 | 1.4348 | 969.4879 | 0.00024823 | 0.00069336 | 0.0039944 | 0.01921 | 0.10486 | 0.002578%
11805 | 1-59.5 | -59.262 | 1.4348 | 971.102 | 0.0002507 | 0.00071052 | 0.0042004 | 0.02053 | 0.11326 | 0.00279%
11806 | 1-59 | -58.9907 | 1.4348 | 973.065 | 0.00025594 | 0.00074078 | 0.0045163 | 0.022423 | 0.12475 | 0.00306%
11807 | 1-58.5 | -58.7194 | 1.4348 | 975.3748 | 0.00025775 | 0.00076438 | 0.0048516 | 0.02465 | 0.13919 | 0.003418%
11808 | 1-58.5 | -58.448 | 1.4348 | 978.0289 | 0.0002536 | 0.00077676 | 0.0052013 | 0.027251 | 0.15715 | 0.003897%
11809 | 1-58 | -58.1767 | 1.4348 | 981.0246 | 0.00025336 | 0.00080543 | 0.0056872 | 0.030605 | 0.17944 | 0.004434%
11810 | 1-58 | -57.9054 | 1.4348 | 984.3587 | 0.00025686 | 0.00084781 | 0.0062809 | 0.034584 | 0.20558 | 0.005%
11811 | 1-57.5 | -57.6341 | 1.4348 | 988.0277 | 0.00026374 | 0.00090355 | 0.0069877 | 0.039231 | 0.23506 | 0.005578%
11812 | 1-57.5 | -57.3628 | 1.4348 | 992.0281 | 0.00031876 | 0.0010657 | 0.0080475 | 0.044922 | 0.26785 | 0.005755%
11813 | 1-57 | -57.0914 | 1.4348 | 996.3558 | 0.00034611 | 0.0011864 | 0.009064 | 0.05072 | 0.30142 | 0.006158%
11814 | 1-57 | -56.8201 | 1.4348 | 1001.0065 | 0.00037189 | 0.0012951 | 0.01005 | 0.056554 | 0.33528 | 0.006558%
11815 | 2-61.5 | -61.4326 | 1.7062 | 949.3404 | 0.00037985 | 0.00090734 | 0.0045522 | 0.020791 | 0.111 | 0.002101%
11816 | 2-61 | -61.1613 | 1.7062 | 948.468 | 0.00038212 | 0.00091115 | 0.0046034 | 0.021359 | 0.11622 | 0.002208%
11817 | 2-61 | -60.8899 | 1.7062 | 947.9555 | 0.00038429 | 0.00091555 | 0.0046622 | 0.021972 | 0.12179 | 0.002322%
11818 | 2-60.5 | -60.6186 | 1.7062 | 947.8035 | 0.00049075 | 0.0010938 | 0.0050909 | 0.023344 | 0.12941 | 0.002111%
11819 | 2-60.5 | -60.3473 | 1.7062 | 948.0122 | 0.0002781 | 0.00078279 | 0.0046654 | 0.023519 | 0.13608 | 0.003171%
11820 | 2-60 | -60.076 | 1.7062 | 948.5813 | 0.00025875 | 0.00075148 | 0.0047256 | 0.024588 | 0.14521 | 0.003533%
11821 | 2-60 | -59.8046 | 1.7062 | 949.5102 | 0.00025795 | 0.00076167 | 0.0049415 | 0.026219 | 0.15689 | 0.003825%
11822 | 2-59.5 | -59.5333 | 1.7062 | 950.7979 | 0.00026053 | 0.00078258 | 0.0052229 | 0.02816 | 0.17018 | 0.004122%
11823 | 2-59.5 | -59.262 | 1.7062 | 952.4428 | 0.00026411 | 0.00080788 | 0.0055409 | 0.030294 | 0.18449 | 0.004425%
11824 | 2-59 | -58.9907 | 1.7062 | 954.4431 | 0.00027085 | 0.00084926 | 0.0060141 | 0.033352 | 0.20461 | 0.004817%
11825 | 2-58.5 | -58.7194 | 1.7062 | 956.7966 | 0.00027477 | 0.00088878 | 0.0065801 | 0.037324 | 0.23202 | 0.005367%
11826 | 2-58.5 | -58.448 | 1.7062 | 959.5007 | 0.00027346 | 0.00092303 | 0.0072549 | 0.042428 | 0.26688 | 0.006093%
11827 | 2-58 | -58.1767 | 1.7062 | 962.5525 | 0.00027672 | 0.00097858 | 0.0081371 | 0.048815 | 0.30848 | 0.006869%
11828 | 2-58 | -57.9054 | 1.7062 | 965.9486 | 0.00028357 | 0.0010478 | 0.009149 | 0.056114 | 0.3554 | 0.007654%
11829 | 2-57.5 | -57.6341 | 1.7062 | 969.6855 | 0.00029416 | 0.0011334 | 0.010325 | 0.064508 | 0.40742 | 0.008435%
11830 | 2-57.5 | -57.3628 | 1.7062 | 973.7591 | 0.0003533 | 0.0013281 | 0.011882 | 0.074104 | 0.46304 | 0.008733%
11831 | 2-57 | -57.0914 | 1.7062 | 978.1653 | 0.00038515 | 0.0014838 | 0.013422 | 0.083951 | 0.51962 | 0.009273%
11832 | 2-57 | -56.8201 | 1.7062 | 982.8997 | 0.00041592 | 0.0016304 | 0.014962 | 0.093995 | 0.57666 | 0.009799%
11833 | 2-61.5 | -61.4326 | 1.9775 | 930.6241 | 0.00048214 | 0.0014365 | 0.0092726 | 0.045795 | 0.24474 | 0.004382%
11834 | 2-61 | -61.1613 | 1.9775 | 929.7346 | 0.00047281 | 0.0013967 | 0.0091335 | 0.046192 | 0.25381 | 0.004576%
11835 | 2-61 | -60.8899 | 1.9775 | 929.212 | 0.00046391 | 0.0013573 | 0.0089884 | 0.04665 | 0.26474 | 0.004796%
11836 | 2-60.5 | -60.6186 | 1.9775 | 929.0571 | 0.00056317 | 0.0015062 | 0.0092899 | 0.048122 | 0.27861 | 0.004557%
11837 | 2-60.5 | -60.3473 | 1.9775 | 929.2698 | 0.00034443 | 0.0011699 | 0.0087561 | 0.048441 | 0.29153 | 0.005959%
11838 | 2-60 | -60.076 | 1.9775 | 929.8501 | 0.00031996 | 0.0011168 | 0.0087201 | 0.049649 | 0.30657 | 0.006412%
11839 | 2-60 | -59.8046 | 1.9775 | 930.7972 | 0.00031665 | 0.0011178 | 0.0089388 | 0.051853 | 0.32549 | 0.006767%
11840 | 2-59.5 | -59.5333 | 1.9775 | 932.11 | 0.00031753 | 0.0011353 | 0.0092904 | 0.054772 | 0.34736 | 0.007135%
11841 | 2-59.5 | -59.262 | 1.9775 | 933.7869 | 0.0003187 | 0.0011556 | 0.0096971 | 0.058129 | 0.37131 | 0.00753%
11842 | 2-59 | -58.9907 | 1.9775 | 935.8261 | 0.00032588 | 0.0012095 | 0.010445 | 0.063497 | 0.40459 | 0.00802%
11843 | 2-58.5 | -58.7194 | 1.9775 | 938.225 | 0.00033392 | 0.001284 | 0.011531 | 0.071263 | 0.45039 | 0.008686%
11844 | 2-58.5 | -58.448 | 1.9775 | 940.9811 | 0.00034046 | 0.0013768 | 0.012998 | 0.081909 | 0.50989 | 0.00955%
11845 | 2-58 | -58.1767 | 1.9775 | 944.0911 | 0.00035376 | 0.001502 | 0.014774 | 0.09442 | 0.57828 | 0.01042%
11846 | 2-58 | -57.9054 | 1.9775 | 947.5515 | 0.00037067 | 0.001641 | 0.016687 | 0.10795 | 0.652 | 0.01125%
11847 | 2-57.5 | -57.6341 | 1.9775 | 951.3586 | 0.00039105 | 0.0017953 | 0.018762 | 0.12263 | 0.73047 | 0.01205%
11848 | 2-57.5 | -57.3628 | 1.9775 | 955.5082 | 0.00046796 | 0.002101 | 0.021559 | 0.13984 | 0.81312 | 0.01236%
11849 | 2-57 | -57.0914 | 1.9775 | 959.9959 | 0.00052023 | 0.002384 | 0.024515 | 0.15835 | 0.89869 | 0.01291%
11850 | 2-57 | -56.8201 | 1.9775 | 964.8168 | 0.00057351 | 0.0026713 | 0.027627 | 0.17806 | 0.98684 | 0.01346%
11851 | 2-61.5 | -61.4326 | 2.2488 | 911.909 | 0.00058566 | 0.0020544 | 0.015921 | 0.086311 | 0.47979 | 0.007482%
11852 | 2-61 | -61.1613 | 2.2488 | 911.0017 | 0.00056893 | 0.0019867 | 0.015719 | 0.087448 | 0.49721 | 0.007788%
11853 | 2-61 | -60.8899 | 2.2488 | 910.4687 | 0.00055135 | 0.0019119 | 0.015463 | 0.088713 | 0.51895 | 0.008148%
11854 | 2-60.5 | -60.6186 | 2.2488 | 910.3106 | 0.00055069 | 0.0018861 | 0.015433 | 0.090818 | 0.54415 | 0.008452%
11855 | 2-60.5 | -60.3473 | 2.2488 | 910.5276 | 0.00031327 | 0.0014992 | 0.014781 | 0.091997 | 0.5675 | 0.01061%
11856 | 2-60 | -60.076 | 2.2488 | 911.1195 | 0.00028162 | 0.0014221 | 0.014699 | 0.094039 | 0.59107 | 0.01129%
11857 | 2-60 | -59.8046 | 2.2488 | 912.0855 | 0.00027565 | 0.0014218 | 0.015058 | 0.097836 | 0.61936 | 0.01175%
11858 | 2-59.5 | -59.5333 | 2.2488 | 913.4245 | 0.00027395 | 0.0014398 | 0.015607 | 0.10292 | 0.65299 | 0.01222%
11859 | 2-59.5 | -59.262 | 2.2488 | 915.1347 | 0.00027241 | 0.0014615 | 0.016263 | 0.10903 | 0.69114 | 0.01275%
11860 | 2-59 | -58.9907 | 2.2488 | 917.2142 | 0.00028028 | 0.0015397 | 0.017543 | 0.11899 | 0.74432 | 0.01336%
11861 | 2-58.5 | -58.7194 | 2.2488 | 919.6604 | 0.00029187 | 0.00166 | 0.019465 | 0.1336 | 0.81658 | 0.01414%
11862 | 2-58.5 | -58.448 | 2.2488 | 922.4704 | 0.00030396 | 0.0018165 | 0.022073 | 0.15361 | 0.90809 | 0.01514%
11863 | 2-58 | -58.1767 | 2.2488 | 925.6409 | 0.0003235 | 0.0020102 | 0.025039 | 0.17575 | 1.0094 | 0.01607%
11864 | 2-58 | -57.9054 | 2.2488 | 929.1681 | 0.00034732 | 0.0022203 | 0.028122 | 0.19851 | 1.1137 | 0.0169%
11865 | 2-57.5 | -57.6341 | 2.2488 | 933.0481 | 0.00037365 | 0.0024404 | 0.031287 | 0.22176 | 1.2198 | 0.01766%
11866 | 2-57.5 | -57.3628 | 2.2488 | 937.2765 | 0.00043354 | 0.0028115 | 0.035609 | 0.24984 | 1.3296 | 0.01808%
11867 | 2-57 | -57.0914 | 2.2488 | 941.8485 | 0.00050102 | 0.0032335 | 0.040519 | 0.28142 | 1.4449 | 0.01852%
11868 | 2-57 | -56.8201 | 2.2488 | 946.7593 | 0.00057339 | 0.0036938 | 0.045937 | 0.31566 | 1.5657 | 0.01899%
11869 | 3-61.5 | -61.4326 | 2.5201 | 893.1952 | 0.00068699 | 0.0027336 | 0.024438 | 0.1446 | 0.80941 | 0.01085%
11870 | 3-61 | -61.1613 | 2.5201 | 892.2694 | 0.00066589 | 0.0026532 | 0.024353 | 0.14798 | 0.8416 | 0.01129%
11871 | 3-61 | -60.8899 | 2.5201 | 891.7254 | 0.00064214 | 0.0025553 | 0.024155 | 0.15173 | 0.88263 | 0.01182%
11872 | 3-60.5 | -60.6186 | 2.5201 | 891.5641 | 0.0006242 | 0.0024826 | 0.024128 | 0.15644 | 0.92813 | 0.01235%
11873 | 3-60.5 | -60.3473 | 2.5201 | 891.7856 | 0.00038171 | 0.0020781 | 0.023563 | 0.16019 | 0.96987 | 0.0147%
11874 | 3-60 | -60.076 | 2.5201 | 892.3896 | 0.00034828 | 0.001997 | 0.023622 | 0.16459 | 1.0084 | 0.01545%
11875 | 3-60 | -59.8046 | 2.5201 | 893.3753 | 0.00034487 | 0.0020194 | 0.024378 | 0.17179 | 1.052 | 0.01594%
11876 | 3-59.5 | -59.5333 | 2.5201 | 894.7415 | 0.00034506 | 0.0020588 | 0.02538 | 0.18116 | 1.104 | 0.01647%
11877 | 3-59.5 | -59.262 | 2.5201 | 896.4864 | 0.00034531 | 0.002104 | 0.026577 | 0.1926 | 1.1628 | 0.01708%
11878 | 3-59 | -58.9907 | 2.5201 | 898.6079 | 0.000358 | 0.0022292 | 0.028746 | 0.21053 | 1.2413 | 0.01774%
11879 | 3-58.5 | -58.7194 | 2.5201 | 901.1032 | 0.00037632 | 0.0024148 | 0.031897 | 0.2361 | 1.3446 | 0.01859%
11880 | 3-58.5 | -58.448 | 2.5201 | 903.9693 | 0.00039578 | 0.0026485 | 0.036048 | 0.26932 | 1.4736 | 0.01963%
11881 | 3-58 | -58.1767 | 2.5201 | 907.2026 | 0.00042275 | 0.0029193 | 0.040542 | 0.30463 | 1.6122 | 0.02059%
11882 | 3-58 | -57.9054 | 2.5201 | 910.7993 | 0.00045614 | 0.0032142 | 0.04511 | 0.33969 | 1.7487 | 0.02139%
11883 | 3-57.5 | -57.6341 | 2.5201 | 914.755 | 0.00049206 | 0.0035153 | 0.049622 | 0.37396 | 1.8807 | 0.02208%
11884 | 3-57.5 | -57.3628 | 2.5201 | 919.0651 | 0.00056481 | 0.0040204 | 0.055995 | 0.4153 | 2.0149 | 0.02248%
11885 | 3-57 | -57.0914 | 2.5201 | 923.7247 | 0.00065471 | 0.0046248 | 0.06351 | 0.46237 | 2.1579 | 0.02286%
11886 | 3-57 | -56.8201 | 2.5201 | 928.7285 | 0.00075816 | 0.0053149 | 0.072069 | 0.51424 | 2.3106 | 0.02326%
11887 | 3-61.5 | -61.4326 | 2.7914 | 874.4827 | 0.0019476 | 0.0086568 | 0.070507 | 0.35569 | 1.4455 | 0.01282%
11888 | 3-61 | -61.1613 | 2.7914 | 873.5376 | 0.0020248 | 0.0090292 | 0.073826 | 0.3697 | 1.499 | 0.01304%
11889 | 3-61 | -60.8899 | 2.7914 | 872.9823 | 0.0021165 | 0.0094707 | 0.077764 | 0.38595 | 1.5649 | 0.01329%
11890 | 3-60.5 | -60.6186 | 2.7914 | 872.8177 | 0.0022688 | 0.010126 | 0.082642 | 0.40374 | 1.635 | 0.01343%
11891 | 3-60.5 | -60.3473 | 2.7914 | 873.0438 | 0.0022176 | 0.010544 | 0.087677 | 0.42235 | 1.7027 | 0.01401%
11892 | 3-60 | -60.076 | 2.7914 | 873.6603 | 0.0023705 | 0.011309 | 0.093968 | 0.44439 | 1.7702 | 0.01418%
11893 | 3-60 | -59.8046 | 2.7914 | 874.6666 | 0.0026137 | 0.012427 | 0.10251 | 0.47321 | 1.8464 | 0.01427%
11894 | 3-59.5 | -59.5333 | 2.7914 | 876.0612 | 0.0028865 | 0.013685 | 0.11227 | 0.5062 | 1.9337 | 0.01441%
11895 | 3-59.5 | -59.262 | 2.7914 | 877.8422 | 0.003143 | 0.01494 | 0.12287 | 0.54219 | 2.0299 | 0.01466%
11896 | 3-59 | -58.9907 | 2.7914 | 880.0074 | 0.0034442 | 0.016394 | 0.13502 | 0.58472 | 2.1475 | 0.01497%
11897 | 3-58.5 | -58.7194 | 2.7914 | 882.5538 | 0.0037239 | 0.017828 | 0.14803 | 0.63554 | 2.2929 | 0.01548%
11898 | 3-58.5 | -58.448 | 2.7914 | 885.4783 | 0.0039122 | 0.019036 | 0.16176 | 0.6953 | 2.4681 | 0.01628%
11899 | 3-58 | -58.1767 | 2.7914 | 888.777 | 0.0041018 | 0.020241 | 0.17533 | 0.75549 | 2.6505 | 0.01705%
11900 | 3-58 | -57.9054 | 2.7914 | 892.4458 | 0.0042739 | 0.021367 | 0.18823 | 0.8132 | 2.8255 | 0.01778%
11901 | 3-57.5 | -57.6341 | 2.7914 | 896.4802 | 0.0044158 | 0.022362 | 0.20028 | 0.86775 | 2.9898 | 0.01846%
11902 | 3-57.5 | -57.3628 | 2.7914 | 900.8753 | 0.0045982 | 0.023556 | 0.21391 | 0.92772 | 3.1524 | 0.0191%
11903 | 3-57 | -57.0914 | 2.7914 | 905.6257 | 0.0047509 | 0.024706 | 0.22842 | 0.99329 | 3.3246 | 0.01983%
11904 | 3-57 | -56.8201 | 2.7914 | 910.726 | 0.00488 | 0.025816 | 0.24378 | 1.0637 | 3.5086 | 0.02063%
11905 | 3-61.5 | -61.4326 | 3.0628 | 855.7717 | 0.0032493 | 0.016734 | 0.15007 | 0.7006 | 2.3307 | 0.01697%
11906 | 3-61 | -61.1613 | 3.0628 | 854.8065 | 0.0034345 | 0.017777 | 0.16059 | 0.73458 | 2.4151 | 0.01723%
11907 | 3-61 | -60.8899 | 3.0628 | 854.2394 | 0.0036471 | 0.018995 | 0.17326 | 0.77377 | 2.5185 | 0.01756%
11908 | 3-60.5 | -60.6186 | 3.0628 | 854.0712 | 0.0039928 | 0.020736 | 0.18871 | 0.81556 | 2.6267 | 0.0177%
11909 | 3-60.5 | -60.3473 | 3.0628 | 854.3021 | 0.0043359 | 0.022623 | 0.20601 | 0.86145 | 2.738 | 0.01792%
11910 | 3-60 | -60.076 | 3.0628 | 854.9319 | 0.0047074 | 0.024651 | 0.2253 | 0.91449 | 2.8576 | 0.0182%
11911 | 3-60 | -59.8046 | 3.0628 | 855.9595 | 0.0052225 | 0.027363 | 0.24907 | 0.97935 | 2.9938 | 0.01843%
11912 | 3-59.5 | -59.5333 | 3.0628 | 857.3837 | 0.0058052 | 0.030443 | 0.27538 | 1.0503 | 3.1456 | 0.01868%
11913 | 3-59.5 | -59.262 | 3.0628 | 859.2024 | 0.0063566 | 0.033541 | 0.30313 | 1.1247 | 3.308 | 0.01904%
11914 | 3-59 | -58.9907 | 3.0628 | 861.4131 | 0.0069916 | 0.037009 | 0.33269 | 1.2045 | 3.4898 | 0.0194%
11915 | 3-58.5 | -58.7194 | 3.0628 | 864.0128 | 0.0075839 | 0.04036 | 0.3623 | 1.2911 | 3.6986 | 0.0199%
11916 | 3-58.5 | -58.448 | 3.0628 | 866.998 | 0.00799 | 0.043113 | 0.39152 | 1.3852 | 3.9367 | 0.02067%
11917 | 3-58 | -58.1767 | 3.0628 | 870.3648 | 0.0084104 | 0.045889 | 0.41968 | 1.4764 | 4.177 | 0.02138%
11918 | 3-58 | -57.9054 | 3.0628 | 874.1087 | 0.0087912 | 0.048464 | 0.44585 | 1.5611 | 4.4026 | 0.02203%
11919 | 3-57.5 | -57.6341 | 3.0628 | 878.225 | 0.0091041 | 0.050717 | 0.46961 | 1.6381 | 4.6091 | 0.02263%
11920 | 3-57.5 | -57.3628 | 3.0628 | 882.7083 | 0.0094814 | 0.053208 | 0.4936 | 1.7167 | 4.8045 | 0.02314%
11921 | 3-57 | -57.0914 | 3.0628 | 887.5532 | 0.0097714 | 0.055402 | 0.51685 | 1.7993 | 5.0065 | 0.02375%
11922 | 3-57 | -56.8201 | 3.0628 | 892.7537 | 0.0099894 | 0.057331 | 0.53987 | 1.8854 | 5.2179 | 0.02442%
11923 | 3-61.5 | -61.4326 | 3.3341 | 837.0623 | 0.0054743 | 0.029759 | 0.28312 | 1.205 | 3.4992 | 0.02088%
11924 | 3-61 | -61.1613 | 3.3341 | 836.0761 | 0.0058218 | 0.031905 | 0.30534 | 1.2635 | 3.6271 | 0.0212%
11925 | 3-61 | -60.8899 | 3.3341 | 835.4966 | 0.0062107 | 0.034373 | 0.33134 | 1.3304 | 3.7779 | 0.02159%
11926 | 3-60.5 | -60.6186 | 3.3341 | 835.3247 | 0.0068009 | 0.037747 | 0.36218 | 1.4016 | 3.9322 | 0.02181%
11927 | 3-60.5 | -60.3473 | 3.3341 | 835.5607 | 0.0074423 | 0.041514 | 0.39684 | 1.4815 | 4.0967 | 0.02207%
11928 | 3-60 | -60.076 | 3.3341 | 836.2041 | 0.0080768 | 0.045434 | 0.43506 | 1.575 | 4.2823 | 0.02249%
11929 | 3-60 | -59.8046 | 3.3341 | 837.2542 | 0.0089167 | 0.050485 | 0.48112 | 1.688 | 4.4955 | 0.0229%
11930 | 3-59.5 | -59.5333 | 3.3341 | 838.7092 | 0.0098741 | 0.056247 | 0.5316 | 1.8098 | 4.728 | 0.02331%
11931 | 3-59.5 | -59.262 | 3.3341 | 840.5672 | 0.010805 | 0.062145 | 0.58435 | 1.935 | 4.9714 | 0.0238%
11932 | 3-59 | -58.9907 | 3.3341 | 842.8254 | 0.011845 | 0.068586 | 0.639 | 2.0634 | 5.2303 | 0.02426%
11933 | 3-58.5 | -58.7194 | 3.3341 | 845.4807 | 0.012833 | 0.074833 | 0.69197 | 2.1944 | 5.5114 | 0.0248%
11934 | 3-58.5 | -58.448 | 3.3341 | 848.5293 | 0.013586 | 0.080141 | 0.74216 | 2.3293 | 5.8171 | 0.02553%
11935 | 3-58 | -58.1767 | 3.3341 | 851.967 | 0.014343 | 0.085439 | 0.78983 | 2.4579 | 6.1161 | 0.02619%
11936 | 3-58 | -57.9054 | 3.3341 | 855.7891 | 0.015045 | 0.090412 | 0.83408 | 2.5765 | 6.39 | 0.02677%
11937 | 3-57.5 | -57.6341 | 3.3341 | 859.9905 | 0.015644 | 0.094831 | 0.87434 | 2.6836 | 6.6347 | 0.02731%
11938 | 3-57.5 | -57.3628 | 3.3341 | 864.5657 | 0.016354 | 0.099608 | 0.91346 | 2.787 | 6.8593 | 0.02772%
11939 | 3-57 | -57.0914 | 3.3341 | 869.5086 | 0.016953 | 0.10388 | 0.95002 | 2.8914 | 7.0867 | 0.02819%
11940 | 3-57 | -56.8201 | 3.3341 | 874.8132 | 0.017433 | 0.10757 | 0.98473 | 2.9968 | 7.3205 | 0.02872%
11941 | 4-61.5 | -61.4326 | 3.6054 | 818.3545 | 0.017685 | 0.093003 | 0.68504 | 2.1299 | 5.2637 | 0.02114%
11942 | 4-61 | -61.1613 | 3.6054 | 817.3464 | 0.018695 | 0.099596 | 0.72952 | 2.2232 | 5.4307 | 0.02145%
11943 | 4-61 | -60.8899 | 3.6054 | 816.754 | 0.019749 | 0.10696 | 0.7797 | 2.3304 | 5.6268 | 0.02186%
11944 | 4-60.5 | -60.6186 | 3.6054 | 816.5783 | 0.021177 | 0.11632 | 0.83696 | 2.4466 | 5.8302 | 0.02217%
11945 | 4-60.5 | -60.3473 | 3.6054 | 816.8195 | 0.022793 | 0.12718 | 0.90082 | 2.5784 | 6.0517 | 0.02251%
11946 | 4-60 | -60.076 | 3.6054 | 817.4773 | 0.024461 | 0.13918 | 0.97138 | 2.7325 | 6.3056 | 0.02298%
11947 | 4-60 | -59.8046 | 3.6054 | 818.5507 | 0.026446 | 0.15344 | 1.0528 | 2.9126 | 6.5986 | 0.02351%
11948 | 4-59.5 | -59.5333 | 3.6054 | 820.038 | 0.028621 | 0.16934 | 1.14 | 3.1031 | 6.9138 | 0.02405%
11949 | 4-59.5 | -59.262 | 3.6054 | 821.937 | 0.030817 | 0.18608 | 1.2295 | 3.2967 | 7.2383 | 0.02462%
11950 | 4-59 | -58.9907 | 3.6054 | 824.2449 | 0.033202 | 0.20369 | 1.3198 | 3.4907 | 7.5744 | 0.02514%
11951 | 4-58.5 | -58.7194 | 3.6054 | 826.9581 | 0.035591 | 0.22108 | 1.4063 | 3.6833 | 7.9276 | 0.02567%
11952 | 4-58.5 | -58.448 | 3.6054 | 830.0728 | 0.037828 | 0.23746 | 1.4873 | 3.8745 | 8.2994 | 0.02624%
11953 | 4-58 | -58.1767 | 3.6054 | 833.5845 | 0.040313 | 0.2541 | 1.5629 | 4.0536 | 8.6563 | 0.02667%
11954 | 4-58 | -57.9054 | 3.6054 | 837.4881 | 0.042835 | 0.27043 | 1.6323 | 4.2167 | 8.9801 | 0.027%
11955 | 4-57.5 | -57.6341 | 3.6054 | 841.7782 | 0.045319 | 0.28611 | 1.6955 | 4.3625 | 9.2671 | 0.02725%
11956 | 4-57.5 | -57.3628 | 3.6054 | 846.4489 | 0.048299 | 0.3034 | 1.7597 | 4.5034 | 9.5345 | 0.02736%
11957 | 4-57 | -57.0914 | 3.6054 | 851.4939 | 0.051371 | 0.32095 | 1.8232 | 4.6449 | 9.8081 | 0.02748%
11958 | 4-57 | -56.8201 | 3.6054 | 856.9067 | 0.054469 | 0.33851 | 1.8866 | 4.7868 | 10.0917 | 0.02762%
11959 | 4-61.5 | -61.4326 | 3.8767 | 799.6486 | 0.037481 | 0.21304 | 1.3325 | 3.4695 | 7.4935 | 0.02379%
11960 | 4-61 | -61.1613 | 3.8767 | 798.6174 | 0.039777 | 0.22931 | 1.4021 | 3.6088 | 7.7121 | 0.02404%
11961 | 4-61 | -60.8899 | 3.8767 | 798.0115 | 0.042142 | 0.24713 | 1.4799 | 3.7659 | 7.9674 | 0.0244%
11962 | 4-60.5 | -60.6186 | 3.8767 | 797.8318 | 0.045208 | 0.26851 | 1.5681 | 3.9357 | 8.2365 | 0.02467%
11963 | 4-60.5 | -60.3473 | 3.8767 | 798.0785 | 0.04877 | 0.29303 | 1.6672 | 4.1267 | 8.5331 | 0.02497%
11964 | 4-60 | -60.076 | 3.8767 | 798.7514 | 0.05262 | 0.32024 | 1.7782 | 4.3476 | 8.8744 | 0.02538%
11965 | 4-60 | -59.8046 | 3.8767 | 799.8492 | 0.057041 | 0.35108 | 1.904 | 4.5999 | 9.2637 | 0.02586%
11966 | 4-59.5 | -59.5333 | 3.8767 | 801.3702 | 0.061811 | 0.38441 | 2.0372 | 4.8636 | 9.6777 | 0.02636%
11967 | 4-59.5 | -59.262 | 3.8767 | 803.3121 | 0.066736 | 0.4191 | 2.174 | 5.1283 | 10.1006 | 0.02687%
11968 | 4-59 | -58.9907 | 3.8767 | 805.6719 | 0.072029 | 0.45473 | 2.3105 | 5.3885 | 10.5291 | 0.02732%
11969 | 4-58.5 | -58.7194 | 3.8767 | 808.4457 | 0.077378 | 0.48989 | 2.4416 | 5.6407 | 10.967 | 0.02776%
11970 | 4-58.5 | -58.448 | 3.8767 | 811.6295 | 0.082639 | 0.52374 | 2.5654 | 5.8841 | 11.4155 | 0.0282%
11971 | 4-58 | -58.1767 | 3.8767 | 815.2183 | 0.088625 | 0.55826 | 2.6814 | 6.1065 | 11.837 | 0.02846%
11972 | 4-58 | -57.9054 | 3.8767 | 819.2069 | 0.094835 | 0.59238 | 2.7892 | 6.3085 | 12.2157 | 0.02862%
11973 | 4-57.5 | -57.6341 | 3.8767 | 823.5895 | 0.10114 | 0.62552 | 2.8888 | 6.489 | 12.5492 | 0.02868%
11974 | 4-57.5 | -57.3628 | 3.8767 | 828.3597 | 0.10876 | 0.6637 | 2.997 | 6.6714 | 12.8745 | 0.02864%
11975 | 4-57 | -57.0914 | 3.8767 | 833.511 | 0.11694 | 0.70548 | 3.1127 | 6.862 | 13.2204 | 0.02861%
11976 | 4-57 | -56.8201 | 3.8767 | 839.0363 | 0.12548 | 0.74952 | 3.2301 | 7.0601 | 13.5902 | 0.02863%
11977 | 4-61.5 | -61.4326 | 4.1481 | 780.9445 | 0.07078 | 0.42016 | 2.2108 | 5.247 | 10.2397 | 0.02668%
11978 | 4-61 | -61.1613 | 4.1481 | 779.8893 | 0.075476 | 0.45035 | 2.3155 | 5.4291 | 10.526 | 0.02686%
11979 | 4-61 | -60.8899 | 4.1481 | 779.2693 | 0.080348 | 0.48295 | 2.432 | 5.6328 | 10.8574 | 0.02716%
11980 | 4-60.5 | -60.6186 | 4.1481 | 779.0853 | 0.086407 | 0.5215 | 2.5644 | 5.8538 | 11.2111 | 0.02739%
11981 | 4-60.5 | -60.3473 | 4.1481 | 779.3378 | 0.093603 | 0.56607 | 2.7147 | 6.1033 | 11.6042 | 0.02764%
11982 | 4-60 | -60.076 | 4.1481 | 780.0264 | 0.10166 | 0.61626 | 2.8846 | 6.3908 | 12.0562 | 0.02798%
11983 | 4-60 | -59.8046 | 4.1481 | 781.1498 | 0.11085 | 0.67268 | 3.0754 | 6.7161 | 12.5659 | 0.02839%
11984 | 4-59.5 | -59.5333 | 4.1481 | 782.7062 | 0.12085 | 0.73343 | 3.2758 | 7.0543 | 13.1038 | 0.02881%
11985 | 4-59.5 | -59.262 | 4.1481 | 784.693 | 0.13146 | 0.79704 | 3.4798 | 7.3943 | 13.6505 | 0.02921%
11986 | 4-59 | -58.9907 | 4.1481 | 787.107 | 0.14283 | 0.86182 | 3.6811 | 7.7259 | 14.1946 | 0.02955%
11987 | 4-58.5 | -58.7194 | 4.1481 | 789.9442 | 0.15443 | 0.92563 | 3.8741 | 8.0448 | 14.738 | 0.02987%
11988 | 4-58.5 | -58.448 | 4.1481 | 793.2001 | 0.16608 | 0.98753 | 4.0559 | 8.3496 | 15.2809 | 0.03016%
11989 | 4-58 | -58.1767 | 4.1481 | 796.8696 | 0.17929 | 1.0502 | 4.2254 | 8.6252 | 15.7789 | 0.03025%
11990 | 4-58 | -57.9054 | 4.1481 | 800.9469 | 0.19323 | 1.112 | 4.3831 | 8.875 | 16.222 | 0.03021%
11991 | 4-57.5 | -57.6341 | 4.1481 | 805.426 | 0.20761 | 1.1723 | 4.529 | 9.0985 | 16.6103 | 0.03009%
11992 | 4-57.5 | -57.3628 | 4.1481 | 810.3 | 0.22478 | 1.2404 | 4.6881 | 9.3364 | 17.0138 | 0.02988%
11993 | 4-57 | -57.0914 | 4.1481 | 815.562 | 0.24345 | 1.3138 | 4.8582 | 9.5958 | 17.4487 | 0.02972%
11994 | 4-57 | -56.8201 | 4.1481 | 821.2044 | 0.26298 | 1.3908 | 5.0327 | 9.8755 | 17.9163 | 0.02962%
11995 | 4-61.5 | -61.4326 | 4.4194 | 762.2425 | 0.17481 | 0.88362 | 3.6065 | 7.5633 | 13.7988 | 0.02602%
11996 | 4-61 | -61.1613 | 4.4194 | 761.1621 | 0.18885 | 0.94117 | 3.7626 | 7.8007 | 14.1677 | 0.02597%
11997 | 4-61 | -60.8899 | 4.4194 | 760.5272 | 0.2038 | 1.0014 | 3.9299 | 8.0609 | 14.5835 | 0.02599%
11998 | 4-60.5 | -60.6186 | 4.4194 | 760.3389 | 0.2208 | 1.0686 | 4.1129 | 8.3402 | 15.0231 | 0.02601%
11999 | 4-60.5 | -60.3473 | 4.4194 | 760.5974 | 0.23993 | 1.1442 | 4.3171 | 8.6542 | 15.508 | 0.02606%
12000 | 4-60 | -60.076 | 4.4194 | 761.3025 | 0.26108 | 1.2288 | 4.5468 | 9.0164 | 16.0642 | 0.02622%
12001 | 4-60 | -59.8046 | 4.4194 | 762.4527 | 0.28529 | 1.324 | 4.8049 | 9.4288 | 16.6924 | 0.02643%
12002 | 4-59.5 | -59.5333 | 4.4194 | 764.0461 | 0.31214 | 1.4278 | 5.0787 | 9.8657 | 17.3601 | 0.02666%
12003 | 4-59.5 | -59.262 | 4.4194 | 766.08 | 0.34141 | 1.5382 | 5.3611 | 10.3151 | 18.0456 | 0.02687%
12004 | 4-59 | -58.9907 | 4.4194 | 768.5508 | 0.37282 | 1.6509 | 5.6404 | 10.7564 | 18.727 | 0.02702%
12005 | 4-58.5 | -58.7194 | 4.4194 | 771.4543 | 0.40511 | 1.7613 | 5.9052 | 11.1783 | 19.3945 | 0.02714%
12006 | 4-58.5 | -58.448 | 4.4194 | 774.7857 | 0.43772 | 1.8669 | 6.1493 | 11.5764 | 20.0425 | 0.02722%
12007 | 4-58 | -58.1767 | 4.4194 | 778.5395 | 0.47224 | 1.9713 | 6.3733 | 11.9315 | 20.6215 | 0.02715%
12008 | 4-58 | -57.9054 | 4.4194 | 782.7096 | 0.50785 | 2.0741 | 6.5811 | 12.2516 | 21.1308 | 0.027%
12009 | 4-57.5 | -57.6341 | 4.4194 | 787.2894 | 0.54427 | 2.175 | 6.7738 | 12.5385 | 21.5743 | 0.02676%
12010 | 4-57.5 | -57.3628 | 4.4194 | 792.2717 | 0.58322 | 2.2849 | 6.9815 | 12.8445 | 22.034 | 0.02656%
12011 | 4-57 | -57.0914 | 4.4194 | 797.6491 | 0.62313 | 2.4012 | 7.202 | 13.1774 | 22.5268 | 0.02644%
12012 | 4-57 | -56.8201 | 4.4194 | 803.4135 | 0.66334 | 2.5222 | 7.4284 | 13.5354 | 23.057 | 0.02642%
12013 | 5-61.5 | -61.4326 | 4.6907 | 743.5427 | 0.36747 | 1.5856 | 5.4609 | 10.4574 | 18.2582 | 0.02624%
12014 | 5-61 | -61.1613 | 4.6907 | 742.4359 | 0.39718 | 1.6775 | 5.6662 | 10.7667 | 18.7025 | 0.02608%
12015 | 5-61 | -60.8899 | 4.6907 | 741.7854 | 0.42828 | 1.7716 | 5.8813 | 11.0963 | 19.1817 | 0.02598%
12016 | 5-60.5 | -60.6186 | 4.6907 | 741.5924 | 0.46245 | 1.8747 | 6.1116 | 11.4419 | 19.6711 | 0.02587%
12017 | 5-60.5 | -60.3473 | 4.6907 | 741.8573 | 0.5005 | 1.9899 | 6.3668 | 11.8278 | 20.2088 | 0.02581%
12018 | 5-60 | -60.076 | 4.6907 | 742.5797 | 0.54289 | 2.1195 | 6.6545 | 12.2742 | 20.8325 | 0.02584%
12019 | 5-60 | -59.8046 | 4.6907 | 743.758 | 0.59267 | 2.269 | 6.9824 | 12.7926 | 21.5508 | 0.02591%
12020 | 5-59.5 | -59.5333 | 4.6907 | 745.3903 | 0.64959 | 2.4371 | 7.3385 | 13.36 | 22.3329 | 0.02598%
12021 | 5-59.5 | -59.262 | 4.6907 | 747.4736 | 0.71209 | 2.6227 | 7.7162 | 13.9596 | 23.1576 | 0.02608%
12022 | 5-59 | -58.9907 | 4.6907 | 750.004 | 0.77802 | 2.8124 | 8.0941 | 14.5551 | 23.9859 | 0.02617%
12023 | 5-58.5 | -58.7194 | 4.6907 | 752.977 | 0.84481 | 2.9983 | 8.4536 | 15.122 | 24.7836 | 0.02623%
12024 | 5-58.5 | -58.448 | 4.6907 | 756.3875 | 0.91183 | 3.1763 | 8.7854 | 15.6495 | 25.537 | 0.02626%
12025 | 5-58 | -58.1767 | 4.6907 | 760.2295 | 0.98035 | 3.3484 | 9.0864 | 16.1135 | 26.1997 | 0.02615%
12026 | 5-58 | -57.9054 | 4.6907 | 764.4966 | 1.0497 | 3.5159 | 9.3643 | 16.5299 | 26.7801 | 0.02597%
12027 | 5-57.5 | -57.6341 | 4.6907 | 769.1817 | 1.1198 | 3.6792 | 9.6222 | 16.9041 | 27.2862 | 0.02572%
12028 | 5-57.5 | -57.3628 | 4.6907 | 774.2771 | 1.1907 | 3.8481 | 9.891 | 17.2909 | 27.8037 | 0.02553%
12029 | 5-57 | -57.0914 | 4.6907 | 779.7748 | 1.2602 | 4.0195 | 10.1688 | 17.6985 | 28.3503 | 0.02545%
12030 | 5-57 | -56.8201 | 4.6907 | 785.6664 | 1.3276 | 4.1917 | 10.4489 | 18.1244 | 28.9302 | 0.02547%
12031 | 5-61.5 | -61.4326 | 4.962 | 724.8453 | 0.68381 | 2.5411 | 7.7137 | 14.0319 | 23.3915 | 0.027%
12032 | 5-61 | -61.1613 | 4.962 | 723.7107 | 0.73699 | 2.6828 | 7.9816 | 14.4364 | 23.9042 | 0.0268%
12033 | 5-61 | -60.8899 | 4.962 | 723.0438 | 0.79343 | 2.829 | 8.2572 | 14.8551 | 24.4429 | 0.02662%
12034 | 5-60.5 | -60.6186 | 4.962 | 722.8459 | 0.8548 | 2.9876 | 8.5464 | 15.2821 | 24.9826 | 0.02642%
12035 | 5-60.5 | -60.3473 | 4.962 | 723.1176 | 0.92178 | 3.1639 | 8.8646 | 15.7502 | 25.5735 | 0.02627%
12036 | 5-60 | -60.076 | 4.962 | 723.8581 | 0.9953 | 3.3587 | 9.2245 | 16.2896 | 26.2635 | 0.02624%
12037 | 5-60 | -59.8046 | 4.962 | 725.066 | 1.0801 | 3.5801 | 9.6408 | 16.9183 | 27.0708 | 0.02628%
12038 | 5-59.5 | -59.5333 | 4.962 | 726.7392 | 1.1757 | 3.827 | 10.1047 | 17.6171 | 27.9698 | 0.02638%
12039 | 5-59.5 | -59.262 | 4.962 | 728.8742 | 1.2806 | 4.0979 | 10.6107 | 18.3703 | 28.9415 | 0.02654%
12040 | 5-59 | -58.9907 | 4.962 | 731.4672 | 1.3914 | 4.3751 | 11.1228 | 19.1272 | 29.9252 | 0.02669%
12041 | 5-58.5 | -58.7194 | 4.962 | 734.5131 | 1.5038 | 4.6462 | 11.6121 | 19.8446 | 30.8668 | 0.02681%
12042 | 5-58.5 | -58.448 | 4.962 | 738.0065 | 1.6164 | 4.904 | 12.0651 | 20.5016 | 31.7433 | 0.02686%
12043 | 5-58 | -58.1767 | 4.962 | 741.9411 | 1.7296 | 5.1481 | 12.4718 | 21.0677 | 32.5027 | 0.02678%
12044 | 5-58 | -57.9054 | 4.962 | 746.3097 | 1.8429 | 5.382 | 12.8457 | 21.5707 | 33.1658 | 0.02661%
12045 | 5-57.5 | -57.6341 | 4.962 | 751.1049 | 1.9561 | 5.6069 | 13.1923 | 22.0211 | 33.7464 | 0.02637%
12046 | 5-57.5 | -57.3628 | 4.962 | 756.3185 | 2.0659 | 5.8292 | 13.5386 | 22.4701 | 34.3261 | 0.02621%
12047 | 5-57 | -57.0914 | 4.962 | 761.9419 | 2.1702 | 6.045 | 13.8831 | 22.9266 | 34.923 | 0.02616%
12048 | 5-57 | -56.8201 | 4.962 | 767.9662 | 2.269 | 6.2534 | 14.2187 | 23.392 | 35.541 | 0.0262%
12049 | 5-61.5 | -61.4326 | 5.2333 | 706.1505 | 1.2976 | 4.0022 | 10.5565 | 18.4659 | 29.1479 | 0.02645%
12050 | 5-61 | -61.1613 | 5.2333 | 704.9866 | 1.3812 | 4.205 | 10.9063 | 18.9671 | 29.7434 | 0.02638%
12051 | 5-61 | -60.8899 | 5.2333 | 704.3025 | 1.4684 | 4.4106 | 11.2623 | 19.4705 | 30.3566 | 0.02633%
12052 | 5-60.5 | -60.6186 | 5.2333 | 704.0995 | 1.5627 | 4.6289 | 11.635 | 19.9729 | 30.9673 | 0.02624%
12053 | 5-60.5 | -60.3473 | 5.2333 | 704.3781 | 1.6666 | 4.8681 | 12.0469 | 20.5182 | 31.6369 | 0.02619%
12054 | 5-60 | -60.076 | 5.2333 | 705.1378 | 1.7823 | 5.1311 | 12.5159 | 21.1451 | 32.4208 | 0.02623%
12055 | 5-60 | -59.8046 | 5.2333 | 706.3769 | 1.9146 | 5.4253 | 13.0555 | 21.87 | 33.3347 | 0.02634%
12056 | 5-59.5 | -59.5333 | 5.2333 | 708.093 | 2.0642 | 5.7496 | 13.6584 | 22.6767 | 34.3564 | 0.02652%
12057 | 5-59.5 | -59.262 | 5.2333 | 710.2825 | 2.23 | 6.103 | 14.3119 | 23.5519 | 35.4694 | 0.02673%
12058 | 5-59 | -58.9907 | 5.2333 | 712.9412 | 2.4058 | 6.4625 | 14.9725 | 24.4342 | 36.5964 | 0.02694%
12059 | 5-58.5 | -58.7194 | 5.2333 | 716.0638 | 2.5862 | 6.8109 | 15.6042 | 25.2652 | 37.6686 | 0.02708%
12060 | 5-58.5 | -58.448 | 5.2333 | 719.6442 | 2.7698 | 7.1424 | 16.1893 | 26.0237 | 38.6576 | 0.02711%
12061 | 5-58 | -58.1767 | 5.2333 | 723.6757 | 2.9534 | 7.4552 | 16.7142 | 26.6774 | 39.5081 | 0.02699%
12062 | 5-58 | -57.9054 | 5.2333 | 728.1508 | 3.1353 | 7.7535 | 17.1959 | 27.259 | 40.2507 | 0.02681%
12063 | 5-57.5 | -57.6341 | 5.2333 | 733.0613 | 3.3151 | 8.0389 | 17.6418 | 27.7814 | 40.9028 | 0.02656%
12064 | 5-57.5 | -57.3628 | 5.2333 | 738.3986 | 3.4871 | 8.315 | 18.0765 | 28.2934 | 41.5441 | 0.0264%
12065 | 5-57 | -57.0914 | 5.2333 | 744.1534 | 3.6469 | 8.5758 | 18.4939 | 28.8005 | 42.1875 | 0.02633%
12066 | 5-57 | -56.8201 | 5.2333 | 750.3162 | 3.7936 | 8.8199 | 18.8848 | 29.3027 | 42.8349 | 0.02635%
12067 | 6-61.5 | -61.4326 | 5.5047 | 687.4585 | 2.1572 | 5.8749 | 14.055 | 23.5283 | 35.5054 | 0.02724%
12068 | 6-61 | -61.1613 | 5.5047 | 686.2637 | 2.2797 | 6.1376 | 14.5128 | 24.1152 | 36.1975 | 0.02728%
12069 | 6-61 | -60.8899 | 5.5047 | 685.5614 | 2.4082 | 6.4002 | 14.9769 | 24.696 | 36.8981 | 0.0273%
12070 | 6-60.5 | -60.6186 | 5.5047 | 685.353 | 2.5511 | 6.6789 | 15.4648 | 25.279 | 37.5986 | 0.02724%
12071 | 6-60.5 | -60.3473 | 5.5047 | 685.6391 | 2.7141 | 6.987 | 15.9969 | 25.9149 | 38.3711 | 0.02718%
12072 | 6-60 | -60.076 | 5.5047 | 686.4189 | 2.8982 | 7.329 | 16.5941 | 26.6461 | 39.2765 | 0.02719%
12073 | 6-60 | -59.8046 | 5.5047 | 687.6908 | 3.1014 | 7.7076 | 17.2626 | 27.4784 | 40.3142 | 0.0273%
12074 | 6-59.5 | -59.5333 | 5.5047 | 689.4521 | 3.3243 | 8.1213 | 17.9957 | 28.3961 | 41.4634 | 0.0275%
12075 | 6-59.5 | -59.262 | 5.5047 | 691.6991 | 3.5656 | 8.5697 | 18.7824 | 29.3881 | 42.7107 | 0.02777%
12076 | 6-59 | -58.9907 | 5.5047 | 694.427 | 3.8169 | 9.0246 | 19.5736 | 30.3853 | 43.9676 | 0.02804%
12077 | 6-58.5 | -58.7194 | 5.5047 | 697.6301 | 4.072 | 9.467 | 20.329 | 31.325 | 45.1576 | 0.02825%
12078 | 6-58.5 | -58.448 | 5.5047 | 701.302 | 4.3292 | 9.891 | 21.0295 | 32.1844 | 46.2488 | 0.02835%
12079 | 6-58 | -58.1767 | 5.5047 | 705.4354 | 4.5839 | 10.2908 | 21.6572 | 32.9281 | 47.1857 | 0.0283%
12080 | 6-58 | -57.9054 | 5.5047 | 710.0221 | 4.8336 | 10.6705 | 22.2303 | 33.5922 | 48.0065 | 0.02818%
12081 | 6-57.5 | -57.6341 | 5.5047 | 715.0535 | 5.0772 | 11.0322 | 22.7569 | 34.1909 | 48.7317 | 0.02801%
12082 | 6-57.5 | -57.3628 | 5.5047 | 720.5202 | 5.3064 | 11.3762 | 23.2585 | 34.7696 | 49.4376 | 0.02791%
12083 | 6-57 | -57.0914 | 5.5047 | 726.4124 | 5.5117 | 11.6925 | 23.7219 | 35.3269 | 50.1251 | 0.02791%
12084 | 6-57 | -56.8201 | 5.5047 | 732.7199 | 5.6894 | 11.9782 | 24.1446 | 35.8607 | 50.7924 | 0.02801%
12085 | 6-61.5 | -61.4326 | 5.776 | 668.7694 | 3.3331 | 8.1264 | 18.3009 | 29.1401 | 42.4686 | 0.02875%
12086 | 6-61 | -61.1613 | 5.776 | 667.5421 | 3.5156 | 8.4575 | 18.8755 | 29.8201 | 43.267 | 0.0288%
12087 | 6-61 | -60.8899 | 5.776 | 666.8206 | 3.7047 | 8.7915 | 19.4514 | 30.4925 | 44.0681 | 0.02883%
12088 | 6-60.5 | -60.6186 | 5.776 | 666.6066 | 3.911 | 9.1506 | 20.0513 | 31.1734 | 44.8762 | 0.02882%
12089 | 6-60.5 | -60.3473 | 5.776 | 666.9005 | 4.1414 | 9.5522 | 20.6998 | 31.9194 | 45.7732 | 0.02883%
12090 | 6-60 | -60.076 | 5.776 | 667.7016 | 4.3977 | 10.0035 | 21.4196 | 32.775 | 46.8236 | 0.02893%
12091 | 6-60 | -59.8046 | 5.776 | 669.0081 | 4.6748 | 10.4971 | 22.2052 | 33.7286 | 47.9998 | 0.02913%
12092 | 6-59.5 | -59.5333 | 5.776 | 670.8172 | 4.9728 | 11.0304 | 23.05 | 34.7642 | 49.2794 | 0.02943%
12093 | 6-59.5 | -59.262 | 5.776 | 673.1246 | 5.2904 | 11.6042 | 23.9443 | 35.8727 | 50.6523 | 0.0298%
12094 | 6-59 | -58.9907 | 5.776 | 675.9254 | 5.6162 | 12.1838 | 24.8348 | 36.9801 | 52.0226 | 0.03018%
12095 | 6-58.5 | -58.7194 | 5.776 | 679.2134 | 5.9436 | 12.7501 | 25.6847 | 38.0238 | 53.3139 | 0.03049%
12096 | 6-58.5 | -58.448 | 5.776 | 682.9815 | 6.2711 | 13.298 | 26.4768 | 38.981 | 54.496 | 0.0307%
12097 | 6-58 | -58.1767 | 5.776 | 687.222 | 6.592 | 13.8148 | 27.1903 | 39.8153 | 55.5142 | 0.03076%
12098 | 6-58 | -57.9054 | 5.776 | 691.926 | 6.9013 | 14.3031 | 27.8419 | 40.5626 | 56.4111 | 0.03076%
12099 | 6-57.5 | -57.6341 | 5.776 | 697.0842 | 7.1972 | 14.7651 | 28.4396 | 41.238 | 57.2086 | 0.03072%
12100 | 6-57.5 | -57.3628 | 5.776 | 702.6866 | 7.4733 | 15.1963 | 29.0023 | 41.8813 | 57.9781 | 0.03073%
12101 | 6-57 | -57.0914 | 5.776 | 708.7227 | 7.7178 | 15.5827 | 29.5116 | 42.4837 | 58.7063 | 0.03081%
12102 | 6-57 | -56.8201 | 5.776 | 715.1814 | 7.9262 | 15.9199 | 29.9644 | 43.0416 | 59.3871 | 0.03097%
12103 | 6-61.5 | -61.4326 | 6.0473 | 650.0837 | 4.9732 | 10.8894 | 23.1865 | 35.2898 | 49.9853 | 0.03027%
12104 | 6-61 | -61.1613 | 6.0473 | 648.822 | 5.2138 | 11.3148 | 23.8588 | 36.0714 | 50.8925 | 0.03043%
12105 | 6-61 | -60.8899 | 6.0473 | 648.0802 | 5.4653 | 11.7573 | 24.5349 | 36.8545 | 51.8102 | 0.03058%
12106 | 6-60.5 | -60.6186 | 6.0473 | 647.8601 | 5.7375 | 12.2383 | 25.2347 | 37.6526 | 52.7421 | 0.03068%
12107 | 6-60.5 | -60.3473 | 6.0473 | 648.1623 | 6.0372 | 12.7765 | 25.9882 | 38.523 | 53.7739 | 0.03082%
12108 | 6-60 | -60.076 | 6.0473 | 648.9859 | 6.3663 | 13.3817 | 26.8193 | 39.5112 | 54.9723 | 0.03108%
12109 | 6-60 | -59.8046 | 6.0473 | 650.3291 | 6.717 | 14.0301 | 27.7144 | 40.5923 | 56.289 | 0.03145%
12110 | 6-59.5 | -59.5333 | 6.0473 | 652.1885 | 7.0878 | 14.7156 | 28.6652 | 41.7486 | 57.6962 | 0.03191%
12111 | 6-59.5 | -59.262 | 6.0473 | 654.5598 | 7.4799 | 15.4386 | 29.6621 | 42.9712 | 59.1856 | 0.03244%
12112 | 6-59 | -58.9907 | 6.0473 | 657.4375 | 7.8795 | 16.1616 | 30.6493 | 44.1823 | 60.6573 | 0.03297%
12113 | 6-58.5 | -58.7194 | 6.0473 | 660.815 | 8.2803 | 16.8667 | 31.5919 | 45.3222 | 62.0387 | 0.03342%
12114 | 6-58.5 | -58.448 | 6.0473 | 664.6846 | 8.6812 | 17.5491 | 32.474 | 46.3706 | 63.301 | 0.03376%
12115 | 6-58 | -58.1767 | 6.0473 | 669.0377 | 9.0727 | 18.1928 | 33.2716 | 47.2897 | 64.3932 | 0.03394%
12116 | 6-58 | -57.9054 | 6.0473 | 673.865 | 9.4474 | 18.7943 | 33.997 | 48.1113 | 65.3566 | 0.03405%
12117 | 6-57.5 | -57.6341 | 6.0473 | 679.1565 | 9.8025 | 19.3524 | 34.6565 | 48.8485 | 66.2118 | 0.03411%
12118 | 6-57.5 | -57.3628 | 6.0473 | 684.9012 | 10.1275 | 19.8573 | 35.2646 | 49.5342 | 67.0215 | 0.03421%
12119 | 6-57 | -57.0914 | 6.0473 | 691.088 | 10.4123 | 20.2975 | 35.8066 | 50.1632 | 67.7721 | 0.03436%
12120 | 6-57 | -56.8201 | 6.0473 | 697.705 | 10.6528 | 20.6684 | 36.2808 | 50.7335 | 68.4578 | 0.03456%
12121 | 6-61.5 | -61.4326 | 6.3186 | 631.4015 | 6.972 | 14.2294 | 28.5283 | 41.8741 | 57.9199 | 0.03257%
12122 | 6-61 | -61.1613 | 6.3186 | 630.1034 | 7.2745 | 14.7907 | 29.2928 | 42.7574 | 58.9371 | 0.03285%
12123 | 6-61 | -60.8899 | 6.3186 | 629.3402 | 7.6007 | 15.3792 | 30.0763 | 43.6618 | 59.9903 | 0.0331%
12124 | 6-60.5 | -60.6186 | 6.3186 | 629.1137 | 7.9546 | 16.0095 | 30.8877 | 44.5871 | 61.066 | 0.03332%
12125 | 6-60.5 | -60.3473 | 6.3186 | 629.4246 | 8.3413 | 16.698 | 31.7541 | 45.5849 | 62.2421 | 0.03358%
12126 | 6-60 | -60.076 | 6.3186 | 630.2721 | 8.7633 | 17.454 | 32.6991 | 46.6991 | 63.5828 | 0.03395%
12127 | 6-60 | -59.8046 | 6.3186 | 631.6539 | 9.2095 | 18.2502 | 33.7033 | 47.8965 | 65.0288 | 0.03444%
12128 | 6-59.5 | -59.5333 | 6.3186 | 633.5667 | 9.6776 | 19.0778 | 34.7562 | 49.1576 | 66.5486 | 0.035%
12129 | 6-59.5 | -59.262 | 6.3186 | 636.0056 | 10.1688 | 19.9352 | 35.8477 | 50.4734 | 68.1326 | 0.03562%
12130 | 6-59 | -58.9907 | 6.3186 | 638.9646 | 10.6668 | 20.7829 | 36.9212 | 51.767 | 69.6824 | 0.03623%
12131 | 6-58.5 | -58.7194 | 6.3186 | 642.4365 | 11.1663 | 21.6053 | 37.9462 | 52.9838 | 71.1331 | 0.03675%
12132 | 6-58.5 | -58.448 | 6.3186 | 646.4131 | 11.6672 | 22.3992 | 38.9088 | 54.1059 | 72.4593 | 0.03715%
12133 | 6-58 | -58.1767 | 6.3186 | 650.885 | 12.1536 | 23.1439 | 39.7818 | 55.0954 | 73.614 | 0.0374%
12134 | 6-58 | -57.9054 | 6.3186 | 655.8422 | 12.6128 | 23.8229 | 40.5694 | 55.9736 | 74.6268 | 0.03757%
12135 | 6-57.5 | -57.6341 | 6.3186 | 661.2737 | 13.0398 | 24.4263 | 41.2748 | 56.7494 | 75.5133 | 0.03768%
12136 | 6-57.5 | -57.3628 | 6.3186 | 667.1679 | 13.416 | 24.9592 | 41.9076 | 57.4503 | 76.3293 | 0.03784%
12137 | 6-57 | -57.0914 | 6.3186 | 673.5128 | 13.7395 | 25.4175 | 42.4647 | 58.0856 | 77.0779 | 0.03805%
12138 | 6-57 | -56.8201 | 6.3186 | 680.2956 | 14.0096 | 25.8001 | 42.9485 | 58.6582 | 77.7584 | 0.03831%
12139 | 7-61.5 | -61.4326 | 6.5899 | 612.7232 | 9.369 | 18.2557 | 34.339 | 48.9466 | 66.3746 | 0.03566%
12140 | 7-61 | -61.1613 | 6.5899 | 611.3865 | 9.7553 | 18.9408 | 35.1972 | 49.927 | 67.4955 | 0.03601%
12141 | 7-61 | -60.8899 | 6.5899 | 610.6005 | 10.1845 | 19.6642 | 36.0919 | 50.9525 | 68.6836 | 0.03634%
12142 | 7-60.5 | -60.6186 | 6.5899 | 610.3672 | 10.6499 | 20.4311 | 37.0165 | 52.0027 | 69.8998 | 0.03663%
12143 | 7-60.5 | -60.3473 | 6.5899 | 610.6874 | 11.1533 | 21.2545 | 37.9934 | 53.1199 | 71.2069 | 0.03696%
12144 | 7-60 | -60.076 | 6.5899 | 611.5602 | 11.6975 | 22.1424 | 39.0459 | 54.3456 | 72.6636 | 0.0374%
12145 | 7-60 | -59.8046 | 6.5899 | 612.9831 | 12.2689 | 23.0652 | 40.1508 | 55.6425 | 74.2071 | 0.03794%
12146 | 7-59.5 | -59.5333 | 6.5899 | 614.9525 | 12.8639 | 24.0104 | 41.296 | 56.9904 | 75.8044 | 0.03854%
12147 | 7-59.5 | -59.262 | 6.5899 | 617.4629 | 13.4837 | 24.9734 | 42.4706 | 58.3802 | 77.4465 | 0.0392%
12148 | 7-59 | -58.9907 | 6.5899 | 620.508 | 14.1093 | 25.9127 | 43.6186 | 59.7375 | 79.0408 | 0.03984%
12149 | 7-58.5 | -58.7194 | 6.5899 | 624.0798 | 14.736 | 26.8142 | 44.7138 | 61.0135 | 80.5301 | 0.04038%
12150 | 7-58.5 | -58.448 | 6.5899 | 628.1694 | 15.3645 | 27.6783 | 45.7439 | 62.1928 | 81.8924 | 0.04079%
12151 | 7-58 | -58.1767 | 6.5899 | 632.7666 | 15.968 | 28.4862 | 46.6783 | 63.2361 | 83.0825 | 0.04107%
12152 | 7-58 | -57.9054 | 6.5899 | 637.8607 | 16.5269 | 29.2157 | 47.5129 | 64.1537 | 84.1168 | 0.04128%
12153 | 7-57.5 | -57.6341 | 6.5899 | 643.4396 | 17.0325 | 29.8552 | 48.2479 | 64.9504 | 85.0051 | 0.04143%
12154 | 7-57.5 | -57.3628 | 6.5899 | 649.491 | 17.455 | 30.4055 | 48.8886 | 65.6489 | 85.8 | 0.04165%
12155 | 7-57 | -57.0914 | 6.5899 | 656.0018 | 17.807 | 30.873 | 49.4482 | 66.2788 | 86.5303 | 0.04193%
12156 | 7-57 | -56.8201 | 6.5899 | 662.9583 | 18.0942 | 31.2603 | 49.934 | 66.8497 | 87.2036 | 0.04227%
12157 | 7-61.5 | -61.4326 | 6.8613 | 594.0492 | 12.3596 | 22.9842 | 40.6669 | 56.5484 | 75.3758 | 0.03921%
12158 | 7-61 | -61.1613 | 6.8613 | 592.6715 | 12.8573 | 23.7662 | 41.6139 | 57.6202 | 76.5857 | 0.03961%
12159 | 7-61 | -60.8899 | 6.8613 | 591.8612 | 13.4138 | 24.5899 | 42.6062 | 58.7491 | 77.8805 | 0.03998%
12160 | 7-60.5 | -60.6186 | 6.8613 | 591.6208 | 14.0131 | 25.4537 | 43.6263 | 59.9006 | 79.2037 | 0.04032%
12161 | 7-60.5 | -60.3473 | 6.8613 | 591.9509 | 14.6546 | 26.3682 | 44.6939 | 61.1099 | 80.6039 | 0.0407%
12162 | 7-60 | -60.076 | 6.8613 | 592.8505 | 15.3418 | 27.3412 | 45.8323 | 62.4165 | 82.1339 | 0.04119%
12163 | 7-60 | -59.8046 | 6.8613 | 594.3171 | 16.0537 | 28.3449 | 47.0154 | 63.7802 | 83.7308 | 0.04178%
12164 | 7-59.5 | -59.5333 | 6.8613 | 596.3464 | 16.786 | 29.3674 | 48.2325 | 65.1867 | 85.3706 | 0.04244%
12165 | 7-59.5 | -59.262 | 6.8613 | 598.9328 | 17.5393 | 30.4046 | 49.4743 | 66.6304 | 87.0495 | 0.04317%
12166 | 7-59 | -58.9907 | 6.8613 | 602.0691 | 18.2925 | 31.4135 | 50.6844 | 68.0386 | 88.6792 | 0.04389%
12167 | 7-58.5 | -58.7194 | 6.8613 | 605.7467 | 19.0369 | 32.3778 | 51.835 | 69.3597 | 90.1971 | 0.04454%
12168 | 7-58.5 | -58.448 | 6.8613 | 609.9559 | 19.7701 | 33.297 | 52.9126 | 70.5753 | 91.5776 | 0.04506%
12169 | 7-58 | -58.1767 | 6.8613 | 614.6856 | 20.461 | 34.1491 | 53.8822 | 71.6422 | 92.7761 | 0.04545%
12170 | 7-58 | -57.9054 | 6.8613 | 619.9241 | 21.0895 | 34.9118 | 54.7404 | 72.5723 | 93.8128 | 0.04577%
12171 | 7-57.5 | -57.6341 | 6.8613 | 625.6584 | 21.6457 | 35.574 | 55.4879 | 73.371 | 94.6978 | 0.04604%
12172 | 7-57.5 | -57.3628 | 6.8613 | 631.8752 | 22.0948 | 36.1333 | 56.1267 | 74.0594 | 95.4799 | 0.04636%
12173 | 7-57 | -57.0914 | 6.8613 | 638.5602 | 22.4549 | 36.6032 | 56.6817 | 74.6807 | 96.2044 | 0.04677%
12174 | 7-57 | -56.8201 | 6.8613 | 645.6991 | 22.7374 | 36.9896 | 57.1637 | 75.2489 | 96.8841 | 0.04725%
12175 | 7-61.5 | -61.4326 | 7.1326 | 575.3798 | 16.0186 | 28.1574 | 47.3414 | 64.5103 | 84.7709 | 0.04316%
12176 | 7-61 | -61.1613 | 7.1326 | 573.9585 | 16.6431 | 29.0175 | 48.3658 | 65.6612 | 86.0702 | 0.04363%
12177 | 7-61 | -60.8899 | 7.1326 | 573.1225 | 17.3261 | 29.9199 | 49.4355 | 66.8664 | 87.4522 | 0.0441%
12178 | 7-60.5 | -60.6186 | 7.1326 | 572.8744 | 18.0487 | 30.859 | 50.5269 | 68.0839 | 88.8507 | 0.04455%
12179 | 7-60.5 | -60.3473 | 7.1326 | 573.215 | 18.8101 | 31.8453 | 51.6586 | 69.3461 | 90.3099 | 0.04505%
12180 | 7-60 | -60.076 | 7.1326 | 574.1432 | 19.614 | 32.8869 | 52.8547 | 70.6922 | 91.8812 | 0.04567%
12181 | 7-60 | -59.8046 | 7.1326 | 575.6562 | 20.4379 | 33.9551 | 54.0879 | 72.0829 | 93.4998 | 0.04639%
12182 | 7-59.5 | -59.5333 | 7.1326 | 577.7494 | 21.2778 | 35.0389 | 55.3523 | 73.5144 | 95.1597 | 0.0472%
12183 | 7-59.5 | -59.262 | 7.1326 | 580.4165 | 22.1339 | 36.1352 | 56.6417 | 74.9865 | 96.8674 | 0.04811%
12184 | 7-59 | -58.9907 | 7.1326 | 583.6497 | 22.983 | 37.1998 | 57.8996 | 76.4271 | 98.5347 | 0.04903%
12185 | 7-58.5 | -58.7194 | 7.1326 | 587.4395 | 23.8065 | 38.2107 | 59.0884 | 77.771 | 100.0791 | 0.04989%
12186 | 7-58.5 | -58.448 | 7.1326 | 591.7754 | 24.5958 | 39.1649 | 60.1904 | 78.9931 | 101.4646 | 0.05063%
12187 | 7-58 | -58.1767 | 7.1326 | 596.6453 | 25.3149 | 40.0367 | 61.1669 | 80.0466 | 102.6434 | 0.05123%
12188 | 7-58 | -57.9054 | 7.1326 | 602.0364 | 25.9615 | 40.8104 | 62.0252 | 80.9591 | 103.6583 | 0.05173%
12189 | 7-57.5 | -57.6341 | 7.1326 | 607.9347 | 26.5288 | 41.4768 | 62.7689 | 81.7417 | 104.5274 | 0.05216%
12190 | 7-57.5 | -57.3628 | 7.1326 | 614.3257 | 26.9798 | 42.0299 | 63.3934 | 82.4081 | 105.2886 | 0.05263%
12191 | 7-57 | -57.0914 | 7.1326 | 621.1941 | 27.3354 | 42.4878 | 63.9297 | 83.0091 | 105.9957 | 0.05316%
12192 | 7-57 | -56.8201 | 7.1326 | 628.5242 | 27.6089 | 42.8583 | 64.3911 | 83.5607 | 106.6624 | 0.05375%
12193 | 7-61.5 | -61.4326 | 7.4039 | 556.7156 | 20.3228 | 33.72 | 54.3828 | 72.8357 | 94.6729 | 0.04809%
12194 | 7-61 | -61.1613 | 7.4039 | 555.2477 | 21.0454 | 34.6448 | 55.4683 | 74.0352 | 96.0149 | 0.04871%
12195 | 7-61 | -60.8899 | 7.4039 | 554.3842 | 21.8249 | 35.6112 | 56.5967 | 75.2852 | 97.4331 | 0.04936%
12196 | 7-60.5 | -60.6186 | 7.4039 | 554.1279 | 22.6407 | 36.6113 | 57.7413 | 76.541 | 98.8588 | 0.05%
12197 | 7-60.5 | -60.3473 | 7.4039 | 554.4797 | 23.4908 | 37.6547 | 58.9188 | 77.8318 | 100.3315 | 0.05069%
12198 | 7-60 | -60.076 | 7.4039 | 555.4385 | 24.378 | 38.7498 | 60.1526 | 79.1953 | 101.8994 | 0.05151%
12199 | 7-60 | -59.8046 | 7.4039 | 557.001 | 25.278 | 39.8665 | 61.4153 | 80.5931 | 103.5006 | 0.05243%
12200 | 7-59.5 | -59.5333 | 7.4039 | 559.1623 | 26.1857 | 40.9953 | 62.706 | 82.0314 | 105.1439 | 0.05347%
12201 | 7-59.5 | -59.262 | 7.4039 | 561.9153 | 27.1007 | 42.1339 | 64.0213 | 83.5163 | 106.8444 | 0.05465%
12202 | 7-59 | -58.9907 | 7.4039 | 565.2516 | 27.9971 | 43.2366 | 65.3042 | 84.9758 | 108.5154 | 0.05588%
12203 | 7-58.5 | -58.7194 | 7.4039 | 569.1607 | 28.8563 | 44.2762 | 66.5071 | 86.3303 | 110.0523 | 0.05702%
12204 | 7-58.5 | -58.448 | 7.4039 | 573.631 | 29.672 | 45.2471 | 67.608 | 87.5479 | 111.4072 | 0.05801%
12205 | 7-58 | -58.1767 | 7.4039 | 578.6496 | 30.4052 | 46.12 | 68.5642 | 88.578 | 112.5374 | 0.0588%
12206 | 7-58 | -57.9054 | 7.4039 | 584.2021 | 31.0587 | 46.8877 | 69.3975 | 89.466 | 113.5098 | 0.05948%
12207 | 7-57.5 | -57.6341 | 7.4039 | 590.2737 | 31.6278 | 47.5448 | 70.1173 | 90.231 | 114.3492 | 0.06008%
12208 | 7-57.5 | -57.3628 | 7.4039 | 596.8484 | 32.0729 | 48.0789 | 70.7066 | 90.8726 | 115.071 | 0.06066%
12209 | 7-57 | -57.0914 | 7.4039 | 603.9097 | 32.4172 | 48.5107 | 71.1986 | 91.4438 | 115.7287 | 0.06128%
12210 | 7-57 | -56.8201 | 7.4039 | 611.4409 | 32.6756 | 48.8503 | 71.6135 | 91.9616 | 116.3364 | 0.06194%
12211 | 8-61.5 | -61.4326 | 7.6752 | 538.0571 | 25.1795 | 39.6537 | 61.8033 | 81.4803 | 104.8979 | 0.05446%
12212 | 8-61 | -61.1613 | 7.6752 | 536.5394 | 25.9506 | 40.6166 | 62.9028 | 82.6782 | 106.1962 | 0.05527%
12213 | 8-61 | -60.8899 | 7.6752 | 535.6465 | 26.7826 | 41.6272 | 64.0539 | 83.9413 | 107.5786 | 0.05614%
12214 | 8-60.5 | -60.6186 | 7.6752 | 535.3815 | 27.6534 | 42.6743 | 65.2257 | 85.221 | 108.9781 | 0.05703%
12215 | 8-60.5 | -60.3473 | 7.6752 | 535.7453 | 28.558 | 43.763 | 66.4266 | 86.5343 | 110.4226 | 0.05798%
12216 | 8-60 | -60.076 | 7.6752 | 536.7367 | 29.4973 | 44.8985 | 67.6744 | 87.9106 | 111.9476 | 0.05905%
12217 | 8-60 | -59.8046 | 7.6752 | 538.3521 | 30.4454 | 46.0496 | 68.9417 | 89.3124 | 113.4948 | 0.06023%
12218 | 8-59.5 | -59.5333 | 7.6752 | 540.5861 | 31.3945 | 47.2042 | 70.2279 | 90.7458 | 115.0739 | 0.06152%
12219 | 8-59.5 | -59.262 | 7.6752 | 543.4308 | 32.343 | 48.3589 | 71.5294 | 92.2156 | 116.7025 | 0.06297%
12220 | 8-59 | -58.9907 | 7.6752 | 546.877 | 33.2631 | 49.4669 | 72.7885 | 93.6503 | 118.2994 | 0.06445%
12221 | 8-58.5 | -58.7194 | 7.6752 | 550.9131 | 34.1384 | 50.5037 | 73.961 | 94.9739 | 119.7638 | 0.06584%
12222 | 8-58.5 | -58.448 | 7.6752 | 555.5264 | 34.9636 | 51.4652 | 75.0269 | 96.1568 | 121.0501 | 0.06705%
12223 | 8-58 | -58.1767 | 7.6752 | 560.7026 | 35.696 | 52.318 | 75.9401 | 97.1465 | 122.117 | 0.06803%
12224 | 8-58 | -57.9054 | 7.6752 | 566.4264 | 36.3423 | 53.0607 | 76.7306 | 97.9988 | 123.0377 | 0.06889%
12225 | 8-57.5 | -57.6341 | 7.6752 | 572.6811 | 36.8996 | 53.6901 | 77.4112 | 98.7364 | 123.8386 | 0.06966%
12226 | 8-57.5 | -57.3628 | 7.6752 | 579.4498 | 37.3255 | 54.1888 | 77.9537 | 99.3382 | 124.4991 | 0.07035%
12227 | 8-57 | -57.0914 | 7.6752 | 586.7145 | 37.6458 | 54.5806 | 78.3948 | 99.859 | 125.0879 | 0.07103%
12228 | 8-57 | -56.8201 | 7.6752 | 594.4571 | 37.877 | 54.877 | 78.7567 | 100.3168 | 125.6214 | 0.07172%
12229 | 8-61.5 | -61.4326 | 7.9465 | 519.4049 | 30.3604 | 45.8396 | 69.4163 | 90.4995 | 115.0737 | 0.06276%
12230 | 8-61 | -61.1613 | 7.9465 | 517.8339 | 31.1596 | 46.8049 | 70.4734 | 91.6233 | 116.2745 | 0.06369%
12231 | 8-61 | -60.8899 | 7.9465 | 516.9095 | 32.0279 | 47.8323 | 71.6092 | 92.8509 | 117.5897 | 0.06477%
12232 | 8-60.5 | -60.6186 | 7.9465 | 516.6351 | 32.9416 | 48.9082 | 72.7897 | 94.1296 | 118.9498 | 0.06591%
12233 | 8-60.5 | -60.3473 | 7.9465 | 517.0118 | 33.8902 | 50.0277 | 74.0056 | 95.4512 | 120.3628 | 0.06716%
12234 | 8-60 | -60.076 | 7.9465 | 518.0381 | 34.8706 | 51.1896 | 75.2626 | 96.8274 | 121.8463 | 0.06854%
12235 | 8-60 | -59.8046 | 7.9465 | 519.7102 | 35.8539 | 52.3591 | 76.5298 | 98.2167 | 123.339 | 0.07001%
12236 | 8-59.5 | -59.5333 | 7.9465 | 522.022 | 36.827 | 53.517 | 77.7962 | 99.6103 | 124.8404 | 0.07158%
12237 | 8-59.5 | -59.262 | 7.9465 | 524.9648 | 37.7855 | 54.6559 | 79.0528 | 101.0046 | 126.3619 | 0.07326%
12238 | 8-59 | -58.9907 | 7.9465 | 528.5283 | 38.6995 | 55.7287 | 80.2427 | 102.3327 | 127.8262 | 0.07493%
12239 | 8-58.5 | -58.7194 | 7.9465 | 532.6999 | 39.5603 | 56.7238 | 81.3448 | 103.5497 | 129.1649 | 0.0765%
12240 | 8-58.5 | -58.448 | 7.9465 | 537.4655 | 40.3672 | 57.6445 | 82.351 | 104.6415 | 130.3491 | 0.07789%
12241 | 8-58 | -58.1767 | 7.9465 | 542.8094 | 41.0747 | 58.453 | 83.21 | 105.5552 | 131.3386 | 0.07906%
12242 | 8-58 | -57.9054 | 7.9465 | 548.7147 | 41.6909 | 59.1489 | 83.9507 | 106.3451 | 132.2 | 0.0801%
12243 | 8-57.5 | -57.6341 | 7.9465 | 555.1636 | 42.2139 | 59.7295 | 84.5859 | 107.0325 | 132.9566 | 0.08105%
12244 | 8-57.5 | -57.3628 | 7.9465 | 562.1372 | 42.6006 | 60.1737 | 85.0791 | 107.5806 | 133.5725 | 0.08186%
12245 | 8-57 | -57.0914 | 7.9465 | 569.6164 | 42.8792 | 60.5079 | 85.4695 | 108.0455 | 134.1187 | 0.08264%
12246 | 8-57 | -56.8201 | 7.9465 | 577.5814 | 43.0676 | 60.7447 | 85.7804 | 108.4462 | 134.6086 | 0.0834%
12247 | 8-61.5 | -61.4326 | 8.2179 | 500.7597 | 35.8512 | 52.2973 | 77.2783 | 99.8366 | 125.0683 | 0.07323%
12248 | 8-61 | -61.1613 | 8.2179 | 499.1314 | 36.6617 | 53.2422 | 78.2684 | 100.8399 | 126.1577 | 0.07427%
12249 | 8-61 | -60.8899 | 8.2179 | 498.1731 | 37.554 | 54.2706 | 79.3759 | 101.9961 | 127.4148 | 0.07556%
12250 | 8-60.5 | -60.6186 | 8.2179 | 497.8887 | 38.5017 | 55.3641 | 80.562 | 103.2569 | 128.7695 | 0.07705%
12251 | 8-60.5 | -60.3473 | 8.2179 | 498.2792 | 39.4845 | 56.5023 | 81.791 | 104.5729 | 130.1883 | 0.07868%
12252 | 8-60 | -60.076 | 8.2179 | 499.3431 | 40.493 | 57.6732 | 83.0493 | 105.9262 | 131.659 | 0.08044%
12253 | 8-60 | -59.8046 | 8.2179 | 501.0761 | 41.4934 | 58.8358 | 84.2993 | 107.2649 | 133.1107 | 0.08226%
12254 | 8-59.5 | -59.5333 | 8.2179 | 503.4713 | 42.4678 | 59.963 | 85.5189 | 108.5632 | 134.5287 | 0.08411%
12255 | 8-59.5 | -59.262 | 8.2179 | 506.5193 | 43.4109 | 61.0434 | 86.6925 | 109.8128 | 135.9167 | 0.08598%
12256 | 8-59 | -58.9907 | 8.2179 | 510.2084 | 44.2911 | 62.0347 | 87.7678 | 110.9566 | 137.2074 | 0.08775%
12257 | 8-58.5 | -58.7194 | 8.2179 | 514.5248 | 45.111 | 62.9431 | 88.7544 | 111.997 | 138.3859 | 0.0894%
12258 | 8-58.5 | -58.448 | 8.2179 | 519.4529 | 45.8751 | 63.7811 | 89.6595 | 112.9427 | 139.4459 | 0.09092%
12259 | 8-58 | -58.1767 | 8.2179 | 524.9753 | 46.5357 | 64.5098 | 90.4323 | 113.7421 | 140.3408 | 0.09222%
12260 | 8-58 | -57.9054 | 8.2179 | 531.0737 | 47.1017 | 65.1275 | 91.0973 | 114.4398 | 141.1268 | 0.0934%
12261 | 8-57.5 | -57.6341 | 8.2179 | 537.7284 | 47.5718 | 65.631 | 91.6647 | 115.0521 | 141.8219 | 0.09448%
12262 | 8-57.5 | -57.3628 | 8.2179 | 544.9189 | 47.9027 | 65.9984 | 92.0937 | 115.5347 | 142.3835 | 0.0954%
12263 | 8-57 | -57.0914 | 8.2179 | 552.6244 | 48.1262 | 66.2589 | 92.4255 | 115.945 | 142.8843 | 0.09627%
12264 | 8-57 | -56.8201 | 8.2179 | 560.8237 | 48.2614 | 66.4265 | 92.684 | 116.3029 | 143.339 | 0.09709%
12265 | 15-90 | -89.9213 | 15.0009 | 1950.9712 | 103.9212 | 135.7297 | 179.8339 | 206.5479 | 237.1173 | 0.6226%
12266 | 15-89.5 | -89.65 | 15.0009 | 1932.9256 | 104.1334 | 135.9913 | 180.4249 | 207.6251 | 238.682 | 0.63%
12267 | 15-89.5 | -89.3787 | 15.0009 | 1914.8793 | 104.266 | 136.1453 | 180.74 | 208.3451 | 239.7589 | 0.6346%
12268 | 15-89 | -89.1074 | 15.0009 | 1896.8322 | 104.2102 | 135.9974 | 180.691 | 208.5602 | 240.1627 | 0.6343%
12269 | 15-89 | -88.836 | 15.0009 | 1878.7843 | 104.0917 | 135.6153 | 180.4031 | 208.4919 | 240.1852 | 0.6313%
12270 | 15-88.5 | -88.5647 | 15.0009 | 1860.7357 | 104.2852 | 135.6585 | 180.4734 | 208.7708 | 240.6127 | 0.6339%
12271 | 15-88.5 | -88.2934 | 15.0009 | 1842.6864 | 104.864 | 136.2278 | 180.9893 | 209.5612 | 241.6653 | 0.6438%
12272 | 15-88 | -88.0221 | 15.0009 | 1824.6364 | 105.8378 | 137.3252 | 181.9739 | 210.9198 | 243.4258 | 0.6616%
12273 | 15-90 | -89.9213 | 15.2722 | 1949.4976 | 102.7337 | 134.4551 | 179.0159 | 205.9513 | 236.764 | 0.6069%
12274 | 15-89.5 | -89.65 | 15.2722 | 1931.4626 | 103.6371 | 135.5176 | 180.309 | 207.7521 | 239.1386 | 0.6253%
12275 | 15-89.5 | -89.3787 | 15.2722 | 1913.4268 | 104.4362 | 136.4578 | 181.3097 | 209.1826 | 241.0118 | 0.641%
12276 | 15-89 | -89.1074 | 15.2722 | 1895.3902 | 105.0187 | 137.0668 | 181.9051 | 210.0786 | 242.1779 | 0.6517%
12277 | 15-89 | -88.836 | 15.2722 | 1877.3528 | 105.4822 | 137.3846 | 182.1887 | 210.634 | 242.9038 | 0.6586%
12278 | 15-88.5 | -88.5647 | 15.2722 | 1859.3146 | 106.2112 | 138.0474 | 182.787 | 211.4877 | 243.9831 | 0.6707%
12279 | 15-88.5 | -88.2934 | 15.2722 | 1841.2756 | 107.2988 | 139.1852 | 183.8108 | 212.8296 | 245.665 | 0.6903%
12280 | 15-88 | -88.0221 | 15.2722 | 1823.2358 | 108.7618 | 140.8113 | 185.2876 | 214.723 | 248.039 | 0.7185%
12281 | 16-90 | -89.9213 | 15.5435 | 1948.1886 | 101.9492 | 133.567 | 178.4822 | 205.6028 | 236.6598 | 0.5969%
12282 | 16-89.5 | -89.65 | 15.5435 | 1930.166 | 103.5177 | 135.4161 | 180.4675 | 208.1362 | 239.8794 | 0.6259%
12283 | 16-89.5 | -89.3787 | 15.5435 | 1912.1426 | 104.9561 | 137.1183 | 182.1269 | 210.2732 | 242.5647 | 0.6526%
12284 | 16-89 | -89.1074 | 15.5435 | 1894.1183 | 106.1483 | 138.4507 | 183.3219 | 211.8325 | 244.4877 | 0.6742%
12285 | 16-89 | -88.836 | 15.5435 | 1876.0933 | 107.1731 | 139.4258 | 184.1304 | 212.9865 | 245.8966 | 0.6915%
12286 | 16-88.5 | -88.5647 | 15.5435 | 1858.0674 | 108.4298 | 140.6848 | 185.225 | 214.4042 | 247.6233 | 0.714%
12287 | 16-88.5 | -88.2934 | 15.5435 | 1840.0407 | 110.022 | 142.3736 | 186.73 | 216.2865 | 249.9262 | 0.7446%
12288 | 16-88 | -88.0221 | 15.5435 | 1822.0133 | 111.9696 | 144.5102 | 188.6721 | 218.6976 | 252.8951 | 0.7848%
12289 | 16-90 | -89.9213 | 15.8149 | 1947.0444 | 101.5622 | 133.0729 | 178.2314 | 205.5177 | 236.8055 | 0.5923%
12290 | 16-89.5 | -89.65 | 15.8149 | 1929.0361 | 103.7636 | 135.6678 | 180.8475 | 208.7583 | 240.8571 | 0.6315%
12291 | 16-89.5 | -89.3787 | 15.8149 | 1911.0269 | 105.8121 | 138.0941 | 183.1148 | 211.577 | 244.3402 | 0.6691%
12292 | 16-89 | -89.1074 | 15.8149 | 1893.0169 | 107.5919 | 140.121 | 184.8847 | 213.786 | 247.0191 | 0.7021%
12293 | 16-89 | -88.836 | 15.8149 | 1875.0062 | 109.1689 | 141.7297 | 186.214 | 215.542 | 249.1273 | 0.7308%
12294 | 16-88.5 | -88.5647 | 15.8149 | 1856.9946 | 110.9491 | 143.5689 | 187.8023 | 217.5279 | 251.5148 | 0.765%
12295 | 16-88.5 | -88.2934 | 15.8149 | 1838.9823 | 113.0424 | 145.7938 | 189.7813 | 219.9523 | 254.4481 | 0.8084%
12296 | 16-88 | -88.0221 | 15.8149 | 1820.9692 | 115.4703 | 148.4244 | 192.1735 | 222.8774 | 258.0138 | 0.8629%
12297 | 16-90 | -89.9213 | 16.0862 | 1946.0654 | 101.814 | 133.3285 | 178.5521 | 206.0759 | 237.6694 | 0.5973%
12298 | 16-89.5 | -89.65 | 16.0862 | 1928.0731 | 104.5903 | 136.6066 | 181.7395 | 209.9692 | 242.4958 | 0.6466%
12299 | 16-89.5 | -89.3787 | 16.0862 | 1910.0801 | 107.1987 | 139.6985 | 184.5698 | 213.4216 | 246.7273 | 0.6955%
12300 | 16-89 | -89.1074 | 16.0862 | 1892.0863 | 109.5284 | 142.3617 | 186.8931 | 216.2517 | 250.1377 | 0.7406%
12301 | 16-89 | -88.836 | 16.0862 | 1874.0917 | 111.6373 | 144.5611 | 188.7517 | 218.6055 | 252.9501 | 0.7819%
12302 | 16-88.5 | -88.5647 | 16.0862 | 1856.0965 | 113.9223 | 146.9401 | 190.8313 | 221.1482 | 255.9906 | 0.8297%
12303 | 16-88.5 | -88.2934 | 16.0862 | 1838.1005 | 116.4962 | 149.6593 | 193.2662 | 224.094 | 259.5337 | 0.888%
12304 | 16-88 | -88.0221 | 16.0862 | 1820.1038 | 119.3744 | 152.7388 | 196.0741 | 227.5029 | 263.6634 | 0.9592%
12305 | 16-90 | -89.9213 | 16.3575 | 1945.2518 | 102.5047 | 134.1394 | 179.1886 | 206.9364 | 238.8061 | 0.6086%
12306 | 16-89.5 | -89.65 | 16.3575 | 1927.2775 | 105.7492 | 137.9931 | 182.8389 | 211.3554 | 244.2503 | 0.6672%
12307 | 16-89.5 | -89.3787 | 16.3575 | 1909.3024 | 108.8386 | 141.656 | 186.1626 | 215.3562 | 249.1271 | 0.7271%
12308 | 16-89 | -89.1074 | 16.3575 | 1891.3267 | 111.6651 | 144.8879 | 189.0071 | 218.7601 | 253.2154 | 0.785%
12309 | 16-89 | -88.836 | 16.3575 | 1873.3503 | 114.279 | 147.638 | 191.3997 | 221.7004 | 256.7237 | 0.8403%
12310 | 16-88.5 | -88.5647 | 16.3575 | 1855.3733 | 117.0375 | 150.5101 | 193.9587 | 224.7764 | 260.3925 | 0.9032%
12311 | 16-88.5 | -88.2934 | 16.3575 | 1837.3956 | 120.0504 | 153.6701 | 196.8188 | 228.2081 | 264.5054 | 0.9783%
12312 | 16-88 | -88.0221 | 16.3575 | 1819.4173 | 123.3343 | 157.1388 | 200.0022 | 232.055 | 269.1461 | 1.068%
12313 | 17-90 | -89.9213 | 16.6288 | 1944.6039 | 103.4434 | 135.2304 | 179.9417 | 207.8669 | 239.9498 | 0.6233%
12314 | 17-89.5 | -89.65 | 16.6288 | 1926.6493 | 106.9811 | 139.4281 | 183.8485 | 212.5741 | 245.7178 | 0.6886%
12315 | 17-89.5 | -89.3787 | 16.6288 | 1908.6941 | 110.4231 | 143.4933 | 187.5021 | 216.9569 | 251.0374 | 0.7577%
12316 | 17-89 | -89.1074 | 16.6288 | 1890.7383 | 113.6673 | 147.1879 | 190.7538 | 220.8431 | 255.6965 | 0.8274%
12317 | 17-89 | -88.836 | 16.6288 | 1872.782 | 116.7551 | 150.4439 | 193.6572 | 224.3523 | 259.8874 | 0.8976%
12318 | 17-88.5 | -88.5647 | 16.6288 | 1854.8252 | 119.9504 | 153.7648 | 196.6645 | 227.9407 | 264.1661 | 0.9766%
12319 | 17-88.5 | -88.2934 | 16.6288 | 1836.8679 | 123.3633 | 157.316 | 199.9104 | 231.8296 | 268.8203 | 1.069%
12320 | 17-88 | -88.0221 | 16.6288 | 1818.9101 | 127.0108 | 161.1187 | 203.4349 | 236.0775 | 273.9326 | 1.179%
12321 | 17-90 | -89.9213 | 16.9002 | 1944.1217 | 104.4975 | 136.392 | 180.6714 | 208.7083 | 240.9197 | 0.639%
12322 | 17-89.5 | -89.65 | 16.9002 | 1926.1887 | 108.1043 | 140.6395 | 184.5873 | 213.3914 | 246.6192 | 0.707%
12323 | 17-89.5 | -89.3787 | 16.9002 | 1908.2552 | 111.7385 | 144.8826 | 188.3964 | 217.9401 | 252.1144 | 0.7819%
12324 | 17-89 | -89.1074 | 16.9002 | 1890.3213 | 115.3073 | 148.9103 | 191.9594 | 222.1938 | 257.2073 | 0.8617%
12325 | 17-89 | -88.836 | 16.9002 | 1872.387 | 118.8315 | 152.6276 | 195.3398 | 226.254 | 262.0664 | 0.9466%
12326 | 17-88.5 | -88.5647 | 16.9002 | 1854.4524 | 122.4306 | 156.3583 | 198.7596 | 230.3402 | 266.9448 | 1.042%
12327 | 17-88.5 | -88.2934 | 16.9002 | 1836.5174 | 126.2095 | 160.2588 | 202.3701 | 234.6665 | 272.1231 | 1.153%
12328 | 17-88 | -88.0221 | 16.9002 | 1818.5821 | 130.1841 | 164.3476 | 206.21 | 239.2893 | 277.6805 | 1.283%
12329 | 17-90 | -89.9213 | 17.1715 | 1943.8055 | 105.722 | 137.8116 | 181.5329 | 209.6436 | 241.9293 | 0.6581%
12330 | 17-89.5 | -89.65 | 17.1715 | 1925.8958 | 109.1536 | 141.8747 | 185.1877 | 213.9535 | 247.1123 | 0.7244%
12331 | 17-89.5 | -89.3787 | 17.1715 | 1907.9859 | 112.7886 | 146.0554 | 188.933 | 218.3892 | 252.4306 | 0.8009%
12332 | 17-89 | -89.1074 | 17.1715 | 1890.0758 | 116.5605 | 150.2289 | 192.6658 | 222.8341 | 257.7386 | 0.8876%
12333 | 17-89 | -88.836 | 17.1715 | 1872.1655 | 120.4628 | 154.3243 | 196.4492 | 227.3744 | 263.1814 | 0.9858%
12334 | 17-88.5 | -88.5647 | 17.1715 | 1854.255 | 124.4233 | 158.4047 | 200.239 | 231.9111 | 268.6067 | 1.096%
12335 | 17-88.5 | -88.2934 | 17.1715 | 1836.3444 | 128.5275 | 162.596 | 204.1722 | 236.6281 | 274.2573 | 1.224%
12336 | 17-88 | -88.0221 | 17.1715 | 1818.4336 | 132.7868 | 166.9091 | 208.2825 | 241.5747 | 280.202 | 1.373%
12337 | 17-90 | -89.9213 | 17.4428 | 1943.6552 | 107.3383 | 139.7808 | 182.8761 | 211.2048 | 243.7431 | 0.6864%
12338 | 17-89.5 | -89.65 | 17.4428 | 1925.7708 | 110.5664 | 143.5972 | 186.2505 | 215.128 | 248.4048 | 0.7511%
12339 | 17-89.5 | -89.3787 | 17.4428 | 1907.8864 | 114.1372 | 147.6233 | 189.8664 | 219.3737 | 253.4559 | 0.8286%
12340 | 17-89 | -89.1074 | 17.4428 | 1890.0019 | 118.0256 | 151.8058 | 193.6716 | 223.8906 | 258.834 | 0.9208%
12341 | 17-89 | -88.836 | 17.4428 | 1872.1175 | 122.2032 | 156.129 | 197.7318 | 228.7672 | 264.6842 | 1.031%
12342 | 17-88.5 | -88.5647 | 17.4428 | 1854.2331 | 126.4364 | 160.4285 | 201.7921 | 233.6314 | 270.5053 | 1.155%
12343 | 17-88.5 | -88.2934 | 17.4428 | 1836.3488 | 130.7827 | 164.7879 | 205.956 | 238.6242 | 276.4851 | 1.299%
12344 | 17-88 | -88.0221 | 17.4428 | 1818.4646 | 135.2465 | 169.207 | 210.2496 | 243.7844 | 282.6787 | 1.465%
12345 | 18-90 | -89.9213 | 17.7141 | 1943.671 | 109.3222 | 142.2388 | 184.6708 | 213.3527 | 246.3111 | 0.7246%
12346 | 18-89.5 | -89.65 | 17.7141 | 1925.8137 | 112.3723 | 145.7947 | 187.8051 | 216.953 | 250.546 | 0.7885%
12347 | 18-89.5 | -89.3787 | 17.7141 | 1907.9565 | 115.8536 | 149.6213 | 191.2722 | 220.9915 | 255.3167 | 0.8672%
12348 | 18-89 | -89.1074 | 17.7141 | 1890.0996 | 119.7879 | 153.7101 | 195.0737 | 225.4889 | 260.6542 | 0.9643%
12349 | 18-89 | -88.836 | 17.7141 | 1872.2429 | 124.1251 | 158.088 | 199.2846 | 230.5445 | 266.717 | 1.084%
12350 | 18-88.5 | -88.5647 | 17.7141 | 1854.3866 | 128.5278 | 162.4523 | 203.5057 | 235.5985 | 272.762 | 1.22%
12351 | 18-88.5 | -88.2934 | 17.7141 | 1836.5306 | 133.02 | 166.8458 | 207.7995 | 240.7394 | 278.9107 | 1.377%
12352 | 18-88 | -88.0221 | 17.7141 | 1818.675 | 137.597 | 171.2655 | 212.1825 | 245.9934 | 285.2017 | 1.557%
12353 | 18-90 | -89.9213 | 17.9854 | 1943.8528 | 111.419 | 144.8206 | 186.5639 | 215.5845 | 248.9414 | 0.7673%
12354 | 18-89.5 | -89.65 | 17.9854 | 1926.0244 | 114.3347 | 148.1456 | 189.518 | 218.948 | 252.8694 | 0.8316%
12355 | 18-89.5 | -89.3787 | 17.9854 | 1908.1963 | 117.7343 | 151.7871 | 192.8565 | 222.8131 | 257.4104 | 0.9122%
12356 | 18-89 | -89.1074 | 17.9854 | 1890.3688 | 121.6665 | 155.7494 | 196.6099 | 227.2402 | 262.6496 | 1.014%
12357 | 18-89 | -88.836 | 17.9854 | 1872.5419 | 126.0539 | 160.0732 | 200.8555 | 232.3304 | 268.7459 | 1.141%
12358 | 18-88.5 | -88.5647 | 17.9854 | 1854.7155 | 130.5205 | 164.4109 | 205.1267 | 237.4362 | 274.8438 | 1.286%
12359 | 18-88.5 | -88.2934 | 17.9854 | 1836.8898 | 135.0591 | 168.759 | 209.4467 | 242.5955 | 280.9998 | 1.453%
12360 | 18-88 | -88.0221 | 17.9854 | 1819.0648 | 139.6561 | 173.1028 | 213.8225 | 247.8218 | 287.2361 | 1.643%
12361 | 18-90 | -89.9213 | 18.2568 | 1944.2006 | 113.7405 | 147.6947 | 188.7477 | 218.1821 | 252.0289 | 0.8187%
12362 | 18-89.5 | -89.65 | 18.2568 | 1926.4028 | 116.484 | 150.7443 | 191.4814 | 221.2665 | 255.6059 | 0.8827%
12363 | 18-89.5 | -89.3787 | 18.2568 | 1908.6058 | 119.7572 | 154.1509 | 194.6435 | 224.9039 | 259.8559 | 0.9643%
12364 | 18-89 | -89.1074 | 18.2568 | 1890.8096 | 123.6405 | 157.9381 | 198.299 | 229.2028 | 264.9292 | 1.07%
12365 | 18-89 | -88.836 | 18.2568 | 1873.0142 | 128.0278 | 162.1574 | 202.5305 | 234.2693 | 270.9896 | 1.204%
12366 | 18-88.5 | -88.5647 | 18.2568 | 1855.2197 | 132.5166 | 166.4299 | 206.8132 | 239.381 | 277.0855 | 1.358%
12367 | 18-88.5 | -88.2934 | 18.2568 | 1837.4263 | 137.0649 | 170.7017 | 211.1276 | 244.5207 | 283.2036 | 1.533%
12368 | 18-88 | -88.0221 | 18.2568 | 1819.6339 | 141.6494 | 174.9443 | 215.4699 | 249.6881 | 289.3483 | 1.733%

## REST
RETROFITTING ECONOMIC SUPPORT TOOL (REST)
REST Excel application for the economic evaluation of SMART retrofitting of healthcare facilities. Please, read the user guide that accompanies this application.
REST Report for Add a name
Dominica ¦ Sep/30/2025
SAVINGS measured by dollars ($)
Annual estimates
DRR - Earthquake | 1475.2009 | → Dollar amount that is saved in a year due to SMART retrofittings on earthquake disaster risk reduction (DRR).
DRR - Cyclone | 5543.536 | → Dollar amount that is saved in a year due to SMART retrofittings on cyclone disaster risk reduction (DRR).
Green - Energy | 22980.65 | → Dollar amount that is saved in a year due to SMART retrofittings on energy efficient upgrades.
Green - Water | 4319.4 | → Dollar amount that is saved in a year due to SMART retrofittings on water efficient upgrades.
Total per year | 34318.7869 | → Total dollar amount that is saved in a year due to SMART retrofittings.
TOTAL over 20 years (discount rate 3%) | 510576.8892 | → Total dollar amount that is saved over 20 years discounted at a 3% rate.
SAVINGS measured by QALYs
Annual estimates
DRR - Earthquake | 16.3399 | → Quality-adjusted life years (QALYs) gained in a year due to SMART retrofittings on earthquake disaster risk reduction (DRR).
DRR - Cyclone | 224.2385 | → Quality-adjusted life years (QALYs) gained in a year due to SMART retrofittings on cyclone disaster risk reduction (DRR).
Total per year | 240.5784 | → Total QALYs gained in a year due to SMART retrofittings.
TOTAL over 20 years (discount rate 3%) | 3579.1987 | → Total QALYs gained over 20 years discounted at a 3% rate.
COSTS measured by dollars ($)
DRR | 205300 | → Total cost spent on SMART retrofittings on earthquake and cyclone disaster risk reduction (DRR).
Green - Energy | 163900 | → Total cost spent on SMART retrofittings on energy efficient upgrades.
Green - Water | 7400 | → Total cost spent on SMART retrofittings on water efficient upgrades.
TOTAL costs | 376600 | → Total cost spent on SMART retrofittings.
ECONOMIC EVALUATION
Total ROI (Return on Investment) * | 1.3558 | → Amount earned per dollar invested.
DRR ROI | 0.50863 | → Return on DRR infrastructure investments.
Green - Energy ROI | 2.086 | → Return on investment in energy efficient upgrades.
Green - Water ROI | 8.684 | → Return on investment in water efficient upgrades.
Total ICER (Incremental cost-effectiveness ratio) ** | -37.4321 | → The cost (savings if a negative dollar value) of gaining 1 quality-adjusted life year (QALY) due to SMART retrofittings.
DRR ICER | 28.1848 | → The cost (savings if a negative dollar value) of gaining 1 quality-adjusted life year (QALY) due to SMART retrofittings on DRR infrastructure investments only.
NOTES:
* A ROI greater than 1 means that savings in dollars exceed the investment, making the SMART retrofitting a financially sustainable project. In this case, the ROI is 1.4 (greater than 1.0), which implies a positive return of 0.4 dollars for each dollar invested on the SMART retrofitting project.
** An ICER shows the net costs paid for one QALY gained. The lower the ICER, the lower the cost paid per QALY gained in the project. Therefore, projects with lower ICERs are preferred because they are more cost-effective. ICERs are usually compared with the one year per-capita GDP of the country, which reflects the value people are willing to pay for one QALY gained. In this case, the ICER is $-37.4/QALY (negative), which implies that the SMART retrofitting project is saving $-37.4 dollars per QALY gained, making it a cost-effective investment.
START A NEW
REST
For internal use
CONTINUE WITH PREVIOUS REST

## Calculations (hidden)
Hazards | Magnitude | Probability
Earthquake (cm/seg2) | 30 | 10.73% | Equiv magn=6
Cyclone (km/h) | 150 | 2.937%
Physical damage
Earthquake | Quality | MDR | Loss | Savings | Expected Saving
Quality Level - baseline | 1.52 | 1.414% | 14142.3254
Quality Level - post-ret. | 2.95 | 0.03882% | 388.2076 | 13754.1178 | 1475.2009
Cyclone |  | MDR | Loss | Savings | Expected Saving
Quality Level - baseline |  | 18.91% | 189057.6645
Quality Level - post-ret. |  | 0.03047% | 304.7369 | 188752.9276 | 5543.536
Personal damage
Earthquake | Level | MDR
Quality Level - baseline | 1.52 | 1.414%
Quality Level - post-ret. | 2.95 | 0.03882%
Emergency period | Baseline | Post-ret | No Disaster |  |  | III level | Pain | Mobility | Daily liv | Total QALY | Gain if hospitalize | <<QALY hosp Vs. non-hosp, by AIS source Table 8: https://cms.data.fra.dot.gov/sites/dot.gov/files/docs/Spicer%20and%20Miller%202010%20qaly_injury_revision_pdf_final_report_02-05-10.pdf
1-day capacity | 8.2566 | 8.3717 | 8.375 | people per day | <<Source: http://www.cidrap.umn.edu/sites/default/files/public/php/258/258_acstools.pdf | 1 | 0.97 | 0.93 | 0.92 | 0.948 | 0.2844
Sev 1 - No served | 0 | 0 | 0 | <<Admitted on first 7 days |  | 2 | 0.85 | 0.79 | 0.83 | 0.828 | 0.3312
Sev 2 - No served | 0 | 0 | 0 | <<Admitted on first 7 days |  | 3 | 0.64 | 0.5 | 0.64 | 0.598 | 0.3588
Sev 3 - No served | 0 | 0 | 0 | <<Admitted on day 0 |  | 4 | 0.4 | 0.4 | 0.37 | 0.394 | 0.3546
Reconstruction period | Baseline | Post-ret | No Disaster
1-year Ambulatory capacity | 6506.6607 | 6597.4378 | 6600 |  |  |  | QALY
1-year Inpatient capacity | 0 | 0 | 0 |  |  | Sev 1 - No served | 0.29376 | <<Lots of assumptions about QALY gain by being hospitalized, and average QALY of ambulatory and inpatient
Amb - No served | 93.3393 | 2.5622 | 90.7772 |  |  | Sev 2 - No served | 0.3588
Imp - No served | 0 | 0 | 0 |  |  | Sev 3 - No served | 0.3546
[6 empty] | Sev 4 - No served | 0
TOTAL QALYs (Expected) |  |  |  | 16.3399 |  | 1-day Ambulatory care | 0.18
TOTAL QALYs in $$ (Expected) |  |  |  | 269041.7135 | <<Use: 2.03 GDP/QALY : http://journals.plos.org/plosone/article?id=10.1371/journal.pone.0122760 | 1-day Inpatient care | 0.4
Cyclone |  | MDR
Quality Level - baseline |  | 18.91%
Quality Level - post-ret. |  | 0.03047%
Emergency period | Baseline | Post-ret | No Disaster
1-day capacity | 6.7916 | 8.3724 | 8.375
Sev 1 - No served | 0 | 0 | 0
Sev 2 - No served | 0 | 0 | 0
Reconstruction period | Baseline | Post-ret | No Disaster
1-year Ambulatory capacity | 5352.2194 | 6597.9887 | 6600
1-year Inpatient capacity | 0 | 0 | 0
Amb - No served | 1247.7806 | 2.0113 | 1245.7693
Imp - No served | 0 | 0 | 0
TOTAL QALYs (Expected) |  |  |  | 224.2385

## PARAMETERS (hidden)
List of Parameters from the REST Survey
Linking items from VBA forms to parameter values
Description | Draw value |  | Input values
I) Global parameters |  |  |  |  | Construction Class |  |  | Construction Material |  |  | Number of floors |  |  | Percentage - type of constructions in sorrounded area |  |  | Country GDP (2019)
[5 empty] | Item# | Parameter | Description | Item# | Parameter | Description | Item# | Parameter | Description | Item# | Parameter | Description | Belize | 4815.2
Hospital Name |  |  | Add a name |  | 0 | W1 | "W1: Wood, Light Frame (450 m2 or less)" | 0 |  | "Brick" | 0 | 1 | "1 floor" | 0 | 90% | "81 to 100%" | Dominica | 8110.6
Country |  |  | Dominica |  | 1 | W2 | "W2: Wood, Commercial and Industrial (more than 450 m2)" | 1 |  | "Concrete" | 1 | 2 | "2 floors" | 1 | 70% | "61 to 80%" | Grenada | 10808.7
Latitude |  |  | 15.4239 |  | 2 | S1 | "S1: Steel Moment Frame" | 2 |  | "Steel" | 2 | 3 | "3 floors" | 2 | 50% | "41 to 60%" | Guyana | 6609.6
Longitude |  |  | -60.6399 |  | 3 | S2 | "S2: Steel Braced Frame" | 3 |  | "Wood" | 3 | 4 | "4 floors" | 3 | 30% | "21 to 40%" | Jamaica | 5582.3
Patient consultations 1 year post-disaster |  |  | 6600 |  | 4 | S3 | "S3: Steel Light Frame" |  |  |  | 4 | 5 | "5 or more floors" | 4 | 10% | "1 to 20%" | Saint Lucia | 11611.4
Hospital admissions 1 year post-disaster |  |  | 0 |  | 5 | S4 | "S4: Steel Frame with Cast-in-Place Concrete Shear Walls" | [9 empty] | Saint Vincent and the Grenadines | 7457.5
Number of staff |  |  | 9 |  | 6 | S5 | "S5: Steel Frame with Unreinforced Masonry Infill Walls"
Catchment population |  |  | 3036 |  | 7 | C1 | "C1: Concrete Moment Frames" | [9 empty] | Source: Word Bank: https://data.worldbank.org/indicator/NY.GDP.PCAP.CD?locations=ZJ
GDP per capita |  |  | 8111 |  | 8 | C2 | "C2: Concrete Shear Walls"
[5 empty] | 9 | C3 | "C3: Concrete Frame with Unreinforced Masonry Infill Walls"
II) Safety parameters |  |  |  |  | 10 | C4 | "C4: Reinforced Concrete Frames and Concrete Shear Walls"
Construction Class of Hospital |  |  | C3 |  | 11 | C5 | "C5: Flat Slab Structure"
Construction Material of Hospital (best guess) |  |  | 0 |  | 12 | PC1 | "PC1: Precast Concrete Tilt-Up Walls"
Number of stories |  |  | 2 |  | 13 | PC2 | "PC2: Precast Concrete Frames with Concrete Shear Walls"
Gross floor area |  |  | 335 |  | 14 | SC1L | "SC1L: Reinforced Concrete Frames and Steel Truss Girder (Warehouses)"
Height to roof (m) |  |  | 3 |  | 15 | RM1 | "RM1: Reinforced Masonry Bearing Walls with Wood or Metal Deck Diaphragms"
Replacement value |  |  | 1000000 |  | 16 | RM2 | "RM2: Reinforced Masonry Bearing Walls with Precast Concrete Diaphragms"
Most common construction class in surrouding areas |  |  | 0.7 |  | 17 | URM | "URM: Unreinforced Masonry Bearing Walls"
1st Building construction class in surrouding areas |  |  | C1 |  | 18 | CM1 | "CM1: Confined Masonry Walls"
1st Average number of storeis in surrounding areas |  |  | 2 |  | 19 | AD1 | "AD1: Adobe"
1st Average height to roof (m) in surrounding areas |  |  | 6 |  | 20 | TA1 | "TA1: Tapia"
2nd most common construction class in surrouding areas |  |  | 0.1
2nd Building construction class in surrouding areas |  |  | C3
2nd Average number of storeis in surrounding areas |  |  | 2
2nd Average height to roof (m) in surrounding areas |  |  | 6
3rd most common construction class in surrouding areas |  |  | 0.1
3rd Building construction class in surrouding areas |  |  | W1
3rd Average number of storeis in surrounding areas |  |  | 2
3rd Average height to roof (m) in surrounding areas |  |  | 6
III) Energy parameters
IV)Flood parameters
Flood velocity |  | 2 | ft/sec
Flood depth |  | 5 | ft
1st Floor hight |  | 0.3 | m | 2.3
Flood channels |  | 3.5 | ft
V) Seismic Parameter
Latitude |  | 15.4239
Longitude |  | -60.6399
Soil type |  | Stiff soil
Design Code |  | 1.4
VI) Wind
Exposure |  | B
Window resistance baseline |  | 40 | psf
Window resistance retrofited |  | 100 | psf
Lenght of roof |  | 60.0339 | ft
Distance from roof supports |  | 9.84 | ft
Window Area |  | 1 | m2
Window Resistance |  | 0.1 | kg-m/s
Roof angle |  | 20 | degree
Hospital MDR
Buildings MDR
Note on C66: Samuel: B: Heavy Obstruction Wooded areas, urban and suburban C: Scatterd Obstruction flat open country, obstructions less than 30ft D: Unobstructed

## Step3 - HSI post-retrofitting (hidden)
Medium and Small Hospitals Safety Index
| Projected retrofitting work to improve safety Columns, beams, walls, slabs and other structural elements that form part of the support system of the building. These aspects to be evaluated by structural engineers and depends on their experienced judgement.2. Aspects relating to the Structural Safety Columns, beams, walls, slabs and other structural elements that form part of the support system of the building. These aspects to be evaluated by structural engineers and depends on their experienced judgement. |  |  |  | Pre | Post
| Components | Weight |  |  | Retrofitting |  | Change? | Pre-retrofitting value |  |  | Post-retrofitting value |  |  | Cost | Construction Class
|  | Earthquake | Cyclone | Injuries | Value | Value | 7 | Earthquake | Cyclone | Injuries | Earthquake | Cyclone | Injuries | 7 | Item# | Parameter | Description
1 | Substructural components | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | "0.00 (Low)"
2 | Superstructural components: Roof | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 36000 | 1 | 0.25 | "0.25"
3 | Superstructural components: Walls | 1 | 0.25 | 1 | 0.5 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 64800 | 2 | 0.5 | "0.50 (Average)"
4 | Superstructural components: Windows | 0.75 | 1 | 1 | 0.25 | 1 | 1 | 1.5 | 1.5 | 1.5 | 3 | 3 | 3 | 47000 | 3 | 0.75 | "0.75"
5 | Superstructural components: Floor | 0.25 | 0.25 | 0.5 | 0.5 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 18300 | 4 | 1 | "1.00 (High)"
6 | Superstructural components: Others | 0.25 | 0.25 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3500
7 | Structures that protect sources of electricity in emergency situations (e.g. generator room) | 1 | 1 | 0.75 | 0.5 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 34000
8 | Structures that protects water reserves in emergency situations (e.g. storage tank room) | 1 | 1 | 0.75 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 1700

## Step4 - Energy & Water (hidden)
Energy
Hospital Name | Add a name
Prices (P)
Electricity (kWh) | 0.47
Natural gas (lbs) | 0
Diesel (gallons) | 4
Oil (gallons) | 0
Post-retrofitting savings (Q)
Electricity (kWh) | 48895
Natural gas (lbs) | 0
Diesel (gallons) | 0
Oil (gallons) | 0
Total Savings (PxQ) | 22980.65
Total Investment (C) | 163900
Water
Hospital Name | Add a name
Price (P) | 0.05
Post-retrofitting saving (Q) | 86388
Total Savings (PxQ) | 4319.4
Total Investment (C) | 7400

## Hospital Outputs (hidden)
Earthquake |  |  |  | Retrofiting options
| Baseline | Retrofited |  | Design Code | 1.5
Building | 1.414% | 0.03882%
Wind |  |  |  | Retrofiting options
| Baseline | Retrofited | % damage
Massonry walls | 0.003167% | 0.003167% | 50% | Wall material | 0
Roof | 61.27% | 0.1156% | 25% | Window resistance | 140
Windows | 71.74% | 0% | 5%
| 18.91% | 0.03047% |  | Retrofiting options
Flood |  |  |  | Flood channels | 3.5
| Baseline | Retrofited
Building | 2.386% | N/A
Operationality | Not Operational | Not Operational
| 0 | 0
| 0 | 0 |  |  |  | 0
| 0 | 0
| 0 | 0 |  |  |  | 0 | 0.010319
| 0 | 0 |  |  |  |  | 0.00048063
| 0 | 0 |  |  |  | 0 | 1.5898e-05
5.5615e-08

## Houses Outputs (hidden)
Most common | 80% |  | Second most common | 10% | Third most common | 10%
Earthquake |  |  | Earthquake |  | Earthquake | [5 empty] | Death |  |  | Community
Damage | Baseline |  | Damage | Baseline | Damage | Baseline | Type of Damage | Severity 1 | Severity 2 | Severity 3 | Severity 4 | Days needed | <<Source: https://books.google.com/books?id=YBw4eGjML48C&pg=PA400&lpg=PA400&dq=mean+damage+ratio+and+type+of+damage+slight+moderate&source=bl&ots=ZSHRksEiKZ&sig=JQo1n3kAwtWj26A5uuauA3EtSIU&hl=en&sa=X&ved=0ahUKEwj5zffDwPrLAhXEmR4KHZR5BkUQ6AEIHDAA#v=onepage&q=mean%20damage%20ratio%20and%20type%20of%20damage%20slight%20moderate&f=false | Function name | Type of Damage
Slight | 9.742% |  | Slight | 15.36% | Slight | 28% | Slight | 0.05% | 0% | 0% | 0% | 0.35687 |  | All | S | Function name | Type of Damage
Moderate | 1.941% |  | Moderate | 1.988% | Moderate | 2.711% | Moderate | 0.25% | 0.03% | 0% | 0% | 0.041007 | << 10 weeks for severity 3, 5 weeks for severity 2, 1 day for severity 1 | Function name | Type of Damage | All | M
Extensive | 0.05012% |  | Extensive | 0.1212% | Extensive | 0.05836% | Extensive | 1% | 0.1% | 0.001% | 0.001% | 0.0069266 | Source time: Kates 2006 >>>http://www.vanderbilt.edu/vector/research/recoveryphase.pdf | All | E | Function name | Type of Damage
Complete | 0.0001386% |  | Complete | 0.001603% | Complete | 0.00778% | Complete | 5% | 1% | 0.1% | 0.1% |  |  |  |  | All | C
MDR | 0.754% |  | MDR | 0.9433% | MDR | 1.415% | People | 0.35687 | 0.020504 | 4.9476e-05 | 4.9476e-05
Wind |  |  | Wind |  | Wind
| Baseline | % damage |  | Baseline |  | Baseline | Type of Damage | Severity 1 | Severity 2
Massonry walls | 0.003167% | 50% | Massonry walls | 0.003167% | Massonry walls | 0.003167% | Extensive | 1% | 0.1%
Roof | 61.27% | 25% | Roof | 61.27% | Roof | 61.27% | Moderate | 0.25% | 0.03%
Windows | 71.74% | 5% | Windows | 71.74% | Windows | 71.74% | Slight | 0.05% | 0%
| 18.91% |  |  | 18.91% |  | 18.91% | People | 5.7403 | 0.55813
Flood |  |  | Flood |  | Flood
| Baseline |  |  | Baseline |  | Baseline
Building | 2.386% |  | Building | 2.386% | Building | 2.386%

## Injuries (hidden)
Source:
Hazard | Function name | Type of Damage | Severity 1 | Severity 2 | Severity 3 | Severity 4 | https://fiudit-my.sharepoint.com/personal/wechen_fiu_edu/Documents/PAHO%20project/Safety%20part/hazus_mr4_earthquake_tech_manual.pdf
| All | S | 0.05% | 0% | 0% | 0%
| All | M | 0.25% | 0.03% | 0% | 0% | Death rates for hurricanes
| All | E | 1% | 0.1% | 0.001% | 0.001% | http://wattsupwiththat.com/2011/08/27/hurricane-fatalities-1900%E2%80%932010-context-in-these-stormy-times/
| All | C | 5% | 1% | 0.1% | 0.1% | 52 per 100 million
5.2e-07
0.000104

## VF-ConstClass (hidden)
Table 5-1 Main Construction classes
No. | Function name | Description | Height |  |  |  | Height to Roof (m) | Period Te (Sec) | Seismic Design Level
|  |  | Range |  | Typical
|  |  | Name | Stories | Stories | Height (m) |  |  | H | M | L | P
1 | W1 | Wood, Light Frame (≤450 m2) | - | 1-2 | 1 | 4.3 | 4.3 | 0.35 | X | X | X | X
2 | W2 | Wood, Commercial and Industrial (>450 m2) | - | All | 2 | 7.3 | 7.3 | 0.4 | X | X | X | X
3 | S1L | Steel Moment Frame | Low-Rise | 1-3 | 2 | 7.3 | 7.3 | 0.5 | X | X | X | X
4 | S1M |  | Mid-Rise | 4-7 | 5 | 18.3 | 18.3 | 1.08 | X | X | X | X
5 | S1H |  | High-Rise | 8+ | 13 | 47.5 | 47.5 | 2.21 | X | X | X | X
6 | S2L | Steel Braced Frame | Low-Rise | 1-3 | 2 | 7.3 | 7.3 | 0.4 | X | X | X | X
7 | S2M |  | Mid-Rise | 4-7 | 5 | 18.3 | 18.3 | 0.86 | X | X | X | X
8 | S2H |  | High-Rise | 8+ | 13 | 47.5 | 47.5 | 1.77 | X | X | X | X
9 | S3 | Steel Light Frame | - | All | 1 | 4.6 | 4.6 | 0.4 | X | X | X | X
10 | S4L | Steel Frame with Cast‐in‐Place Concrete Shear Walls | Low-Rise | 1-3 | 2 | 7.3 | 7.3 | 0.35 | X | X | X | X
11 | S4M |  | Mid-Rise | 4-7 | 5 | 18.3 | 18.3 | 0.65 | X | X | X | X
12 | S4H |  | High-Rise | 8+ | 13 | 47.5 | 47.5 | 1.32 | X | X | X | X
13 | S5L | Steel Frame with Unreinforced Masonry Infill Walls | Low-Rise | 1-3 | 2 | 7.3 | 7.3 | 0.35 | X | X | X | X
14 | S5M |  | Mid-Rise | 4-7 | 5 | 18.3 | 18.3 | 0.65 | X | X | X | X
15 | S5H |  | High-Rise | 8+ | 13 | 47.5 | 47.5 | 1.32 | X | X | X | X
16 | C1L | Concrete Moment Frames | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.4 | X | X | X | X
17 | C1M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.75 | X | X | X | X
18 | C1H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.45 | X | X | X | X
19 | C2L | Concrete Shear Walls | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
20 | C2M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
21 | C2H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
22 | C3L | Concrete Frame with Unreinforced Masonry Infill Walls | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
23 | C3M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
24 | C3H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
39 | C4L | Reinforced Concrete Frames and Concrete Shear Walls | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
40 | C4M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
41 | C4H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
44 | C5L | Flat Slab Structure | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.4 | X | X | X | X
45 | C5M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.75 | X | X | X | X
46 | C5H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.45 | X | X | X | X
25 | PC1L | Precast Concrete Tilt‐Up Walls | Low-Rise | 1-3 | 1 | 4.6 | 4.6 | 0.35 | X | X | X | X
42 | PC1M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
43 | PC1H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
26 | PC2L | Precast Concrete Frames with Concrete Shear Walls | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
27 | PC2M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
28 | PC2H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
47 | SC1L | Reinforced Concrete Frames and Steel Truss Girder (Warehouses) | - | All | 1 | 4.6 | 4.6 | 0.32 | X | X | X | X
29 | RM1L | Reinforced Masonry Bearing Walls with Wood or Metal Deck Diaphragms | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
30 | RM1M |  | Mid-Rise | 4+ | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
31 | RM2L | Reinforced Masonry Bearing Walls with Precast Concrete Diaphragms | Low-Rise | 1-3 | 2 | 6.1 | 6.1 | 0.35 | X | X | X | X
32 | RM2M |  | Mid-Rise | 4-7 | 5 | 15.2 | 15.2 | 0.56 | X | X | X | X
33 | RM2H |  | High-Rise | 8+ | 12 | 36.6 | 36.6 | 1.09 | X | X | X | X
34 | URML | Unreinforced Masonry Bearing Walls | Low-Rise | 1-2 | 1 | 4.6 | 4.6 | 0.35 | - | X | X | X
35 | URMM |  | Mid-Rise | 3+ | 3 | 10.7 | 10.7 | 0.5 | - | X | X | X
38 | CM1L | Confined Masonry Walls | Low-Rise | 1-3 | 3 | 9.1 | 9.1 | 0.4 | - | X | X | X
36 | AD1L | Adobe | Low-Rise | 1-2 | 2 | 6.1 | 6.1 | 0.5 | - | X | X | X
37 | TA1L | Tapia | Low-Rise | 1-2 | 2 | 6.1 | 6.1 | 0.5 | - | X | X | X

## VF-ConstClassParam (hidden)
From page 257-303 | [16 empty] | Page 308-354
Function name | Quality Level | H(m) | Np | Te(sec) | alpha_1 | alpha_2 | Gamma | Lambda | Cs | Mu | Alpha | a | Beta_1 | Beta_2 | Beta_3 | Beta_4 | Y(mph) | Rho_1 | Rho_2
W1 | H | 4.27 | 1 | 0.35 | 0.75 | 0.75 | 1.5 | 3 | 0.2 | 8 | 10 | 0.1 | 1 | 1.48 | 1.7 | 1.27 | 170 | 9 | 8
W1 | M | 4.27 | 1 | 0.35 | 0.75 | 0.75 | 1.5 | 3 | 0.15 | 6 | 10 | 0.1 | 1 | 1.48 | 1.4 | 1.21 | 153 | 9 | 8
W1 | L | 4.27 | 1 | 0.35 | 0.75 | 0.75 | 1.5 | 3 | 0.1 | 6 | 10 | 0.1 | 1 | 1.48 | 1.4 | 1.21 | 136 | 9 | 8
W1 | P | 4.27 | 1 | 0.35 | 0.75 | 0.75 | 1.5 | 3 | 0.05 | 3 | 10 | 0.1 | 1 | 1.48 | 1.1 | 1.11 | 119 | 9 | 8
W2 | H | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2.5 | 0.2 | 8 | 5 | 0.1 | 1.2 | 1.36 | 1.5 | 1.28 | 170 | 9 | 8
W2 | M | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2.5 | 0.1 | 6 | 5 | 0.1 | 1.2 | 1.36 | 1.4 | 1.21 | 153 | 9 | 8
W2 | L | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2.5 | 0.05 | 6 | 5 | 0.1 | 1.2 | 1.36 | 1.4 | 1.21 | 136 | 9 | 8
W2 | P | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2.5 | 0.04 | 4.8 | 5 | 0.1 | 1.2 | 1.36 | 1.3 | 1.17 | 119 | 9 | 8
S1L | H | 7.32 | 2 | 0.5 | 0.8 | 0.75 | 1.5 | 3 | 0.133 | 8 | 2.5 | 0.1 | 1.2 | 1.24 | 1.2 | 1.28 | 220 | 10 | 8
S1L | M | 7.32 | 2 | 0.5 | 0.8 | 0.75 | 1.5 | 3 | 0.067 | 6 | 2.5 | 0.1 | 1.2 | 1.24 | 1.2 | 1.21 | 198 | 10 | 8
S1L | L | 7.32 | 2 | 0.5 | 0.8 | 0.75 | 1.5 | 3 | 0.033 | 5 | 2.5 | 0.1 | 1.2 | 1.24 | 1.2 | 1.18 | 176 | 10 | 8
S1L | P | 7.32 | 2 | 0.5 | 0.8 | 0.75 | 1.5 | 3 | 0.026 | 4 | 2.5 | 0.1 | 1.2 | 1.24 | 1.2 | 1.14 | 154 | 10 | 8
S1M | H | 18.29 | 5 | 1.08 | 0.8 | 0.75 | 1.25 | 3 | 0.1 | 5.3 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.2 | 220 | 10 | 8
S1M | M | 18.29 | 5 | 1.08 | 0.8 | 0.75 | 1.25 | 3 | 0.05 | 4 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.16 | 198 | 10 | 8
S1M | L | 18.29 | 5 | 1.08 | 0.8 | 0.75 | 1.25 | 3 | 0.025 | 3.3 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.14 | 176 | 10 | 8
S1M | P | 18.29 | 5 | 1.08 | 0.8 | 0.75 | 1.25 | 3 | 0.02 | 2.6 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.11 | 154 | 10 | 8
S1H | H | 47.55 | 13 | 2.21 | 0.75 | 0.6 | 1.1 | 3 | 0.067 | 4 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.2 | 220 | 10 | 8
S1H | M | 47.55 | 13 | 2.21 | 0.75 | 0.6 | 1.1 | 3 | 0.033 | 3 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.17 | 198 | 10 | 8
S1H | L | 47.55 | 13 | 2.21 | 0.75 | 0.6 | 1.1 | 3 | 0.017 | 2.5 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.15 | 176 | 10 | 8
S1H | P | 47.55 | 13 | 2.21 | 0.75 | 0.6 | 1.1 | 3 | 0.014 | 2 | 2.5 | 0.1 | 1.4 | 1.24 | 1 | 1.13 | 154 | 10 | 8
S2L | H | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.2 | 8 | 6 | 0.1 | 1.2 | 1.4 | 1.5 | 1.28 | 220 | 10 | 8
S2L | M | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.1 | 6 | 6 | 0.1 | 1.2 | 1.4 | 1.4 | 1.21 | 198 | 10 | 8
S2L | L | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.05 | 5 | 6 | 0.1 | 1.2 | 1.4 | 1.3 | 1.18 | 176 | 10 | 8
S2L | P | 7.32 | 2 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.04 | 4 | 6 | 0.1 | 1.2 | 1.4 | 1.2 | 1.14 | 154 | 10 | 8
S2M | H | 18.29 | 5 | 0.86 | 0.75 | 0.75 | 1.25 | 2 | 0.2 | 5.3 | 6 | 0.1 | 1.3 | 1.4 | 1.1 | 1.2 | 220 | 10 | 8
S2M | M | 18.29 | 5 | 0.86 | 0.75 | 0.75 | 1.25 | 2 | 0.1 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.16 | 198 | 10 | 8
S2M | L | 18.29 | 5 | 0.86 | 0.75 | 0.75 | 1.25 | 2 | 0.05 | 3.3 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.14 | 176 | 10 | 8
S2M | P | 18.29 | 5 | 0.86 | 0.75 | 0.75 | 1.25 | 2 | 0.04 | 2.6 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.11 | 154 | 10 | 8
S2H | H | 47.55 | 13 | 1.77 | 0.65 | 0.6 | 1.1 | 2 | 0.15 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.2 | 220 | 10 | 8
S2H | M | 47.55 | 13 | 1.77 | 0.65 | 0.6 | 1.1 | 2 | 0.075 | 3 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.17 | 198 | 10 | 8
S2H | L | 47.55 | 13 | 1.77 | 0.65 | 0.6 | 1.1 | 2 | 0.038 | 2.5 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.15 | 176 | 10 | 8
S2H | P | 47.55 | 13 | 1.77 | 0.65 | 0.6 | 1.1 | 2 | 0.03 | 2 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.13 | 154 | 10 | 8
S3 | H | 4.57 | 1 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.2 | 8 | 1 | 0.1 | 1 | 1.3 | 1.5 | 1.27 | 156 | 10 | 8
S3 | M | 4.57 | 1 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.1 | 6 | 1 | 0.1 | 1 | 1.3 | 1.4 | 1.21 | 140.4 | 10 | 8
S3 | L | 4.57 | 1 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.05 | 5 | 1 | 0.1 | 1 | 1.3 | 1.3 | 1.17 | 124.8 | 10 | 8
S3 | P | 4.57 | 1 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.04 | 4 | 1 | 0.1 | 1 | 1.3 | 1.2 | 1.14 | 109.2 | 10 | 8
S4L | H | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 1.5 | 0.16 | 8 | 12 | 0.1 | 1.2 | 1.5 | 1.7 | 1.28 | 220 | 10 | 8
S4L | M | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 1.5 | 0.08 | 6 | 12 | 0.1 | 1.2 | 1.5 | 1.4 | 1.21 | 198 | 10 | 8
S4L | L | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 1.5 | 0.04 | 5 | 12 | 0.1 | 1.2 | 1.5 | 1.3 | 1.18 | 176 | 10 | 8
S4L | P | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 1.5 | 0.032 | 4 | 12 | 0.1 | 1.2 | 1.5 | 1.2 | 1.14 | 154 | 10 | 8
S4M | H | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2.5 | 0.16 | 5.3 | 12 | 0.1 | 1.2 | 1.5 | 1.1 | 1.2 | 220 | 10 | 8
S4M | M | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2.5 | 0.08 | 4 | 12 | 0.1 | 1.2 | 1.5 | 1.1 | 1.16 | 198 | 10 | 8
S4M | L | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2.5 | 0.04 | 3.3 | 12 | 0.1 | 1.2 | 1.5 | 1 | 1.14 | 176 | 10 | 8
S4M | P | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2.5 | 0.032 | 2.6 | 12 | 0.1 | 1.2 | 1.5 | 1 | 1.11 | 154 | 10 | 8
S4H | H | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2.5 | 0.12 | 4 | 12 | 0.1 | 1.3 | 1.5 | 1 | 1.2 | 220 | 10 | 8
S4H | M | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2.5 | 0.06 | 3 | 12 | 0.1 | 1.3 | 1.5 | 1 | 1.17 | 198 | 10 | 8
S4H | L | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2.5 | 0.03 | 2.5 | 12 | 0.1 | 1.3 | 1.5 | 1 | 1.15 | 176 | 10 | 8
S4H | P | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2.5 | 0.024 | 2 | 12 | 0.1 | 1.3 | 1.5 | 1 | 1.13 | 154 | 10 | 8
S5L | H | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.147 | 8 | 6 | 0.1 | 1.2 | 1.4 | 1.7 | 1.28 | 220 | 10 | 8
S5L | M | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.074 | 6 | 6 | 0.1 | 1.2 | 1.4 | 1.4 | 1.21 | 198 | 10 | 8
S5L | L | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.05 | 5 | 6 | 0.1 | 1.2 | 1.4 | 1.3 | 1.18 | 176 | 10 | 8
S5L | P | 7.32 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.04 | 4 | 6 | 0.1 | 1.2 | 1.4 | 1.2 | 1.14 | 154 | 10 | 8
S5M | H | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2 | 0.13 | 5.3 | 6 | 0.1 | 1.3 | 1.4 | 1.1 | 1.2 | 220 | 10 | 8
S5M | M | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2 | 0.065 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1.1 | 1.16 | 198 | 10 | 8
S5M | L | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2 | 0.05 | 3.3 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.14 | 176 | 10 | 8
S5M | P | 18.29 | 5 | 0.65 | 0.75 | 0.75 | 1.25 | 2 | 0.04 | 2.6 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.11 | 154 | 10 | 8
S5H | H | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2 | 0.094 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.2 | 220 | 10 | 8
S5H | M | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2 | 0.047 | 3 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.17 | 198 | 10 | 8
S5H | L | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2 | 0.038 | 2.5 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.15 | 176 | 10 | 8
S5H | P | 47.55 | 13 | 1.32 | 0.65 | 0.6 | 1.1 | 2 | 0.03 | 2 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.13 | 154 | 10 | 8
C1L | H | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 3 | 0.133 | 8 | 3 | 0.1 | 1.2 | 1.26 | 1.5 | 1.28 | 220 | 10 | 8
C1L | M | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 3 | 0.067 | 6 | 3 | 0.1 | 1.2 | 1.26 | 1.4 | 1.21 | 198 | 10 | 8
C1L | L | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 3 | 0.033 | 5 | 3 | 0.1 | 1.2 | 1.26 | 1.3 | 1.18 | 176 | 10 | 8
C1L | P | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 3 | 0.026 | 4 | 3 | 0.1 | 1.2 | 1.26 | 1.2 | 1.14 | 154 | 10 | 8
C1M | H | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 3 | 0.13 | 5.3 | 3 | 0.1 | 1.3 | 1.26 | 1.1 | 1.2 | 220 | 10 | 8
C1M | M | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 3 | 0.067 | 4 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.16 | 198 | 10 | 8
C1M | L | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 3 | 0.033 | 3.3 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.14 | 176 | 10 | 8
C1M | P | 15.24 | 5 | 0.65 | 0.8 | 0.75 | 1.25 | 3 | 0.026 | 2.6 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.11 | 154 | 10 | 8
C1H | H | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 3 | 0.067 | 4 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.19 | 220 | 10 | 8
C1H | M | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 3 | 0.033 | 3 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.16 | 198 | 10 | 8
C1H | L | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 3 | 0.017 | 2.5 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.14 | 176 | 10 | 8
C1H | P | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 3 | 0.014 | 2 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.13 | 154 | 10 | 8
C2L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.2 | 8 | 15 | 0.1 | 1.2 | 1.51 | 1.7 | 1.28 | 220 | 10 | 8
C2L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.1 | 6 | 15 | 0.1 | 1.2 | 1.51 | 1.4 | 1.21 | 198 | 10 | 8
C2L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.05 | 5 | 15 | 0.1 | 1.2 | 1.51 | 1.3 | 1.18 | 176 | 10 | 8
C2L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.04 | 4 | 15 | 0.1 | 1.2 | 1.51 | 1.2 | 1.14 | 154 | 10 | 8
C2M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.2 | 5.3 | 15 | 0.1 | 1.2 | 1.51 | 1.2 | 1.2 | 220 | 10 | 8
C2M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.1 | 4 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.16 | 198 | 10 | 8
C2M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.05 | 3.3 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.14 | 176 | 10 | 8
C2M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.04 | 2.6 | 15 | 0.1 | 1.2 | 1.51 | 1 | 1.11 | 154 | 10 | 8
C2H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.5 | 0.15 | 4 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.19 | 220 | 10 | 8
C2H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.5 | 0.075 | 3 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.16 | 198 | 10 | 8
C2H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.5 | 0.038 | 2.5 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.14 | 176 | 10 | 8
C2H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.5 | 0.03 | 2 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.13 | 154 | 10 | 8
C3L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.167 | 8 | 6 | 0.1 | 1.2 | 1.4 | 1.7 | 1.28 | 220 | 10 | 8
C3L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.084 | 6 | 6 | 0.1 | 1.2 | 1.4 | 1.4 | 1.21 | 198 | 10 | 8
C3L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.05 | 5 | 6 | 0.1 | 1.2 | 1.4 | 1.3 | 1.18 | 176 | 10 | 8
C3L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2.5 | 0.04 | 4 | 6 | 0.1 | 1.2 | 1.4 | 1.2 | 1.14 | 154 | 10 | 8
C3M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.167 | 5.3 | 6 | 0.1 | 1.3 | 1.4 | 1.2 | 1.2 | 220 | 10 | 8
C3M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.084 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1.1 | 1.16 | 198 | 10 | 8
C3M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.05 | 3.3 | 6 | 0.1 | 1.3 | 1.4 | 1.1 | 1.14 | 176 | 10 | 8
C3M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2.25 | 0.04 | 2.6 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.11 | 154 | 10 | 8
C3H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.25 | 0.109 | 4 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.19 | 220 | 10 | 8
C3H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.25 | 0.054 | 3 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.16 | 198 | 10 | 8
C3H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.25 | 0.038 | 2.5 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.14 | 176 | 10 | 8
C3H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2.25 | 0.03 | 2 | 6 | 0.1 | 1.3 | 1.4 | 1 | 1.13 | 154 | 10 | 8
C4L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.2 | 8 | 8 | 0.1 | 1.2 | 1.46 | 1.7 | 1.28 | 220 | 10 | 8
C4L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.1 | 6 | 8 | 0.1 | 1.2 | 1.46 | 1.4 | 1.21 | 198 | 10 | 8
C4L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.05 | 5 | 8 | 0.1 | 1.2 | 1.46 | 1.3 | 1.18 | 176 | 10 | 8
C4L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.04 | 4 | 8 | 0.1 | 1.2 | 1.46 | 1.2 | 1.14 | 154 | 10 | 8
C4M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.2 | 5.3 | 8 | 0.1 | 1.3 | 1.46 | 1.2 | 1.2 | 220 | 10 | 8
C4M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.1 | 4 | 8 | 0.1 | 1.3 | 1.46 | 1.1 | 1.16 | 198 | 10 | 8
C4M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.05 | 3.3 | 8 | 0.1 | 1.3 | 1.46 | 1.1 | 1.14 | 176 | 10 | 8
C4M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.04 | 2.6 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.11 | 154 | 10 | 8
C4H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.15 | 4 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.19 | 220 | 10 | 8
C4H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.075 | 3 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.16 | 198 | 10 | 8
C4H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.038 | 2.5 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.14 | 176 | 10 | 8
C4H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.03 | 2 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.13 | 154 | 10 | 8
C5L | H | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 2.7 | 0.133 | 8 | 3 | 0.1 | 1.2 | 1.26 | 1.5 | 1.28 | 220 | 10 | 8
C5L | M | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 2.7 | 0.067 | 6 | 3 | 0.1 | 1.2 | 1.26 | 1.4 | 1.21 | 198 | 10 | 8
C5L | L | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 2.7 | 0.033 | 5 | 3 | 0.1 | 1.2 | 1.26 | 1.3 | 1.18 | 176 | 10 | 8
C5L | P | 6.1 | 2 | 0.4 | 0.8 | 0.75 | 1.5 | 2.7 | 0.026 | 4 | 3 | 0.1 | 1.2 | 1.26 | 1.2 | 1.14 | 154 | 10 | 8
C5M | H | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 2.7 | 0.133 | 5.3 | 3 | 0.1 | 1.3 | 1.26 | 1.1 | 1.2 | 220 | 10 | 8
C5M | M | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 2.7 | 0.067 | 4 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.16 | 198 | 10 | 8
C5M | L | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 2.7 | 0.033 | 3.3 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.14 | 176 | 10 | 8
C5M | P | 15.24 | 5 | 0.75 | 0.8 | 0.75 | 1.25 | 2.7 | 0.026 | 2.6 | 3 | 0.1 | 1.3 | 1.26 | 1 | 1.11 | 154 | 10 | 8
C5H | H | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 2.7 | 0.067 | 4 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.19 | 220 | 10 | 8
C5H | M | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 2.7 | 0.033 | 3 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.16 | 198 | 10 | 8
C5H | L | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 2.7 | 0.017 | 2.5 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.14 | 176 | 10 | 8
C5H | P | 36.58 | 12 | 1.45 | 0.75 | 0.6 | 1.1 | 2.7 | 0.014 | 2 | 3 | 0.1 | 1.4 | 1.26 | 1 | 1.13 | 154 | 10 | 8
PC1L | H | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.2 | 8 | 10 | 0.1 | 1 | 1.48 | 1.7 | 1.27 | 220 | 10 | 8
PC1L | M | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.1 | 6 | 10 | 0.1 | 1 | 1.48 | 1.4 | 1.21 | 198 | 10 | 8
PC1L | L | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.05 | 5 | 10 | 0.1 | 1 | 1.48 | 1.3 | 1.17 | 176 | 10 | 8
PC1L | P | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.04 | 4 | 10 | 0.1 | 1 | 1.48 | 1.2 | 1.14 | 154 | 10 | 8
PC1M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.2 | 5.3 | 10 | 0.1 | 1.3 | 1.48 | 1.2 | 1.2 | 220 | 10 | 8
PC1M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.1 | 4 | 10 | 0.1 | 1.3 | 1.48 | 1.1 | 1.16 | 198 | 10 | 8
PC1M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.05 | 3.3 | 10 | 0.1 | 1.3 | 1.48 | 1.1 | 1.14 | 176 | 10 | 8
PC1M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.04 | 2.6 | 10 | 0.1 | 1.3 | 1.48 | 1 | 1.11 | 154 | 10 | 8
PC1H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.15 | 4 | 10 | 0.1 | 1.3 | 1.48 | 1 | 1.19 | 220 | 10 | 8
PC1H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.075 | 3 | 10 | 0.1 | 1.3 | 1.48 | 1 | 1.16 | 198 | 10 | 8
PC1H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.038 | 2.5 | 10 | 0.1 | 1.3 | 1.48 | 1 | 1.14 | 176 | 10 | 8
PC1H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.03 | 2 | 10 | 0.1 | 1.3 | 1.48 | 1 | 1.13 | 154 | 10 | 8
PC2L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.2 | 8 | 8 | 0.1 | 1.2 | 1.46 | 1.7 | 1.28 | 220 | 10 | 8
PC2L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.1 | 6 | 8 | 0.1 | 1.2 | 1.46 | 1.4 | 1.21 | 198 | 10 | 8
PC2L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.05 | 5 | 8 | 0.1 | 1.2 | 1.46 | 1.3 | 1.18 | 176 | 10 | 8
PC2L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.04 | 4 | 8 | 0.1 | 1.2 | 1.46 | 1.2 | 1.14 | 154 | 10 | 8
PC2M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.2 | 5.3 | 8 | 0.1 | 1.3 | 1.46 | 1.2 | 1.2 | 220 | 10 | 8
PC2M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.1 | 4 | 8 | 0.1 | 1.3 | 1.46 | 1.1 | 1.16 | 198 | 10 | 8
PC2M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.05 | 3.3 | 8 | 0.1 | 1.3 | 1.46 | 1.1 | 1.14 | 176 | 10 | 8
PC2M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.04 | 2.6 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.11 | 154 | 10 | 8
PC2H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.15 | 4 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.19 | 220 | 10 | 8
PC2H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.075 | 3 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.16 | 198 | 10 | 8
PC2H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.038 | 2.5 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.14 | 176 | 10 | 8
PC2H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.03 | 2 | 8 | 0.1 | 1.3 | 1.46 | 1 | 1.13 | 154 | 10 | 8
SC1L | H | 4.57 | 1 | 0.32 | 0.75 | 0.75 | 1.5 | 2 | 0.24 | 8 | 1 | 0.1 | 1 | 1.3 | 1.7 | 1.27 | 156 | 10 | 8
SC1L | M | 4.57 | 1 | 0.32 | 0.75 | 0.75 | 1.5 | 2 | 0.12 | 6 | 1 | 0.1 | 1 | 1.3 | 1.5 | 1.21 | 140.4 | 10 | 8
SC1L | L | 4.57 | 1 | 0.32 | 0.75 | 0.75 | 1.5 | 2 | 0.06 | 5 | 1 | 0.1 | 1 | 1.3 | 1.4 | 1.17 | 124.8 | 10 | 8
SC1L | P | 4.57 | 1 | 0.32 | 0.75 | 0.75 | 1.5 | 2 | 0.048 | 4 | 1 | 0.1 | 1 | 1.3 | 1.3 | 1.14 | 109.2 | 10 | 8
RM1L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.267 | 8 | 15 | 0.1 | 1.2 | 1.51 | 1.7 | 1.28 | 200 | 10 | 8
RM1L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.133 | 6 | 15 | 0.1 | 1.2 | 1.51 | 1.4 | 1.21 | 180 | 10 | 8
RM1L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.067 | 5 | 15 | 0.1 | 1.2 | 1.51 | 1.3 | 1.18 | 160 | 10 | 8
RM1L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.054 | 4 | 15 | 0.1 | 1.2 | 1.51 | 1.2 | 1.14 | 140 | 10 | 8
RM1M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.267 | 5.3 | 15 | 0.1 | 1.2 | 1.51 | 1.2 | 1.2 | 200 | 10 | 8
RM1M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.133 | 4 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.16 | 180 | 10 | 8
RM1M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.067 | 3.3 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.14 | 160 | 10 | 8
RM1M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.054 | 2.6 | 15 | 0.1 | 1.2 | 1.51 | 1 | 1.11 | 140 | 10 | 8
RM2L | H | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.267 | 8 | 8 | 0.1 | 1.2 | 1.51 | 1.7 | 1.28 | 200 | 10 | 8
RM2L | M | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.133 | 6 | 8 | 0.1 | 1.2 | 1.51 | 1.4 | 1.21 | 180 | 10 | 8
RM2L | L | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.067 | 5 | 8 | 0.1 | 1.2 | 1.51 | 1.3 | 1.18 | 160 | 10 | 8
RM2L | P | 6.1 | 2 | 0.35 | 0.75 | 0.75 | 1.5 | 2 | 0.054 | 4 | 8 | 0.1 | 1.2 | 1.51 | 1.2 | 1.14 | 140 | 10 | 8
RM2M | H | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.267 | 5.3 | 15 | 0.1 | 1.2 | 1.51 | 1.2 | 1.2 | 200 | 10 | 8
RM2M | M | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.133 | 4 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.16 | 180 | 10 | 8
RM2M | L | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.067 | 3.3 | 15 | 0.1 | 1.2 | 1.51 | 1.1 | 1.14 | 160 | 10 | 8
RM2M | P | 15.24 | 5 | 0.56 | 0.75 | 0.75 | 1.25 | 2 | 0.054 | 2.6 | 15 | 0.1 | 1.2 | 1.51 | 1 | 1.11 | 140 | 10 | 8
RM2H | H | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.2 | 4 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.19 | 200 | 10 | 8
RM2H | M | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.1 | 3 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.16 | 180 | 10 | 8
RM2H | L | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.05 | 2.5 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.14 | 160 | 10 | 8
RM2H | P | 36.58 | 12 | 1.09 | 0.65 | 0.6 | 1.1 | 2 | 0.04 | 2 | 15 | 0.1 | 1.3 | 1.51 | 1 | 1.13 | 140 | 10 | 8
URML | H | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.11 | 8 | 1 | 0.1 | 1 | 1.3 | 1.7 | 1.27 | 192 | 10 | 8
URML | M | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.08 | 6 | 1 | 0.1 | 1 | 1.3 | 1.4 | 1.21 | 172.8 | 10 | 8
URML | L | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.067 | 5 | 1 | 0.1 | 1 | 1.3 | 1.3 | 1.17 | 153.6 | 10 | 8
URML | P | 4.57 | 1 | 0.35 | 0.5 | 0.75 | 1.5 | 2 | 0.054 | 4 | 1 | 0.1 | 1 | 1.3 | 1.2 | 1.14 | 134.4 | 10 | 8
URMM | H | 10.67 | 3 | 0.5 | 0.75 | 0.75 | 1.25 | 2 | 0.08 | 5.3 | 1 | 0.1 | 1.3 | 1.3 | 1.2 | 1.19 | 192 | 10 | 8
URMM | M | 10.67 | 3 | 0.5 | 0.75 | 0.75 | 1.25 | 2 | 0.08 | 4 | 1 | 0.1 | 1.3 | 1.3 | 1.1 | 1.15 | 172.8 | 10 | 8
URMM | L | 10.67 | 3 | 0.5 | 0.75 | 0.75 | 1.25 | 2 | 0.067 | 3.3 | 1 | 0.1 | 1.3 | 1.3 | 1.1 | 1.13 | 153.6 | 10 | 8
URMM | P | 10.67 | 3 | 0.5 | 0.75 | 0.75 | 1.25 | 2 | 0.054 | 2.6 | 1 | 0.1 | 1.3 | 1.3 | 1 | 1.1 | 134.4 | 10 | 8
CM1L | H | 9.14 | 3 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.267 | 8 | 1 | 0.1 | 1.3 | 1.3 | 1.5 | 1.28 | 200 | 10 | 8
CM1L | M | 9.14 | 3 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.133 | 6 | 1 | 0.1 | 1.3 | 1.3 | 1.4 | 1.22 | 180 | 10 | 8
CM1L | L | 9.14 | 3 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.067 | 5 | 1 | 0.1 | 1.3 | 1.3 | 1.3 | 1.18 | 160 | 10 | 8
CM1L | P | 9.14 | 3 | 0.4 | 0.75 | 0.75 | 1.5 | 2 | 0.054 | 4 | 1 | 0.1 | 1.3 | 1.3 | 1.2 | 1.15 | 140 | 10 | 8
AD1L | H | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.06 | 5.3 | 1 | 0.1 | 1.2 | 1.3 | 1.2 | 1.19 | 192 | 10 | 8
AD1L | M | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.06 | 4 | 1 | 0.1 | 1.2 | 1.3 | 1.1 | 1.14 | 172.8 | 10 | 8
AD1L | L | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.05 | 3.3 | 1 | 0.1 | 1.2 | 1.3 | 1.1 | 1.12 | 153.6 | 10 | 8
AD1L | P | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.04 | 2.6 | 1 | 0.1 | 1.2 | 1.3 | 1 | 1.1 | 134.4 | 10 | 8
TA1L | H | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.06 | 5.3 | 1 | 0.1 | 1.2 | 1.3 | 1.2 | 1.19 | 192 | 10 | 8
TA1L | M | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.06 | 4 | 1 | 0.1 | 1.2 | 1.3 | 1.1 | 1.14 | 172.8 | 10 | 8
TA1L | L | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.05 | 3.3 | 1 | 0.1 | 1.2 | 1.3 | 1.1 | 1.12 | 153.6 | 10 | 8
TA1L | P | 6.1 | 2 | 0.5 | 0.5 | 0.75 | 1.5 | 1.5 | 0.04 | 2.6 | 1 | 0.1 | 1.2 | 1.3 | 1 | 1.1 | 134.4 | 10 | 8
Note on L159: Original=15
Note on J171: Original is 0.080. Changed to 0.08+0.013=0.093

## Response Spectra (hidden)
N° DATA | LAT. | LONG. | 0.2 SEC | 0.5 SEC | 1.0 SEC
217413 | 15.4239 | -60.6399 | 0.1 | 0.1 | 0.1
15.5-60.5 | 15.5 | -60.5
Central and Eastern United States (CEUS) – Rock (Site Class B)
Distance (km) | Sas/PGA given Magnitude, M: |  |  |  | SAs/SAl given Magnitude, M:
| 5 | 6 | 7 | 7.5 | 5 | 6 | 7 | 7.5
10 | 0.8 | 1.1 | 1.4 | 1.7 | 7.7 | 4.2 | 3 | 2.7
25 | 0.9 | 1.2 | 1.4 | 1.5 | 6.9 | 4 | 2.9 | 2.6
50 | 1 | 1.4 | 1.6 | 1.7 | 5.2 | 3.8 | 2.7 | 2.4
75 | 1.2 | 1.5 | 1.7 | 1.8 | 9.2 | 3.5 | 2.6 | 2.4
Dis (km) | SAs 0.2 sec |  |  |  | SAl 0.2 sec
10 | 0.08 | 0.11 | 0.14 | 0.17 | 0.01039 | 0.02619 | 0.046667 | 0.062963
25 | 0.09 | 0.12 | 0.14 | 0.15 | 0.013043 | 0.03 | 0.048276 | 0.057692
50 | 0.1 | 0.14 | 0.16 | 0.17 | 0.019231 | 0.036842 | 0.059259 | 0.070833
75 | 0.12 | 0.15 | 0.17 | 0.18 | 0.013043 | 0.042857 | 0.065385 | 0.075
Dis (km) | SAs 0.5 sec |  |  |  | SAl 0.5 sec
10 | 0.08 | 0.11 | 0.14 | 0.17 | 0.01039 | 0.02619 | 0.046667 | 0.062963
25 | 0.09 | 0.12 | 0.14 | 0.15 | 0.013043 | 0.03 | 0.048276 | 0.057692
50 | 0.1 | 0.14 | 0.16 | 0.17 | 0.019231 | 0.036842 | 0.059259 | 0.070833
75 | 0.12 | 0.15 | 0.17 | 0.18 | 0.013043 | 0.042857 | 0.065385 | 0.075
Dis (km) | SAs 1.0 sec |  |  |  | SAl 1.0 sec
10 | 0.08 | 0.11 | 0.14 | 0.17 | 0.01039 | 0.02619 | 0.046667 | 0.062963
25 | 0.09 | 0.12 | 0.14 | 0.15 | 0.013043 | 0.03 | 0.048276 | 0.057692
50 | 0.1 | 0.14 | 0.16 | 0.17 | 0.019231 | 0.036842 | 0.059259 | 0.070833
75 | 0.12 | 0.15 | 0.17 | 0.18 | 0.013043 | 0.042857 | 0.065385 | 0.075
Dis (km) | T (sec) | Sas (g) | Sal (g)
75 | 0.2 | 0.15 | 0.042857
Magnitude | 0.5 | 0.15 | 0.042857
6 | 1 | 0.15 | 0.042857
SD | 9.8*SA*T^2
T (sec) | Sd (inch) | Sa (g) | ROCK
0 | 0 | 0.15
0.2 | 0.0588 | 0.15
0.5 | 0.105 | 0.042857
1 | 0.42 | 0.042857
| Sd (inch) | Sal (g) | STIFF SOIL
0 | 0 | 0.24 |  | Fa= | 1.6
0.2 | 0.09408 | 0.24
0.5 | 0.252 | 0.10286 |  | Fv= | 2.4
1 | 1.008 | 0.10286 |  |  | 2.4
| Sd (inch) | Sal (g) | SOFT SOIL
0 | 0 | 0.375 |  | Fa= | 2.5
0.2 | 0.147 | 0.375
0.5 | 0.3675 | 0.15 |  | Fv= | 3.5
1 | 1.47 | 0.15 |  |  | 3.5
ROCK |  |  |  |  | STIFF SOIL |  |  |  |  | SOFT SOIL
T | Sd | Sa | Factor |  | T | Sd | Sa | Factor |  | T | Sd | Sa | Factor
0 | 0 | 0.15 | 1.0065e-06 |  | 0 | 0 | 0.24 | 5.3886e-07 |  | 0 | 0 | 0.375 | 3.4221e-07
0.2 | 0.0588 | 0.15 | 7.1923 |  | 0.2 | 0.09408 | 0.24 | 7.7338 | 4.1667 | 0.2 | 0.147 | 0.375 | 8.3235 | 2.6667
0.23 | 0.042546 | 0.082068 | 0.042856 |  | 0.23 | 0.077446 | 0.14939 | 0.10286 |  | 0.23 | 0.11421 | 0.2203 | 0.15
0.26 | 0.039147 | 0.059091 |  |  | 0.26 | 0.080084 | 0.12089 |  |  | 0.26 | 0.11616 | 0.17534
0.29 | 0.041422 | 0.050258 |  |  | 0.29 | 0.091158 | 0.1106 |  |  | 0.29 | 0.13204 | 0.16021
0.32 | 0.046666 | 0.046503 |  |  | 0.32 | 0.10685 | 0.10648 |  |  | 0.32 | 0.15504 | 0.1545
0.35 | 0.053747 | 0.04477 |  |  | 0.35 | 0.12565 | 0.10467 |  |  | 0.35 | 0.18264 | 0.15213
0.38 | 0.062146 | 0.043916 |  |  | 0.38 | 0.14691 | 0.10381 |  |  | 0.38 | 0.21379 | 0.15108
0.41 | 0.071611 | 0.04347 |  |  | 0.41 | 0.17032 | 0.10339 |  |  | 0.41 | 0.24805 | 0.15057
0.44 | 0.08201 | 0.043225 |  |  | 0.44 | 0.19573 | 0.10316 |  |  | 0.44 | 0.28519 | 0.15032
0.47 | 0.093273 | 0.043086 |  |  | 0.47 | 0.22307 | 0.10304 |  |  | 0.47 | 0.32512 | 0.15018
0.5 | 0.10536 | 0.043003 |  |  | 0.5 | 0.25228 | 0.10297 |  |  | 0.5 | 0.36777 | 0.15011
0.51786 | 0.11293 | 0.04297 |  |  | 0.51786 | 0.27055 | 0.10294 |  |  | 0.51786 | 0.39443 | 0.15008
0.53571 | 0.12078 | 0.042946 |  |  | 0.53571 | 0.28947 | 0.10292 |  |  | 0.53571 | 0.42205 | 0.15006
0.55357 | 0.12891 | 0.042927 |  |  | 0.55357 | 0.30905 | 0.10291 |  |  | 0.55357 | 0.45061 | 0.15005
0.57143 | 0.13732 | 0.042912 |  |  | 0.57143 | 0.32927 | 0.1029 |  |  | 0.57143 | 0.48011 | 0.15004
0.58929 | 0.146 | 0.042901 |  |  | 0.58929 | 0.35014 | 0.10289 |  |  | 0.58929 | 0.51056 | 0.15003
0.60714 | 0.15495 | 0.042893 |  |  | 0.60714 | 0.37166 | 0.10288 |  |  | 0.60714 | 0.54195 | 0.15002
0.625 | 0.16417 | 0.042886 |  |  | 0.625 | 0.39383 | 0.10288 |  |  | 0.625 | 0.57428 | 0.15002
0.64286 | 0.17367 | 0.04288 |  |  | 0.64286 | 0.41664 | 0.10287 |  |  | 0.64286 | 0.60755 | 0.15001
0.66071 | 0.18343 | 0.042876 |  |  | 0.66071 | 0.44009 | 0.10287 |  |  | 0.66071 | 0.64176 | 0.15001
0.67857 | 0.19346 | 0.042873 |  |  | 0.67857 | 0.46419 | 0.10287 |  |  | 0.67857 | 0.67691 | 0.15001
0.69643 | 0.20377 | 0.04287 |  |  | 0.69643 | 0.48893 | 0.10287 |  |  | 0.69643 | 0.713 | 0.15001
0.71429 | 0.21434 | 0.042867 |  |  | 0.71429 | 0.51432 | 0.10286 |  |  | 0.71429 | 0.75003 | 0.15001
0.73214 | 0.22518 | 0.042866 |  |  | 0.73214 | 0.54035 | 0.10286 |  |  | 0.73214 | 0.78799 | 0.15
0.75 | 0.23629 | 0.042864 |  |  | 0.75 | 0.56702 | 0.10286 |  |  | 0.75 | 0.82689 | 0.15
0.76786 | 0.24767 | 0.042863 |  |  | 0.76786 | 0.59434 | 0.10286 |  |  | 0.76786 | 0.86673 | 0.15
0.78571 | 0.25931 | 0.042862 |  |  | 0.78571 | 0.6223 | 0.10286 |  |  | 0.78571 | 0.90751 | 0.15
0.80357 | 0.27123 | 0.042861 |  |  | 0.80357 | 0.65091 | 0.10286 |  |  | 0.80357 | 0.94923 | 0.15
0.82143 | 0.28341 | 0.04286 |  |  | 0.82143 | 0.68016 | 0.10286 |  |  | 0.82143 | 0.99188 | 0.15
0.83929 | 0.29587 | 0.04286 |  |  | 0.83929 | 0.71005 | 0.10286 |  |  | 0.83929 | 1.0355 | 0.15
0.85714 | 0.30859 | 0.042859 |  |  | 0.85714 | 0.74058 | 0.10286 |  |  | 0.85714 | 1.08 | 0.15
0.875 | 0.32157 | 0.042859 |  |  | 0.875 | 0.77176 | 0.10286 |  |  | 0.875 | 1.1255 | 0.15
0.89286 | 0.33483 | 0.042858 |  |  | 0.89286 | 0.80358 | 0.10286 |  |  | 0.89286 | 1.1719 | 0.15
0.91071 | 0.34836 | 0.042858 |  |  | 0.91071 | 0.83604 | 0.10286 |  |  | 0.91071 | 1.2192 | 0.15
0.92857 | 0.36215 | 0.042858 |  |  | 0.92857 | 0.86915 | 0.10286 |  |  | 0.92857 | 1.2675 | 0.15
0.94643 | 0.37621 | 0.042858 |  |  | 0.94643 | 0.9029 | 0.10286 |  |  | 0.94643 | 1.3167 | 0.15
0.96429 | 0.39054 | 0.042857 |  |  | 0.96429 | 0.93729 | 0.10286 |  |  | 0.96429 | 1.3669 | 0.15
0.98214 | 0.40514 | 0.042857 |  |  | 0.98214 | 0.97232 | 0.10286 |  |  | 0.98214 | 1.418 | 0.15
1 | 0.42 | 0.042857 |  |  | 1 | 1.008 | 0.10286 |  |  | 1 | 1.47 | 0.15
PGA | Magnitud
0 | 1
0.17 | 3
1.4 | 3.9
9 | 4.9
34 | 5.9
124 | 6.9
5.74
Note on D1: Samuel: PEAK GROUND ACCELERATION

## Capacity Curve (hidden)
LABEL | [5 empty] | Elastic |  |  | Elastic
W1 |  |  |  | Table 3.1 |  |  | Plastic |  | Plastic
RANGE |  | TYPE |  |  |  | 0 | 0.252 | 0.756
NAME | STORIES | STORIES | FEET |  |  | 0 | 0.3024 | 5.4432
Low-Rise | 1-3 | 2 | 6
Quality level | Dy (in) | Ay(g) | Du (in) | Au(g) | table5.7 | [6 empty] | Building type | Pre-code |  |  |  | Low |  |  |  | Moderate |  |  |  | High
1.52 | 0.3024 | 0.252 | 5.4432 | 0.756 | Quality level | [7 empty] | Dy (in) | Ay(g) | Du (in) | Au(g) | Dy (in) | Ay(g) | Du (in) | Au(g) | Dy (in) | Ay(g) | Du (in) | Au(g) | Dy (in) | Ay(g) | Du (in) | Au(g)
Pre-code | 0.24 | 0.2 | 4.32 | 0.6 | 0 | [6 empty] | C1H | 0.5 | 0.024 | 4.52 | 0.073 | 0.5 | 0.024 | 3.77 | 0.073 | 1.01 | 0.049 | 9.05 | 0.147 | 2.01 | 0.098 | 24.13 | 0.293
Low | 0.24 | 0.2 | 4.32 | 0.6 | 1 | [6 empty] | C1L | 0.1 | 0.062 | 1.76 | 0.187 | 0.1 | 0.062 | 1.47 | 0.187 | 0.2 | 0.125 | 3.52 | 0.375 | 0.39 | 0.25 | 9.39 | 0.749
Moderate | 0.36 | 0.3 | 6.48 | 0.9 | 2 | [6 empty] | C1M | 0.29 | 0.052 | 3.46 | 0.156 | 0.29 | 0.052 | 2.88 | 0.156 | 0.58 | 0.104 | 6.91 | 0.312 | 1.15 | 0.208 | 18.44 | 0.624
High | 0.48 | 0.4 | 11.51 | 1.2 | 3 | [6 empty] | C2H | 0.74 | 0.063 | 5.51 | 0.159 | 0.74 | 0.063 | 4.59 | 0.159 | 1.47 | 0.127 | 11.02 | 0.317 | 2.94 | 0.254 | 29.39 | 0.635
[12 empty] | C2L | 0.12 | 0.1 | 1.8 | 0.25 | 0.12 | 0.1 | 1.5 | 0.25 | 0.24 | 0.2 | 3.6 | 0.5 | 0.48 | 0.4 | 9.59 | 1
[12 empty] | C2M | 0.26 | 0.083 | 2.6 | 0.208 | 0.26 | 0.083 | 2.16 | 0.208 | 0.52 | 0.167 | 5.19 | 0.417 | 1.04 | 0.333 | 13.84 | 0.833
[12 empty] | C3H | 0.74 | 0.063 | 4.13 | 0.143 | 0.74 | 0.063 | 4.13 | 0.143 | 0.74 | 0.063 | 4.13 | 0.143 | 0.74 | 0.063 | 4.13 | 0.143
[12 empty] | C3L | 0.12 | 0.1 | 1.35 | 0.225 | 0.12 | 0.1 | 1.35 | 0.225 | 0.12 | 0.1 | 1.35 | 0.225 | 0.12 | 0.1 | 1.35 | 0.225
[12 empty] | C3M | 0.26 | 0.083 | 1.95 | 0.188 | 0.26 | 0.083 | 1.95 | 0.188 | 0.26 | 0.083 | 1.95 | 0.188 | 0.26 | 0.083 | 1.95 | 0.188
[12 empty] | MH | 0.18 | 0.15 | 2.16 | 0.3 | 0.18 | 0.15 | 2.16 | 0.3 | 0.18 | 0.15 | 2.16 | 0.3 | 0.18 | 0.15 | 2.16 | 0.3
[12 empty] | PC1 | 0.18 | 0.15 | 2.16 | 0.3 | 0.18 | 0.15 | 1.8 | 0.3 | 0.36 | 0.3 | 4.32 | 0.6 | 0.72 | 0.6 | 11.51 | 1.2
[12 empty] | PC2H | 0.74 | 0.063 | 4.41 | 0.127 | 0.74 | 0.063 | 3.67 | 0.127 | 1.47 | 0.127 | 8.82 | 0.254 | 2.94 | 0.254 | 23.52 | 0.508
[12 empty] | PC2L | 0.12 | 0.1 | 1.44 | 0.2 | 0.12 | 0.1 | 1.2 | 0.2 | 0.24 | 0.2 | 2.88 | 0.4 | 0.48 | 0.4 | 7.67 | 0.8
[12 empty] | PC2M | 0.26 | 0.083 | 2.08 | 0.167 | 0.26 | 0.083 | 1.73 | 0.167 | 0.52 | 0.167 | 4.15 | 0.333 | 1.04 | 0.333 | 11.07 | 0.667
[12 empty] | RM1L | 0.16 | 0.133 | 1.92 | 0.267 | 0.16 | 0.133 | 1.6 | 0.267 | 0.32 | 0.267 | 3.84 | 0.533 | 0.64 | 0.533 | 10.23 | 1.066
[12 empty] | RM1M | 0.35 | 0.111 | 2.77 | 0.222 | 0.35 | 0.111 | 2.31 | 0.222 | 0.69 | 0.222 | 5.54 | 0.444 | 1.38 | 0.444 | 14.76 | 0.889
[12 empty] | RM2H | 0.98 | 0.085 | 5.88 | 0.169 | 0.98 | 0.085 | 4.9 | 0.169 | 1.96 | 0.169 | 11.76 | 0.338 | 3.92 | 0.338 | 31.35 | 0.677
[12 empty] | RM2L | 0.16 | 0.133 | 1.92 | 0.267 | 0.16 | 0.133 | 1.6 | 0.267 | 0.32 | 0.267 | 3.84 | 0.533 | 0.64 | 0.533 | 10.23 | 1.066
[12 empty] | RM2M | 0.35 | 0.111 | 2.77 | 0.222 | 0.35 | 0.111 | 2.31 | 0.222 | 0.69 | 0.222 | 5.54 | 0.444 | 1.38 | 0.444 | 14.76 | 0.889
[12 empty] | S1H | 1.16 | 0.024 | 10.48 | 0.073 | 1.16 | 0.024 | 8.73 | 0.073 | 2.33 | 0.049 | 20.96 | 0.147 | 4.66 | 0.098 | 55.88 | 0.293
[12 empty] | S1L | 0.15 | 0.062 | 2.75 | 0.187 | 0.15 | 0.062 | 2.29 | 0.187 | 0.31 | 0.125 | 5.5 | 0.375 | 0.61 | 0.25 | 14.67 | 0.749
[12 empty] | S1M | 0.44 | 0.039 | 5.33 | 0.117 | 0.44 | 0.039 | 4.44 | 0.117 | 0.89 | 0.078 | 10.65 | 0.234 | 1.78 | 0.156 | 28.4 | 0.468
[12 empty] | S2H | 1.94 | 0.063 | 11.62 | 0.127 | 1.94 | 0.063 | 9.68 | 0.127 | 3.87 | 0.127 | 23.24 | 0.254 | 7.75 | 0.254 | 61.97 | 0.508
[12 empty] | S2L | 0.16 | 0.1 | 1.88 | 0.2 | 0.16 | 0.1 | 1.57 | 0.2 | 0.31 | 0.2 | 3.76 | 0.4 | 0.63 | 0.4 | 10.02 | 0.8
[12 empty] | S2M | 0.61 | 0.083 | 4.85 | 0.167 | 0.61 | 0.083 | 4.04 | 0.167 | 1.21 | 0.167 | 9.7 | 0.333 | 2.43 | 0.333 | 25.88 | 0.667
[12 empty] | S3 | 0.16 | 0.1 | 1.88 | 0.2 | 0.16 | 0.1 | 1.57 | 0.2 | 0.31 | 0.2 | 3.76 | 0.4 | 0.63 | 0.4 | 10.02 | 0.8
[12 empty] | S4H | 0.87 | 0.051 | 5.88 | 0.114 | 0.87 | 0.051 | 4.9 | 0.114 | 1.74 | 0.102 | 11.76 | 0.228 | 3.49 | 0.203 | 31.37 | 0.457
[12 empty] | S4L | 0.1 | 0.08 | 1.3 | 0.18 | 0.1 | 0.08 | 1.08 | 0.18 | 0.19 | 0.16 | 2.59 | 0.36 | 0.38 | 0.32 | 6.91 | 0.72
| Sd | Sa | Damage state | [8 empty] | S4M | 0.27 | 0.067 | 2.46 | 0.15 | 0.27 | 0.067 | 2.05 | 0.15 | 0.55 | 0.133 | 4.91 | 0.3 | 1.09 | 0.267 | 13.1 | 0.6
Capacity curve | 0.22791 | 0.20269 | Plastic | 0.17437 | 0.46055 | 0.83333 | [5 empty] | S5H | 1.09 | 0.063 | 5.45 | 0.127 | 1.09 | 0.063 | 5.45 | 0.127 | 1.09 | 0.063 | 5.45 | 0.127 | 1.09 | 0.063 | 5.45 | 0.127
Rock | 0.22795 | 0.042865 |  | 1.0065e-06 | 7.1923 | 0.042856 | 0.73663 |  |  |  |  | S5L | 0.12 | 0.1 | 1.2 | 0.2 | 0.12 | 0.1 | 1.2 | 0.2 | 0.12 | 0.1 | 1.2 | 0.2 | 0.12 | 0.1 | 1.2 | 0.2
Capacity curve | 0.31329 | 0.25817 | Plastic | 0.17437 | 0.46055 | 0.83333 | [5 empty] | S5M | 0.34 | 0.083 | 2.27 | 0.167 | 0.34 | 0.083 | 2.27 | 0.167 | 0.34 | 0.083 | 2.27 | 0.167 | 0.34 | 0.083 | 2.27 | 0.167
Stiff Soil | 0.31321 | 0.10291 |  | 5.3886e-07 | 7.7338 | 0.10286 | 0.55729 |  |  | 0.14001 | 0.15363 | URML | 0.24 | 0.2 | 2.4 | 0.4 | 0.24 | 0.2 | 2.4 | 0.4 | 0.24 | 0.2 | 2.4 | 0.4 | 0.24 | 0.2 | 2.4 | 0.4
Capacity curve | 0.40217 | 0.30172 | Plastic | 0.17437 | 0.46055 | 0.83333 |  |  |  | 0.017288 | 0.01988 | URMM | 0.27 | 0.111 | 1.81 | 0.222 | 0.27 | 0.111 | 1.81 | 0.222 | 0.27 | 0.111 | 1.81 | 0.222 | 0.27 | 0.111 | 1.81 | 0.222
Soft Soil | 0.40214 | 0.15008 |  | 3.4221e-07 | 8.3235 | 0.15 | 0.5229 |  |  | 0.00102 | 0.0012119 | W1 | 0.24 | 0.2 | 4.32 | 0.6 | 0.24 | 0.2 | 4.32 | 0.6 | 0.36 | 0.3 | 6.48 | 0.9 | 0.48 | 0.4 | 11.51 | 1.2
[10 empty] | 1.2713e-05 | 1.6029e-05 | W2 | 0.16 | 0.1 | 2.35 | 0.25 | 0.16 | 0.1 | 2.35 | 0.25 | 0.31 | 0.2 | 4.7 | 0.5 | 0.63 | 0.4 | 12.53 | 1
0

## Fragility (hidden)
Design Code | Rock | Stiff soil | Soft soil |  |  | 0.22791 | 0.31329 | 0.40217 | 0
| 0.22791 | 0.31329 | 0.40217 |  |  | 0.22791 | 0.31329 | 0.40217 | 1
Quality level | 2.95
Table 5.9 | Slight |  | Moderate |  | Extensive |  | Complete
Type | Ŝd.S/S | βS | Ŝd.S/M | βM | Ŝd.S/E | βE | Ŝd.S/C | βC
W1 | 0.5 | 0.802 | 1.497 | 0.8125 | 4.981 | 0.852 | 12.4425 | 0.9735 | Quality level
Low | 0.5 | 0.93 | 1.25 | 0.98 | 3.86 | 1.02 | 9.45 | 0.99 | 1
Moderate | 0.5 | 0.84 | 1.25 | 0.86 | 3.86 | 0.89 | 9.45 | 1.04 | 2
High | 0.5 | 0.8 | 1.51 | 0.81 | 5.04 | 0.85 | 12.6 | 0.97 | 3
| ROCK | Cumulative Probability
Damage State | Sd | ŜdS | βds | Ln(Sd/Ŝd.ds)/βd | P[ds¦Sd]
Slight | 0.22791 | 0.5 | 0.802 | -0.9796 | 16.36%
Moderate | 0.22791 | 1.497 | 0.8125 | -2.3166 | 1.026%
Extensive | 0.22791 | 4.981 | 0.852 | -3.6202 | 0.01472%
Complete | 0.22791 | 12.4425 | 0.9735 | -4.1088 | 0.001989%
| STIFF SOIL | Cumulative Probability
Damage State | Sd | ŜdS | βds | Ln(Sd/Ŝd.ds)/βd | P[ds¦Sd]
Slight | 0.31329 | 0.5 | 0.802 | -0.58289 | 28%
Moderate | 0.31329 | 1.497 | 0.8125 | -1.925 | 2.711%
Extensive | 0.31329 | 4.981 | 0.852 | -3.2468 | 0.05836%
Complete | 0.31329 | 12.4425 | 0.9735 | -3.782 | 0.00778%
| SOFT SOIL | Cumulative Probability
Damage State | Sd | ŜdS | βds | Ln(Sd/Ŝd.ds)/βd | P[ds¦Sd]
Slight | 0.40217 | 0.5 | 0.802 | -0.27148 | 39.3%
Moderate | 0.40217 | 1.497 | 0.8125 | -1.6176 | 5.287%
Extensive | 0.40217 | 4.981 | 0.852 | -2.9536 | 0.157%
Complete | 0.40217 | 12.4425 | 0.9735 | -3.5254 | 0.02114%
| Slight | Moderate | Extensive | Complete
0 | 0 | 0 | 0 | 0 |  |  | % Damage | Damage | Current | Baseline | Retrofited
0.022969 | 6.127e-05 | 1.3662e-07 | 1.3624e-10 | 5.0286e-11 |  |  | 2.5% | Slight | 28% | 28% | 1.037%
0.045938 | 0.0014568 | 9.0176e-06 | 1.8976e-08 | 4.3559e-09 |  |  | 25% | Moderate | 2.711% | 2.711% | 0.04837%
0.068906 | 0.006734 | 7.5662e-05 | 2.5274e-07 | 4.71e-08 |  |  | 50% | Extensive | 0.05836% | 0.05836% | 0.001601%
0.091875 | 0.017324 | 0.00029648 | 1.3891e-06 | 2.3027e-07 |  |  | 100% | Complete | 0.00778% | 0.00778% | 5.611e-06%
0.11484 | 0.033311 | 0.00078836 | 4.8296e-06 | 7.44e-07 | [5 empty] | 1.415% | 0.03882%
0.13781 | 0.054041 | 0.0016635 | 1.2731e-05 | 1.868e-06
0.16078 | 0.078583 | 0.0030158 | 2.7919e-05 | 3.9623e-06
0.18375 | 0.10598 | 0.0049156 | 5.3748e-05 | 7.454e-06
0.20672 | 0.13538 | 0.00741 | 9.3942e-05 | 1.2822e-05 |  |  |  | Pre-code | [7 empty] | Low-code | [7 empty] | Moderate-code | [7 empty] | High-code
0.22969 | 0.16604 | 0.010525 | 0.00015244 | 2.0584e-05 |  |  | Building type | Slight |  | Moderate |  | Extensive |  | Complete |  | Slight |  | Moderate |  | Extensive |  | Complete |  | Slight |  | Moderate |  | Extensive |  | Complete |  | Slight |  | Moderate |  | Extensive |  | Complete
0.25266 | 0.19736 | 0.01427 | 0.00023329 | 3.1283e-05 |  |  |  | Ŝd.S/S | βS | Ŝd.S/M | βM | Ŝd.S/E | βE | Ŝd.S/C | βC | Ŝd.S/S | βS | Ŝd.S/M | βM | Ŝd.S/E | βE | Ŝd.S/C | βC | Ŝd.S/S | βS | Ŝd.S/M | βM | Ŝd.S/E | βE | Ŝd.S/C | βC | Ŝd.S/S | βS | Ŝd.S/M | βM | Ŝd.S/E | βE | Ŝd.S/C | βC
0.27563 | 0.22886 | 0.01864 | 0.0003405 | 4.5476e-05 |  |  | C1 | 0.72 | 0.98 | 1.15 | 0.94 | 2.88 | 0.9 | 7.2 | 0.97 | 0.9 | 0.95 | 1.44 | 0.91 | 3.6 | 0.85 | 9 | 0.97 | 0.9 | 0.89 | 1.56 | 0.9 | 4.2 | 0.9 | 10.8 | 0.89 | 0.9 | 0.81 | 1.8 | 0.84 | 5.4 | 0.86 | 14.4 | 0.81
0.29859 | 0.26018 | 0.023619 | 0.00047799 | 6.3729e-05 |  |  | C1M | 1.2 | 0.73 | 1.92 | 0.77 | 4.8 | 0.83 | 12 | 0.98 | 1.5 | 0.7 | 2.4 | 0.74 | 6 | 0.86 | 15 | 0.98 | 1.5 | 0.7 | 2.6 | 0.7 | 7 | 0.7 | 18 | 0.89 | 1.5 | 0.68 | 3 | 0.67 | 9 | 0.68 | 24 | 0.81
0.32156 | 0.29102 | 0.029182 | 0.00064952 | 8.6604e-05 |  |  | C2L | 0.58 | 1.11 | 1.1 | 1.09 | 2.84 | 1.07 | 7.2 | 0.93 | 0.72 | 1.04 | 1.37 | 1.02 | 3.55 | 0.99 | 9 | 0.95 | 0.72 | 0.91 | 1.52 | 0.97 | 4.17 | 1.03 | 10.8 | 0.87 | 0.72 | 0.81 | 1.8 | 0.84 | 5.4 | 0.93 | 14.4 | 0.92
0.34453 | 0.32119 | 0.0353 | 0.00085865 | 0.00011466 |  |  | C3L | 0.43 | 1.19 | 0.86 | 1.15 | 2.16 | 1.15 | 5.04 | 0.92 | 0.54 | 1.09 | 1.08 | 1.07 | 2.7 | 1.08 | 6.3 | 0.91 | 0.54 | 1.09 | 1.08 | 1.07 | 2.7 | 1.08 | 6.3 | 0.91 | 0.54 | 1.09 | 1.08 | 1.07 | 2.7 | 1.08 | 6.3 | 0.91
0.3675 | 0.35053 | 0.04194 | 0.0011087 | 0.00014843 |  |  | RM1L | 0.58 | 1.2 | 0.92 | 1.17 | 2.31 | 1.17 | 6.3 | 0.94 | 0.72 | 1.11 | 1.15 | 1.1 | 2.89 | 1.1 | 7.88 | 0.92 | 0.72 | 0.96 | 1.25 | 0.99 | 3.37 | 1.05 | 9.45 | 0.94 | 0.72 | 0.84 | 1.44 | 0.86 | 4.32 | 0.92 | 12.6 | 1.01
0.39047 | 0.37893 | 0.049064 | 0.0014026 | 0.00018845 |  |  | RM2L | 0.58 | 1.14 | 0.92 | 1.1 | 2.31 | 1.15 | 6.3 | 0.92 | 0.72 | 1.05 | 1.15 | 1.07 | 2.89 | 1.09 | 7.88 | 0.91 | 0.72 | 0.91 | 1.25 | 0.96 | 3.37 | 1.02 | 9.45 | 0.93 | 0.72 | 0.8 | 1.44 | 0.81 | 4.32 | 0.91 | 12.6 | 0.98
0.41344 | 0.40631 | 0.056637 | 0.0017433 | 0.00023523 |  |  | W1 | 0.4 | 1.01 | 1 | 1.05 | 3.09 | 1.07 | 7.56 | 1.06 | 0.5 | 0.93 | 1.25 | 0.98 | 3.86 | 1.02 | 9.45 | 0.99 | 0.5 | 0.84 | 1.25 | 0.86 | 3.86 | 0.89 | 9.45 | 1.04 | 0.5 | 0.8 | 1.51 | 0.81 | 5.04 | 0.85 | 12.6 | 0.97
0.43641 | 0.43265 | 0.064621 | 0.0021332 | 0.00028925 |  |  | W2 | 0.69 | 1.04 | 1.71 | 0.97 | 5.29 | 0.9 | 12.96 | 0.99 | 0.86 | 0.97 | 2.14 | 0.9 | 6.62 | 0.89 | 16.2 | 0.99 | 0.86 | 0.89 | 2.14 | 0.95 | 6.62 | 0.95 | 16.2 | 0.92 | 0.86 | 0.81 | 2.59 | 0.88 | 8.64 | 0.9 | 21.6 | 0.83
0.45937 | 0.45793 | 0.072977 | 0.0025745 | 0.00035098
0.48234 | 0.48212 | 0.081671 | 0.0030692 | 0.00042087
0.50531 | 0.50526 | 0.090666 | 0.003619 | 0.00049933
0.52828 | 0.52735 | 0.099929 | 0.0042253 | 0.00058675
0.55125 | 0.54842 | 0.10943 | 0.0048892 | 0.00068351
0.57422 | 0.56851 | 0.11913 | 0.0056119 | 0.00078995
0.59719 | 0.58764 | 0.12901 | 0.006394 | 0.00090639
0.62016 | 0.60586 | 0.13905 | 0.0072361 | 0.0010331
0.64312 | 0.62319 | 0.1492 | 0.0081387 | 0.0011705
0.66609 | 0.63969 | 0.15946 | 0.0091018 | 0.0013186
0.68906 | 0.65539 | 0.1698 | 0.010126 | 0.0014779
0.71203 | 0.67032 | 0.18021 | 0.01121 | 0.0016484
0.735 | 0.68452 | 0.19065 | 0.012355 | 0.0018303
0.75797 | 0.69803 | 0.20112 | 0.01356 | 0.002024
0.78094 | 0.71088 | 0.2116 | 0.014824 | 0.0022294
0.80391 | 0.72311 | 0.22207 | 0.016148 | 0.0024468
0.82687 | 0.73475 | 0.23253 | 0.01753 | 0.0026762
0.84984 | 0.74582 | 0.24296 | 0.01897 | 0.0029178
0.87281 | 0.75636 | 0.25335 | 0.020467 | 0.0031717
0.89578 | 0.7664 | 0.26368 | 0.022019 | 0.0034379
0.91875 | 0.77596 | 0.27396 | 0.023628 | 0.0037165
0.94172 | 0.78506 | 0.28418 | 0.02529 | 0.0040076
0.96469 | 0.79373 | 0.29432 | 0.027006 | 0.0043112
0.98766 | 0.802 | 0.30438 | 0.028774 | 0.0046273
1.0106 | 0.80988 | 0.31435 | 0.030594 | 0.0049559
1.0336 | 0.81739 | 0.32423 | 0.032463 | 0.0052971
1.0566 | 0.82456 | 0.33402 | 0.034382 | 0.0056509
1.0795 | 0.8314 | 0.3437 | 0.036349 | 0.0060172
1.1025 | 0.83792 | 0.35328 | 0.038363 | 0.006396
1.1255 | 0.84415 | 0.36276 | 0.040422 | 0.0067873
1.1484 | 0.8501 | 0.37213 | 0.042526 | 0.007191
1.1714 | 0.85578 | 0.38138 | 0.044673 | 0.0076072
1.1944 | 0.8612 | 0.39052 | 0.046863 | 0.0080357
1.2173 | 0.86639 | 0.39955 | 0.049093 | 0.0084766
1.2403 | 0.87135 | 0.40846 | 0.051364 | 0.0089297
1.2633 | 0.8761 | 0.41725 | 0.053674 | 0.009395
1.2862 | 0.88063 | 0.42593 | 0.056021 | 0.0098724
1.3092 | 0.88497 | 0.43449 | 0.058404 | 0.010362
1.3322 | 0.88913 | 0.44292 | 0.060824 | 0.010863
1.3552 | 0.89311 | 0.45124 | 0.063277 | 0.011377
1.3781 | 0.89692 | 0.45944 | 0.065764 | 0.011902
1.4011 | 0.90057 | 0.46753 | 0.068282 | 0.012438
1.47 | 0.91063 | 0.49106 | 0.076021 | 0.014118

## Masonry walls (hidden)
Wind pressure (p) |  |  |  | Wind pressure (p) |  |  |  | Wind pressure (p) |  |  |  | Wind pressure (p) |  |  |  | Wind speed | Wind speed | roof angle | Mean wall Pressure (psf) | Elastic modulus |  |  |  | Building type | Building material
loc code | 16-60 | [18 empty] | 0 | Clay | 1350000
Wind data | 3661 | [18 empty] | 1 | Wood | 1250000
Wind speed | 139.5422 | mph |  | Wind speed | 139.5422 | mph |  | Wind speed | 139.5422 | mph |  | Wind speed | 139.5422 | mph |  | 110 | 110 | 0 | 19.2 | 2 | Concrete | 3045000
R_angle= | 20 |  |  | R_angle= | 20 |  |  | R_angle= | 20 |  |  | R_angle= | 20 |  |  | 115 | 110 | 5 | 19.2 | 3 | Steel | 20000000 |  | C1 | 2
Exposure = | B |  |  | Exposure = | B |  |  | Exposure = | B |  |  | Exposure = | B |  |  | 120 | 110 | 10 | 21.6 |  |  |  |  | C1M | 2
Mean height | 15 | ft |  | Mean height | 23 | ft |  | Mean height | 23 | ft |  | Mean height | 23 | ft |  | 130 | 110 | 15 | 24.1 | Category | V<100 | V>100 |  | C2 | 2
|  |  |  | Building type | C1 |  |  | Building type | C3 |  |  | Building type | W1 |  |  | 140 | 110 | 20 | 26.6 | I | 0.87 | 0.77 |  | C3 | 2
Brick baseline= | 0 |  |  | Brick baseline= | 2 |  |  | Brick baseline= | 2 |  |  | Brick baseline= | 1 |  |  | 150 | 110 | 25 | 24.1 | II | 1 | 1 |  | RM1L | 0
Brick Retrofited= |  |  |  | P = | λ*Kzt*pS30 | ASCE 7-2010 |  | P = | λ*Kzt*pS30 | ASCE 7-2010 |  | P = | λ*Kzt*pS30 | ASCE 7-2010 |  | 160 | 110 | 30 | 21.6 | III | 1.15 | 1.15 |  | RM2L | 0
P = | λ*Kzt*pS30 | ASCE 7-2010 | [13 empty] | 180 | 115 | 0 | 21 | IV | 1.15 | 1.15 |  | W1 | 1
|  |  |  | λ= | 0 |  |  | λ= | 0 |  |  | λ= | 0 |  |  | 200 | 115 | 5 | 21 |  |  |  |  | W2 | 1
λ= | 1 |  |  | Kzt= | 1 |  |  | Kzt= | 1 |  |  | Kzt= | 1 |  |  |  | 115 | 10 | 23.7 | Mean roof height (ft) | Exposure
Kzt= | 1 |  |  | pS30= | 0 | psf |  | pS30= | 0 | psf |  | pS30= | 0 | psf |  |  | 115 | 15 | 26.3 |  | B | C | D
pS30= | 0 | psf | [14 empty] | 115 | 20 | 29 | 15 | 1 | 1.21 | 1.47
|  |  |  | Presure= | 0 | psf |  | Presure= | 0 | psf |  | Presure= | 0 | psf |  |  | 115 | 25 | 26.3 | 20 | 1 | 1.29 | 1.55
Presure= | 0 | psf | [14 empty] | 115 | 30 | 23.6 | 25 | 1 | 1.35 | 1.61
[17 empty] | 120 | 0 | 22.8 | 30 | 1 | 1.4 | 1.66
|  |  |  | Failure Pressures (pr) |  |  |  | Failure Pressures (pr) |  |  |  | Failure Pressures (pr) |  |  |  |  | 120 | 5 | 22.8 | 35 | 1.05 | 1.45 | 1.7
Failure Pressures (pr) |  |  |  | φ= | 0.9 |  |  | φ= | 0.9 |  |  | φ= | 0.9 |  |  |  | 120 | 10 | 25.8 | 40 | 1.09 | 1.49 | 1.74
φ= | 0.9 |  |  | L_wall= | 13.1234 | ft |  | L_wall= | 13.1234 | ft |  | L_wall= | 13.1234 | ft |  |  | 120 | 15 | 28.7 | 45 | 1.12 | 1.53 | 1.78
L_wall= | 60.0339 | ft |  | H_wall= | 23 | ft |  | H_wall= | 23 | ft |  | H_wall= | 23 | ft |  |  | 120 | 20 | 31.6 | 50 | 1.6 | 1.56 | 1.81
H_wall= | 15 | ft | [14 empty] | 120 | 25 | 28.6 | 55 | 1.19 | 1.59 | 1.84
|  |  |  | rH= | 1.6627 |  |  | rH= | 1.6627 |  |  | rH= | 1.6627 |  |  |  | 120 | 30 | 25.7 | 60 | 1.22 | 1.62 | 1.87
rH= | 0.23704 |  |  | rL= | 0.60145 |  |  | rL= | 0.60145 |  |  | rL= | 0.60145 |  |  |  | 130 | 0 | 26.8
rL= | 4.2187 | [15 empty] | 130 | 5 | 26.8
|  |  |  | z/H = | 0.37051 |  |  | z/H = | 0.37051 |  |  | z/H = | 0.37051 |  |  |  | 130 | 10 | 30.2
z/H = | 0.72081 |  |  | x/L= | 0.61374 |  |  | x/L= | 0.61374 |  |  | x/L= | 0.61374 |  |  |  | 130 | 15 | 33.7
x/L= | 0.1791 | [15 empty] | 130 | 20 | 37.1
|  |  |  | E= | 438480000 | psf |  | E= | 438480000 | psf |  | E= | 180000000 | psf |  |  | 130 | 25 | 33.6
E= | 194400000 | psf |  | In= | 0.039301 | in4 |  | In= | 0.039301 | in4 |  | In= | 0.039301 | in4 |  |  | 130 | 30 | 30.1
E retrofited= | 291600000 | psf |  | P= | 558.1835 | lb | ACI-530 | P= | 558.1835 | lb | ACI-530 | P= | 229.1394 | lb | ACI-530 |  | 140 | 0 | 31.1
In= | 0.17979 | in4 |  | m= | 558.1835 | lb |  | m= | 558.1835 | lb |  | m= | 229.1394 | lb |  |  | 140 | 5 | 31.1
P= | 2661.6309 | lb | ACI-530 | pr= | 29.9772 | psf |  | pr= | 29.9772 | psf |  | pr= | 12.3059 | psf |  |  | 140 | 10 | 35.1
P retrofited= | 3992.4463 | lb | ACI-530 | [13 empty] | 140 | 15 | 39
m= | 2661.6309 | lb |  | Walls Failure Probability (Pf) |  |  |  | Walls Failure Probability (Pf) |  |  |  | Walls Failure Probability (Pf) |  |  |  |  | 140 | 20 | 43
m retrofited= | 3992.4463 | lb |  | Pf= | 0.003167% |  |  | Pf= | 0.003167% |  |  | Pf= | 0.003167% |  |  |  | 140 | 25 | 39
pr= | 80.8109 | psf | [14 empty] | 140 | 30 | 35
pr= | 121.2164 | psf | [14 empty] | 150 | 0 | 35.7
[17 empty] | 150 | 5 | 35.7
Walls Failure Probability (Pf) | [16 empty] | 150 | 10 | 40.2
Pf= | 0.003167% | [15 empty] | 150 | 15 | 44.8
Pf= | 0.003167% | [15 empty] | 150 | 20 | 49.4
[17 empty] | 150 | 25 | 44.8
Windows and glass doors (Pf) | [16 empty] | 150 | 30 | 40.1
P= | 0 | psf | [14 empty] | 160 | 0 | 40.6
Media baseline= | 80 | psf | [14 empty] | 160 | 5 | 40.6
Media retrofited= | 140 | psf | [14 empty] | 160 | 10 | 45.8
COV= | 0.2 | [15 empty] | 160 | 15 | 51
σ= | 16 | [15 empty] | 160 | 20 | 56.2
[17 empty] | 160 | 25 | 50.9 | Design Pressure
Pf baseline= | 2.867e-05% | [15 empty] | 160 | 30 | 45.7 | 40
Pf retrofited= | 0% | [15 empty] | 180 | 0 | 51.4 | 60
[17 empty] | 180 | 5 | 51.4 | 80
[17 empty] | 180 | 10 | 58 | 100
[17 empty] | 180 | 15 | 64.5 | 120
[17 empty] | 180 | 20 | 71.1
[17 empty] | 180 | 25 | 64.5
[17 empty] | 180 | 30 | 57.8
[17 empty] | 200 | 0 | 63.5
[17 empty] | 200 | 5 | 63.5
[17 empty] | 200 | 10 | 71.5
[17 empty] | 200 | 15 | 79.7
[17 empty] | 200 | 20 | 87.8
[17 empty] | 200 | 25 | 79.6
[17 empty] | 200 | 30 | 71.3
Note on B6: Samuel: B: Heavy Obstruction Wooded areas, urban and suburban C: Scatterd Obstruction flat open country, obstructions less than 30ft D: Unobstructed
Note on F6: Samuel: B: Heavy Obstruction Wooded areas, urban and suburban C: Scatterd Obstruction flat open country, obstructions less than 30ft D: Unobstructed
Note on J6: Samuel: B: Heavy Obstruction Wooded areas, urban and suburban C: Scatterd Obstruction flat open country, obstructions less than 30ft D: Unobstructed
Note on N6: Samuel: B: Heavy Obstruction Wooded areas, urban and suburban C: Scatterd Obstruction flat open country, obstructions less than 30ft D: Unobstructed

## Roof (hidden)
Wind pressure (p) |  |  |  | Wind speed | roof angle | Mean roof Pressure (psf) |  | Elastic module
Wind speed | 140 | mph |  | 110 | 0 | 23.1 | Clay | 1350000
Exposure = | B |  |  | 110 | 5 | 23.1 | Concrete | 3045000
|  |  |  | 110 | 10 | 23.1
S_roof= | 9.84 | ft |  | 110 | 15 | 23.1 | Category | V<100 | V>100
Type structure an connection quality (baseline) | Low |  |  | 110 | 20 | 23.1 | I | 0.87 | 0.77
Type structure an connection quality (retrofited) | Medium |  |  | 110 | 25 | 10.7 | II | 1 | 1
|  |  |  | 110 | 30 | 1.7 | III | 1.15 | 1.15
λ= | 1 |  |  | 115 | 0 | 25.2 | IV | 1.15 | 1.15
Kzt= | 1 |  |  | 115 | 5 | 25.2
R_angle= | 20 |  |  | 115 | 10 | 25.2 | Mean roof height (ft) | Exposure
pS30= | 37.3 | psf |  | 115 | 15 | 25.2 |  | B | C | D
Presure= | 37.3 | psf |  | 115 | 20 | 25.2 | 15< | 1 | 1.21 | 1.47
|  |  |  | 115 | 25 | 11.7 | 20 | 1 | 1.29 | 1.55
|  |  |  | 115 | 30 | 1.8 | 25 | 1 | 1.35 | 1.61
Roof-Wall Connections |  |  |  | 120 | 0 | 27.4 | 30 | 1 | 1.4 | 1.66
Presure= | 734.064 | lb |  | 120 | 5 | 27.4 | 35 | 1.05 | 1.45 | 1.7
Media baseline= | 676 | lb |  | 120 | 10 | 27.4 | 40 | 1.09 | 1.49 | 1.74
Media retrofited= | 1352 | lb |  | 120 | 15 | 27.4 | 45 | 1.12 | 1.53 | 1.78
COV= | 0.3 |  |  | 120 | 20 | 27.4 | 50 | 1.6 | 1.56 | 1.81
σ= | 202.8 |  |  | 120 | 25 | 12.7 | 55 | 1.19 | 1.59 | 1.84
|  |  |  | 120 | 30 | 2 | >60 | 1.22 | 1.62 | 1.87
Pf= | 61.27% |  |  | 130 | 0 | 32.2
Pf= | 0.1156% |  |  | 130 | 5 | 32.2
|  |  |  | 130 | 10 | 32.2
Type structure | Connection | Media (lb) | COV | 130 | 15 | 32.2
Douglas Fir | three 8d nails | 676 | 0.08 | 130 | 20 | 32.2
Douglas Fir | Strapped connection | 867 | 0.18 | 130 | 25 | 14.9
Douglas Fir | 0.5" straps and two 6d nails | 908 | 0.1 | 130 | 30 | 2.3
SPF lumber | three 8d nails | 319 | 0.2 | 140 | 0 | 37.3
SPF lumber | five 8d nails | 1520 | 0.2 | 140 | 5 | 37.3
SPF lumber | Strapped connection | 900 | 0.15 | 140 | 10 | 37.3
Florida building Code | 0.125" strapp and 8d nails | 1200 | 0.3 | 140 | 15 | 37.3
|  |  |  | 140 | 20 | 37.3
Type structure (quality) | Media (lb) |  |  | 140 | 25 | 17.3
Poor | 319 |  |  | 140 | 30 | 2.7
Low | 676 |  |  | 150 | 0 | 42.9
Medium | 908 |  |  | 150 | 5 | 42.9
High | 1200 |  |  | 150 | 10 | 42.9
|  |  |  | 150 | 15 | 42.9
|  |  |  | 150 | 20 | 42.9
|  |  |  | 150 | 25 | 19.9
|  |  |  | 150 | 30 | 3.1
|  |  |  | 160 | 0 | 48.8
|  |  |  | 160 | 5 | 48.8
|  |  |  | 160 | 10 | 48.8
|  |  |  | 160 | 15 | 48.8
|  |  |  | 160 | 20 | 48.8
|  |  |  | 160 | 25 | 22.6
|  |  |  | 160 | 30 | 3.5
|  |  |  | 180 | 0 | 61.7
|  |  |  | 180 | 5 | 61.7
|  |  |  | 180 | 10 | 61.7
|  |  |  | 180 | 15 | 61.7
|  |  |  | 180 | 20 | 61.7
|  |  |  | 180 | 25 | 28.6
|  |  |  | 180 | 30 | 4.4
|  |  |  | 200 | 0 | 76.2
|  |  |  | 200 | 5 | 76.2
|  |  |  | 200 | 10 | 76.2
|  |  |  | 200 | 15 | 76.2
|  |  |  | 200 | 20 | 76.2
|  |  |  | 200 | 25 | 35.4
|  |  |  | 200 | 30 | 5.5
Note on A5: Samuel: distance from roof support

## Projectiles windows (hidden)
V | 62.5856 | Meters/s
h | 2.286 | Meters |  |  |  | 0 | Clay | 7.1
[6 empty] | 1 | Wood | 6.4
Distance from Buildings (m) | Factors |  |  |  | N° impacts | 2 | Concrete | 10.6
| x | n | h0 | f
60 | 2.1788 | 10.5198 | 24 | 2.4445 | 25.7152
Wall Resistance | 7.1 | kg-m/s
Window Resistance | 0.1 | kg-m/s
Window Resistance | 0.175 | kg-m/s
Probability of no damage
Pm wall | 100%
Pm window | 95.09%
Pm window | 99.95%
Area Wall | 274.4748 | m2
Area Window | 1 | m2
Probability of impact damage
Pd Wall | 0%
Pd Window | 71.74% | 2.867e-05% | 71.74%
Pd Window | 0% | 0% | 0%

## Flood (hidden)
Masonry and Concrete Structure
Flood velocity | 2 | ft/sec
Flood depth | 5 | ft
1st Floor hight | 0.98425 | ft
Flood channels | 3.5 | ft
Stories | Velocity Threshold | Collapse Potential | Damage
1 | 6.31 | No collapse | 4.944%
2 | 7.47 | No collapse | 2.386%
3 | 9.02 | No collapse | 15.21%
Operational | Not Operational
Operational | Not Operational